## SOP
Standard of Performance data for the month of October-2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2016-10-01 | 0:00 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR08/437 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
3 | SR1L03 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2016-10-07 | 17:42 | 2016-10-13 | 10:38 | -- | -- | -- |  |  |  | 136.9333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/183 |  | 100 | 744
[5 empty] | -- | 2016-10-13 | 18:19 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 437.6833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/327 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 574.6167 | [6 empty] | 744
4 | SR1L04 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2016-10-01 | 0:00 | 2016-10-07 | 11:12 | -- | -- | -- |  |  |  | 155.2 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 155.2 | [6 empty] | 744
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2016-10-01 | 0:16 | 2016-10-01 | 4:57 | -- | -- | -- |  |  |  | 4.6833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/01 |  | 100 | 744
[5 empty] | -- | 2016-10-02 | 0:21 | 2016-10-02 | 6:57 | -- | -- | -- |  |  |  | 6.6 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/28 |  |  | 744
[5 empty] | -- | 2016-10-02 | 23:03 | 2016-10-03 | 6:20 | -- | -- | -- |  |  |  | 7.2833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/43 |  |  | 744
[5 empty] | -- | 2016-10-04 | 0:10 | 2016-10-04 | 7:04 | -- | -- | -- |  |  |  | 6.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/78 |  |  | 744
[5 empty] | -- | 2016-10-05 | 0:18 | 2016-10-05 | 7:01 | -- | -- | -- |  |  |  | 6.7167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/101 |  |  | 744
[5 empty] | -- | 2016-10-07 | 0:01 | 2016-10-07 | 9:15 | -- | -- | -- |  |  |  | 9.2333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/162 |  |  | 744
[5 empty] | -- | 2016-10-08 | 2:03 | 2016-10-08 | 6:53 | -- | -- | -- |  |  |  | 4.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/198 |  |  | 744
[5 empty] | -- | 2016-10-09 | 15:31 | 2016-10-10 | 7:02 | -- | -- | -- |  |  |  | 15.5167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/233 |  |  | 744
[5 empty] | -- | 2016-10-10 | 17:20 | 2016-10-11 | 5:51 | -- | -- | -- |  |  |  | 12.5167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/256 |  |  | 744
[5 empty] | -- | 2016-10-11 | 20:50 | 2016-10-12 | 7:36 | -- | -- | -- |  |  |  | 10.7667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/277 |  |  | 744
[5 empty] | -- | 2016-10-13 | 18:09 | 2016-10-14 | 10:15 | -- | -- | -- |  |  |  | 16.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/325 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 101.15 | [6 empty] | 744
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | 2016-10-18 | 11:58 | 2016-10-21 | 18:02 | -- | -- | -- |  |  |  | 78.0667 | N/A | N/A | N/A | Shutdown availed by Vallur for arresting SF6 gas leakage in Yph CB at their end vide SRLDC code: CR10/461 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 78.0667 | [6 empty] | 744
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | 2016-10-06 | 12:16 | 2016-10-06 | 12:44 | -- | -- | -- |  | 0.46667 |  |  | N/A | N/A | N/A | Tripped at Gajwel end only on DT reciept due to PLCC maloperation at Gajwel(TSTRANSCO) end. Line is holding from HYD(PGCIL) end. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.46667 | 0 | 0 | [6 empty] | 744
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
16 | SR1L16 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | 2016-10-01 | 0:00 | 2016-10-01 | 15:51 | -- | -- | -- |  |  |  | 15.85 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/918 |  | 100 | 744
[5 empty] | -- | 2016-10-05 | 21:58 | 2016-10-06 | 7:04 | -- | -- | -- |  |  |  | 9.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/127 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 24.95 | [6 empty] | 744
17 | SR1L17 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | 2016-10-02 | 2:00 | 2016-10-05 | 12:00 | -- | -- | -- |  |  |  | 82 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/29 |  | 100 | 744
[5 empty] | -- | 2016-10-09 | 20:35 | 2016-10-13 | 9:49 | -- | -- | -- |  |  |  | 85.2333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/237 |  |  | 744
[5 empty] | -- | 2016-10-17 | 0:10 | 2016-10-18 | 12:52 | -- | -- | -- |  |  |  | 36.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/424 |  |  | 744
[5 empty] | -- | 2016-10-24 | 23:05 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 168.9167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/619 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 372.85 | [6 empty] | 744
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | 2016-10-01 | 0:00 | 2016-10-03 | 9:18 | -- | -- | -- |  |  |  | 57.3 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/796 |  | 100 | 744
[5 empty] | -- | 2016-10-30 | 23:21 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 24.65 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/742 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 81.95 | [6 empty] | 744
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | 2016-10-01 | 0:00 | 2016-10-03 | 9:47 | -- | -- | -- |  |  |  | 57.7833 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/922 |  | 100 | 744
[5 empty] | -- | 2016-10-09 | 2:00 | 2016-10-09 | 2:05 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at HYD end. Direct Trip Signal received at NSR end |  |  | 744
[5 empty] | -- | 2016-10-09 | 2:05 | 2016-10-09 | 7:11 | -- | -- | -- |  |  |  | 5.1 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 744
[5 empty] | -- | 2016-10-10 | 2:00 | 2016-10-10 | 2:05 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at HYD end. Direct Trip Signal received at NSR end |  |  | 744
[5 empty] | -- | 2016-10-10 | 2:05 | 2016-10-10 | 7:25 | -- | -- | -- |  |  |  | 5.3333 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 744
[5 empty] | -- | 2016-10-11 | 1:48 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 502.2 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/262 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 570.4167 | [6 empty] | 744
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | 2016-10-13 | 18:13 | 2016-10-13 | 22:12 | -- | -- | -- | 3.9833 |  |  |  | N/A | N/A | N/A | Shutdown availed for replacement of Y-Ph CVT at GWK end vide SRLDC Code CR10/324 |  | 99.4646 | 744
[6 empty] | Sub Total --> | [6 empty] | 3.9833 | 0 | 0 | 0 | [6 empty] | 744
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | 2016-10-01 | 0:00 | 2016-10-03 | 9:29 | -- | -- | -- |  |  |  | 57.4833 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  | 100 | 744
[5 empty] | -- | 2016-10-09 | 0:15 | 2016-10-31 | 11:26 | -- | -- | -- |  |  |  | 539.1833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/219 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 596.6667 | [6 empty] | 744
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2016-10-15 | 10:15 | 2016-10-15 | 18:19 | -- | -- | -- |  |  |  | 8.0667 | N/A | N/A | N/A | Shutdown availed by M/s TSTRANSCO for general maintenance works at their end vide SRLDC code CR10/392 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.0667 | [6 empty] | 744
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | 2016-10-07 | 17:55 | 2016-10-07 | 19:37 | -- | -- | -- | 1.7 |  |  |  | N/A | N/A | N/A | Shutdown availed for attending hotspot on 41289L isolator at NPS end vide SRLDC code CR10/185. |  | 99.7715 | 744
[6 empty] | Sub Total --> | [6 empty] | 1.7 | 0 | 0 | 0 | [6 empty] | 744
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | 2016-10-06 | 8:20 | 2016-10-14 | 13:25 | -- | -- | -- |  |  |  | 197.0833 | -- | -- | -- | Shutdown availed for shifting of Line CVT and LAs for Bus Reactor foundation work under RT2 package at NLR end vide SRLDC code CR10/137. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 197.0833 | [6 empty] | 744
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | 2016-10-13 | 10:48 | 2016-10-13 | 17:59 | -- | -- | -- |  |  |  | 7.1833 | -- | -- | -- | Shutdown availed for shifting of Line CVT and LAs for Bus Reactor foundation work under RT2 package at NLR end vide SRLDC code CR10/312. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.1833 | [6 empty] | 744
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | 2016-10-24 | 20:28 | 2016-10-24 | 20:28 | -- | -- | -- | 7.7618e-12 |  |  |  | -- | -- | -- | Line autoreclosed successfully on B-N fault. FL: 35.86kms, 9.1kA from NLR end |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 7.7618e-12 | 0 | 0 | 0 | [6 empty] | 744
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | 2016-10-31 | 8:35 | 2016-10-31 | 18:22 | -- | -- | -- |  |  |  | 9.7833 | N/A | N/A | N/A | Emergency shutdown availed by M/s TPCIL for attending Rph isolator hotspot at their end vide SRLDC code: CR10/743 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.7833 | [6 empty] | 744
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2016-10-24 | 4:07 | 2016-10-24 | 5:26 | -- | -- | -- | 1.3167 |  |  |  | -- | -- | -- | Shutdown availed by CPDR for isolating L/R to attend oil leakage problem vide SRLDC code: CR10/605 |  | 99.6112 | 744
[5 empty] | -- | 2016-10-27 | 4:41 | 2016-10-27 | 5:38 | -- | -- | -- | 0.95 |  |  |  | N/A | N/A | N/A | Line tripped on malopeartion of L/R Buchholz relay at CPDR end. |  |  | 744
[5 empty] | -- | 2016-10-27 | 5:38 | 2016-10-27 | 8:07 | -- | -- | -- |  | 2.4833 |  |  | N/A | N/A | N/A | Line charging delayed due to CB problem at NTPC/RDM end |  |  | 744
[5 empty] | -- | 2016-10-28 | 22:43 | 2016-10-28 | 23:20 | -- | -- | -- | 0.61667 |  |  |  | N/A | N/A | N/A | Shutdown availed by CPDR for taking L/R into service vide SRLDC code: CR10/721 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 2.8833 | 2.4833 | 0 | 0 | [6 empty] | 744
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | 2016-10-02 | 22:55 | 2016-10-03 | 8:53 | -- | -- | -- |  |  |  | 9.9667 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/42 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.9667 | [6 empty] | 744
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | 2016-10-25 | 6:18 | 2016-10-25 | 19:35 | -- | -- | -- |  |  |  | 13.2833 | -- | -- | -- | Shutdown availed for construction works: LILO arrangement of Vijawada-Gajuwaka Ckt.I at Vemagiri GIS(PG) vide SRLDC code CR10/621 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.2833 | [6 empty] | 744
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2016-10-04 | 23:43 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 648.2833 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR10/100 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 648.2833 | [6 empty] | 744
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | 2016-10-03 | 9:40 | 2016-10-03 | 17:00 | -- | -- | -- | 7.3333 |  |  |  | N/A | N/A | N/A | Shutdown availed for attending oil leakages from radiator banks of Line Reactor at KMM end vide SRLDC code CR10/61 |  | 99.0143 | 744
[6 empty] | Sub Total --> | [6 empty] | 7.3333 | 0 | 0 | 0 | [6 empty] | 744
74 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | 2016-10-19 | 10:11 | 2016-10-19 | 19:55 | -- | -- | -- | 9.7333 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR10/477 |  | 98.6918 | 744
[6 empty] | Sub Total --> | [6 empty] | 9.7333 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
76 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
80 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
81 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
82 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
83 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
87 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
88 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
91 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
92 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
93 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | 2016-10-14 | 11:45 | 2016-10-14 | 12:55 | -- | -- | -- |  |  |  | 1.1667 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for Tan delta measurement at their end vide SRLDC code CR10/361 |  | 100 | 744
[5 empty] | -- | 2016-10-21 | 8:49 | 2016-10-21 | 13:20 | -- | -- | -- |  |  |  | 4.5167 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for attending jumper problem at their end vide SRLDC code CR10/543 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.6833 | [6 empty] | 744
94 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | 2016-10-14 | 13:08 | 2016-10-14 | 14:39 | -- | -- | -- |  |  |  | 1.5167 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for Tan delta measurement at their end vide SRLDC code CR10/370 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.5167 | [6 empty] | 744
95 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | 2016-10-14 | 15:11 | 2016-10-14 | 18:25 | -- | -- | -- |  |  |  | 3.2333 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for Tan delta measurement at their end vide SRLDC code CR10/378 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.2333 | [6 empty] | 744
96 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | 2016-10-17 | 10:12 | 2016-10-17 | 15:07 | -- | -- | -- |  |  |  | 4.9167 | N/A | N/A | N/A | Shutdown availed for 33kV side construction works vide SRLDC code CR10/432 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.9167 | [6 empty] | 744
97 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
98 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
99 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
100 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | 2016-10-19 | 9:47 | 2016-10-19 | 21:29 | -- | -- | -- |  |  |  | 11.7 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for replacement of CT's at their 220kV Switchyard vide SRLDC code CR10/478 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.7 | [6 empty] | 744
101 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
102 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
103 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
106 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
107 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
108 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | 2016-10-08 | 9:19 | 2016-10-08 | 15:33 | -- | -- | -- | 6.2333 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR10/206. |  | 99.1622 | 744
[6 empty] | Sub Total --> | [6 empty] | 6.2333 | 0 | 0 | 0 | [6 empty] | 744
109 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
110 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
111 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
112 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | 2016-10-06 | 10:01 | 2016-10-06 | 14:16 | -- | -- | -- | 4.25 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR10/143. |  | 99.4288 | 744
[6 empty] | Sub Total --> | [6 empty] | 4.25 | 0 | 0 | 0 | [6 empty] | 744
113 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
114 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
115 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
116 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
117 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2016-10-01 | 0:00 | 2016-11-01 | 0:00 | -- | -- | -- |  |  |  | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR08/606 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
119 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
120 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
121 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
122 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
|  |  | Note in type of failure column please indicate following : | [9 empty] | 36.1167 | 2.95 | 0.16667 | 4964.5667
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF OCTOBER 2016
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I FSC at CDP
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
|  | NSR II FSC at CDP | [14 empty] | Shutdown availed for attending oil leakage
27 |  | NSR II FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
|  | FSC-2 at GTY | [14 empty] | Bypassed due to failure of DC Power supply card
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VTPS LR at NLRAP
32 |  | VTPS LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA LR at NLRAP
33 |  | VJA LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VJA
34 |  | NLRAP LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VTPS
35 |  | NLRAP LR at VTPS | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
36 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
37 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
38 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
39 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
40 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
41 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0