## SOP
Standard of Performance data for the month of DECEMBER -2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
Annexure - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2018-12-02 | 22:57 | 2018-12-11 | 10:14 |  |  |  | 0 | 0 | 0 | 203.2833 |  |  |  | H/T on voltage regulation vide SR-81,NL-77 |  | 100 | 744
[6 empty] | 2018-12-16 | 23:59 | 2018-12-19 | 7:04 |  |  |  | 0 | 0 | 0 | 55.0833 |  |  |  | H/T on voltage regulation vide SR-917,NL-847.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 258.3667 | [6 empty] | 744
3 | SR1L03 | KURNOOL(NEW) - KADAPA- I | 203.8 | SR-I | -- | 2018-12-01 | 0:00 | 2018-12-03 | 9:08 |  |  |  | 0 | 0 | 0 | 57.1333 |  |  |  | H/T on voltage regulation vide SR-1143,NL-1050,continued from last month |  | 100 | 744
[5 empty] | -- | 2018-12-11 | 22:29 | 2018-12-12 | 9:04 |  |  |  | 0 | 0 | 0 | 10.5833 |  |  |  | H/T on voltage regulation vide SR-607,NL-592. |  |  | 744
[6 empty] | 2018-12-15 | 21:17 | 2018-12-16 | 11:00 |  |  |  | 0 | 0 | 0 | 13.7167 |  |  |  | H/T on voltage regulation vide SR-883,NL-814.
[6 empty] | 2018-12-24 | 22:57 | 2018-12-26 | 9:33 |  |  |  | 0 | 0 | 0 | 34.6 |  |  |  | H/T on voltage regulation vide SR-1463,NL-1309
[6 empty] | 2018-12-27 | 19:28 | 2018-12-28 | 11:46 |  |  |  | 0 | 0 | 0 | 16.3 |  |  |  | H/T on voltage regulation vide SR-1623,NL-1485 |  |  | 744
[6 empty] | 2018-12-28 | 20:11 | 2018-12-28 | 20:16 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on Over voltage operation at Kadapa end. |  |  | 744
[6 empty] | 2018-12-28 | 20:16 | 2018-12-29 | 8:11 |  |  |  | 0 | 0 | 0 | 11.9167 |  |  |  | Line tripped on Over voltage operation at Kadapa end and kept under LVRD Vide code:SR-1705,NL-1552. |  |  | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 144.25 | [6 empty] | 744
4 | SR1L04 | KURNOOL(NEW) - KADAPA- II | 203.8 | SR-I | -- | 2018-12-07 | 1:27 | 2018-12-08 | 7:58 |  |  |  | 0 | 0 | 0 | 30.5167 |  |  |  | H/T on voltage regulation vide SR-346,NL-339. |  | 100 | 744
[6 empty] | 2018-12-13 | 20:19 | 2018-12-15 | 7:16 |  |  |  | 0 | 0 | 0 | 34.95 |  |  |  | H/T on voltage regulation vide SR-749,NL-692.
[6 empty] | 2018-12-16 | 19:23 | 2018-12-17 | 8:10 |  |  |  | 0 | 0 | 0 | 12.7833 |  |  |  | H/T on voltage regulation vide SR-906,NL-840.
[6 empty] | 2018-12-19 | 22:38 | 2018-12-24 | 10:12 |  |  |  | 0 | 0 | 0 | 107.5667 |  |  |  | H/T on voltage regulation vide SR-1121,NL-1014.
[6 empty] | 2018-12-26 | 19:38 | 2018-12-27 | 9:08 |  |  |  | 0 | 0 | 0 | 13.5 |  |  |  | H/T on voltage regulation vide SR-1556,NL-1408
[6 empty] | 2018-12-29 | 18:15 | 2019-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 53.75 |  |  |  | H/T on voltage regulation vide SR-1756,NL-1597
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 253.0667 | [6 empty] | 744
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2018-12-02 | 0:12 | 2018-12-02 | 9:18 |  |  |  | 0 | 0 | 0 | 9.1 | [5 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.1 | [6 empty] | 744
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[5 empty] | -- | [11 empty] | N/A | N/A | N/A |  |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | [5 empty] | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | 2018-12-12 | 8:25 | 2018-12-12 | 19:15 |  |  |  | 10.8333 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-619. |  | 98.5439 | 744
[6 empty] | Sub Total --> | [6 empty] | 10.8333 | 0 | 0 | 0 | [6 empty] | 744
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | 2018-12-13 | 8:12 | 2018-12-13 | 18:37 |  |  |  | 10.4167 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-696. |  | 98.5999 | 744
[6 empty] | Sub Total --> | [6 empty] | 10.4167 | 0 | 0 | 0 | [6 empty] | 744
16 | SR1L16 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
17 | SR1L17 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | 2018-12-28 | 7:29 | 2018-12-29 | 19:14 |  |  |  | 0 | 0 | 0 | 35.75 |  |  |  | H/T for Madhugiri line Construction works vide SR-1647 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.75 | [6 empty] | 744
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | 2018-12-15 | 10:20 | 2018-12-15 | 19:03 |  |  |  | 0 | 0 | 0 | 8.7167 |  |  |  | S/D Availed by APTRANSCO vide code SR-856 to attend pending Retrofit works |  | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.7167 | [6 empty] | 744
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | 2018-12-06 | 11:11 | 2018-12-06 | 16:58 |  |  |  | 0 | 0 | 0 | 5.7833 |  |  |  | H/T for retrofitting works at Narnoor vide SR-298 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.7833 | [6 empty] | 744
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | 2018-12-11 | 12:08 | 2018-12-11 | 17:10 |  |  |  | 0 | 0 | 0 | 5.0333 |  |  |  | S/D availed by M/s AP Transco vide SR-574. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.0333 | [6 empty] | 744
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | 2018-12-03 | 8:40 | 2018-12-04 | 1:05 |  |  |  | 0 | 0 | 0 | 16.4167 |  |  |  | S/D availed by NCC(SGPL) |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16.4167 | [6 empty] | 744
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | 2018-12-10 | 9:55 | 2018-12-11 | 22:36 |  |  |  | 0 | 0 | 0 | 36.6833 |  |  |  | S/D availed by TPCIL |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 36.6833 | [6 empty] | 744
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | 2018-12-13 | 8:37 | 2018-12-14 | 18:56 |  |  |  | 0 | 0 | 0 | 34.3167 |  |  |  | S/D availed by TPCIL |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 34.3167 | [6 empty] | 744
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | 2018-12-08 | 7:07 | 2018-12-10 | 18:23 |  |  |  | 0 | 0 | 0 | 59.2667 |  |  |  | H/T for line crossing works of Kadapa-Madhugiri D/C line vide SR-418. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 59.2667 | [6 empty] | 744
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | 2018-12-08 | 7:17 | 2018-12-10 | 16:30 |  |  |  | 0 | 0 | 0 | 57.2167 |  |  |  | H/T for line crossing works of Kadapa-Madhugiri D/C line vide SR-419. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 57.2167 | [6 empty] | 744
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | 2018-12-17 | 11:07 | 2018-12-19 | 16:20 |  |  |  | 0 | 0 | 0 | 53.2167 |  |  |  | H/T on request of RTPS for isolator MOM box replacement vide:SR 941 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 53.2167 | [6 empty] | 744
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | 2018-12-20 | 8:29 | 2018-12-20 | 18:40 |  |  |  | 0 | 0 | 0 | 10.1833 |  |  |  | S/D availed by TSTRANSCO for stringing works of 400kV Jangaon -Tippapur line vide SR-1143 |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.1833 | [6 empty] | 744
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | 2018-12-15 | 7:36 | 2018-12-15 | 19:43 |  |  |  | 0 | 0 | 0 | 12.1167 |  |  |  | S/D Availed by TSTRANSCO vide code SR-846 for Stringing work of 400 Kv line from Jangaon SS to Tippapur LISS Loc.No,13/0 to 14/0 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.1167 | [6 empty] | 744
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I |  | 2018-12-15 | 7:33 | 2018-12-15 | 19:46 |  |  |  | 0 | 0 | 0 | 12.2167 |  |  |  | S/D Availed by TSTRANSCO vide code SR-847 for Stringing work f 400 Kv line from Jangaon SS to Tippapur LISS Loc.No,13/0 to 14/0 |  | 100 | 744
[6 empty] | 2018-12-19 | 23:06 | 2018-12-20 | 8:03 |  |  |  | 0 | 0 | 0 | 8.95 |  |  |  | H/T on voltage regulation vide SR-1124. |  |  | 744
[6 empty] | 2018-12-29 | 0:28 | 2018-12-29 | 6:37 |  |  |  | 0 | 0 | 0 | 6.15 |  |  |  | H/T on voltage regulation vide SR-1717 |  |  | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.3167 | [6 empty] | 744
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2018-12-14 | 0:42 | 2018-12-14 | 0:50 |  |  |  | 0 | 0 | 0.13333 | 0 |  |  |  | Line tripped on operation of Over voltage stage 1 at Ramagundam end. |  | 100 | 744
[6 empty] | 2018-12-14 | 0:50 | 2018-12-14 | 6:35 |  |  |  | 0 | 0 | 0 | 5.75 |  |  |  | Line tripped on operation of Over voltage stage 1 at Ramagundam end and kept under LVRD.
[6 empty] | 2018-12-16 | 0:51 | 2018-12-16 | 1:00 |  |  |  | 0 | 0 | 0.15 | 0 |  |  |  | Tripped on over voltage, kept out under voltage regulation vide code SR-890
[6 empty] | 2018-12-16 | 1:00 | 2018-12-17 | 18:24 |  |  |  | 0 | 0 | 0 | 41.4 |  |  |  | Tripped on over voltage, kept out under voltage regulation vide code SR-890
[6 empty] | 2018-12-22 | 22:40 | 2018-12-22 | 22:45 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped on over voltage, kept out under voltage regulation vide code SR-1362
[6 empty] | 2018-12-22 | 22:45 | 2018-12-23 | 7:08 |  |  |  | 0 | 0 | 0 | 8.3833 |  |  |  | Tripped on over voltage, kept out under voltage regulation vide code SR-1362
[6 empty] | 2018-12-24 | 22:31 | 2018-12-24 | 22:36 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped on over voltage, kept out under voltage regulation vide code SR-1464
[6 empty] | 2018-12-24 | 22:36 | 2018-12-25 | 5:30 |  |  |  | 0 | 0 | 0 | 6.9 |  |  |  | Tripped on over voltage, kept out under voltage regulation vide code SR-1464
[6 empty] | 2018-12-27 | 6:18 | 2018-12-27 | 17:27 |  |  |  | 0 | 0 | 0 | 11.15 |  |  |  | S/D availed by M/s TSTransco for stringing works vide code SR-1567
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.45 | 73.5833 | [6 empty] | 744
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | 2018-12-01 | 6:29 | 2018-12-02 | 19:59 |  |  |  | 0 | 0 | 0 | 37.5 |  |  |  | S/D availed by TSTRANSCO for line crossing works vide SR-03 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 37.5 | [6 empty] | 744
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | 2018-12-01 | 6:31 | 2018-12-02 | 20:23 |  |  |  | 0 | 0 | 0 | 37.8667 |  |  |  | S/D availed by TSTRANSCO for line crossing works vide SR-04 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 37.8667 | [6 empty] | 744
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | 2018-12-05 | 22:54 | 2018-12-07 | 14:21 |  |  |  | 0 | 0 | 0 | 39.45 |  |  |  | H/T on voltage regulation vide SR-279 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 39.45 | [6 empty] | 744
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2018-12-20 | 8:39 | 2018-12-20 | 19:22 |  |  |  | 10.7167 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-1145 |  | 98.5596 | 744
[6 empty] | Sub Total --> | [6 empty] | 10.7167 | 0 | 0 | 0 | [6 empty] | 744
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2018-12-13 | 21:48 | 2018-12-13 | 21:55 |  |  |  | 0 | 0 | 0.11667 | 0 |  |  |  | Line tripped on operation of Over voltage stage 1 at Vijayawada end. |  | 98.3308 | 744
[6 empty] | 2018-12-13 | 21:55 | 2018-12-14 | 6:49 |  |  |  | 0 | 0 | 0 | 8.9 |  |  |  | Line tripped on operation of Over voltage stage 1 at Vijayawada end and kept under LVRD.
[6 empty] | 2018-12-19 | 9:26 | 2018-12-19 | 21:51 |  |  |  | 12.4167 | 0 | 0 | 0 |  |  |  | H/T for replacement of R-Ph 41089R reactor isolator stack vide SR-1061.
744
[6 empty] | Sub Total --> | [6 empty] | 12.4167 | 0 | 0.11667 | 8.9 | [6 empty] | 744
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | 2018-12-21 | 8:40 | 2018-12-21 | 17:59 |  |  |  | 9.3167 | 0 | 0 | 0 |  |  |  | H/T for attending pending line defects vide SR-1242 |  | 98.7478 | 744
[6 empty] | Sub Total --> | [6 empty] | 9.3167 | 0 | 0 | 0 | [6 empty] | 744
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2018-12-04 | 3:55 | 2018-12-04 | 3:55 |  |  |  | 1.9402e-11 | 0 | 0 | 0 |  |  |  | Line auto reclosed successfully on RN fault Dist:29KM(M2),36KM(M1) ,FC:7KA from VJA. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 1.9402e-11 | 0 | 0 | 0 | [6 empty] | 744
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | 2018-12-12 | 9:17 | 2018-12-12 | 17:18 |  |  |  | 0 | 0 | 0 | 8.0167 |  |  |  | S/D availed by M/s VTPS vide code SR-624. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.0167 | [6 empty] | 744
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
74 | SR1L74 | VEMAGIRI(PG) - GAZUWAKA | 165.454 | SR-I |  | 2018-12-11 | 12:55 | 2018-12-11 | 13:16 |  |  |  | 0.35 | 0 | 0 | 0 |  |  |  | Line tripped on R-N fault. (GWK End: 120KM, 3.5kA & VMG End: 57KM, 5.09kA) |  | 99.5721 | 744
[6 empty] | 2018-12-12 | 13:53 | 2018-12-12 | 13:53 |  |  |  | 2.7165e-11 | 0 | 0 | 0 |  |  |  | Line Autoreclosed sucessfully on Y-N fault. (VMG End: 60.8KM, 3.99kA ; GWK: 147.8KM, 3.32kA)
[6 empty] | 2018-12-21 | 12:20 | 2018-12-21 | 15:10 |  |  |  | 2.8333 | 0 | 0 | 0 |  |  |  | H/T for attending hotspot at Vemagiri end vide SR-1266
[6 empty] | Sub Total --> | [6 empty] | 3.1833 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L75 | VIJAYAWADA - VEMAGIRI(PG) | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
76 | SR1L76 | MAHESHWARAM-KURNOOL AP | 174.996 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1L77 | NiZAMABAD-DICHPALLY 1 | 4.428 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1L78 | NiZAMABAD-DICHPALLY 2 | 4.428 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1L79 | NIZAMABAD-MAHESHWARAM 1 | 243.059 | SR-I |  | 2018-12-01 | 0:00 | 2018-12-03 | 8:36 |  |  |  | 0 | 0 | 0 | 56.6 |  |  |  | H/T on voltage regulation vide SR-1550,NL-1481,continued from last month |  | 100 | 744
[6 empty] | 2018-12-04 | 21:35 | 2018-12-05 | 6:54 |  |  |  | 0 | 0 | 0 | 9.3167 |  |  |  | H/T on voltage regulation vide SR-219,NL-209.
[6 empty] | 2018-12-06 | 10:20 | 2018-12-07 | 6:51 |  |  |  | 0 | 0 | 0 | 20.5167 |  |  |  | H/T on voltage regulation vide SR-345,NL-336.
[6 empty] | 2018-12-08 | 22:05 | 2018-12-09 | 8:17 |  |  |  | 0 | 0 | 0 | 10.2 |  |  |  | H/T on voltage regulation vide SR-454,NL-448.
[6 empty] | 2018-12-11 | 22:32 | 2018-12-12 | 8:40 |  |  |  | 0 | 0 | 0 | 10.1333 |  |  |  | H/T on voltage regulation vide SR-608,NL-593.
[6 empty] | 2018-12-15 | 20:51 | 2018-12-16 | 8:32 |  |  |  | 0 | 0 | 0 | 11.6833 |  |  |  | H/T on voltage regulation vide SR-882,NL-812.
[6 empty] | 2018-12-17 | 22:00 | 2018-12-18 | 6:18 |  |  |  | 0 | 0 | 0 | 8.3 |  |  |  | H/T on voltage regulation vide SR-960 ,NL-891
[6 empty] | 2018-12-19 | 22:41 | 2018-12-20 | 7:57 |  |  |  | 0 | 0 | 0 | 9.2667 |  |  |  | H/T on voltage regulation vide SR-1122,NL-1015.
[6 empty] | 2018-12-20 | 23:48 | 2018-12-21 | 7:16 |  |  |  | 0 | 0 | 0 | 7.4667 |  |  |  | H/T on voltage regulation vide SR-1222,NL-1084
[6 empty] | 2018-12-21 | 23:19 | 2018-12-22 | 7:20 |  |  |  | 0 | 0 | 0 | 8.0167 |  |  |  | H/T on voltage regulation vide SR-1301,NL-1147
[6 empty] | 2018-12-23 | 21:35 | 2018-12-24 | 6:44 |  |  |  | 0 | 0 | 0 | 9.15 |  |  |  | H/T on voltage regulation vide SR-1394,NL-1243
[6 empty] | 2018-12-27 | 21:06 | 2018-12-28 | 7:16 |  |  |  | 0 | 0 | 0 | 10.1667 |  |  |  | H/T on voltage regulation vide SR-1626,NL-1489
[6 empty] | 2018-12-29 | 20:09 | 2018-12-31 | 6:49 |  |  |  | 0 | 0 | 0 | 34.6667 |  |  |  | H/T on voltage regulation vide SR-1762,NL-1608
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 205.4833 | [6 empty] | 744
80 | SR1L80 | NIZAMABAD-MAHESHWARAM 2 | 243.059 | SR-I |  | 2018-12-04 | 1:14 | 2018-12-04 | 8:04 |  |  |  | 0 | 0 | 0 | 6.8333 |  |  |  | H/T on voltage regulation vide SR-148,NL-140 |  | 100 | 744
[6 empty] | 2018-12-05 | 23:28 | 2018-12-06 | 6:48 |  |  |  | 0 | 0 | 0 | 7.3333 |  |  |  | H/T on voltage regulation vide SR-280,NL-275.
[6 empty] | 2018-12-07 | 21:06 | 2018-12-08 | 8:18 |  |  |  | 0 | 0 | 0 | 11.2 |  |  |  | H/T on voltage regulation vide SR-406,NL-390.
[6 empty] | 2018-12-09 | 21:01 | 2018-12-10 | 6:55 |  |  |  | 0 | 0 | 0 | 9.9 |  |  |  | H/T on voltage regulation vide SR-482,NL-481
[6 empty] | 2018-12-11 | 1:55 | 2018-12-11 | 6:29 |  |  |  | 0 | 0 | 0 | 4.5667 |  |  |  | H/T on voltage regulation vide SR-551,NL-541
[6 empty] | 2018-12-12 | 23:02 | 2018-12-13 | 0:00 |  |  |  | 0 | 0 | 0 | 0.96667 |  |  |  | H/T on voltage regulation vide SR-680,NL-644.
[6 empty] | 2018-12-14 | 0:54 | 2018-12-14 | 6:47 |  |  |  | 0 | 0 | 0 | 5.8833 |  |  |  | H/T on voltage regulation vide SR-767,NL-708.
[6 empty] | 2018-12-14 | 20:23 | 2018-12-15 | 6:34 |  |  |  | 0 | 0 | 0 | 10.1833 |  |  |  | H/T on voltage regulation vide SR-832,NL-765.
[6 empty] | 2018-12-16 | 21:02 | 2018-12-17 | 6:23 |  |  |  | 0 | 0 | 0 | 9.35 |  |  |  | H/T on voltage regulation vide SR-911,NL-845.
[6 empty] | 2018-12-18 | 21:06 | 2018-12-19 | 6:17 |  |  |  | 0 | 0 | 0 | 9.1833 |  |  |  | H/T on voltage regulation vide SR-1034,NL-945.
[6 empty] | 2018-12-22 | 22:54 | 2018-12-23 | 7:06 |  |  |  | 0 | 0 | 0 | 8.2 |  |  |  | H/T on voltage regulation vide SR-1359,NL-1212
[6 empty] | 2018-12-24 | 22:37 | 2018-12-26 | 9:13 |  |  |  | 0 | 0 | 0 | 34.6 |  |  |  | H/T on voltage regulation vide SR-1460,NL-1307
[6 empty] | 2018-12-26 | 22:52 | 2018-12-27 | 6:49 |  |  |  | 0 | 0 | 0 | 7.95 |  |  |  | H/T on voltage regulation vide SR-1562,NL-1420
[6 empty] | 2018-12-28 | 21:49 | 2018-12-29 | 7:20 |  |  |  | 0 | 0 | 0 | 9.5167 |  |  |  | H/T on voltage regulation vide SR-1708,NL-1556
[6 empty] | 2018-12-31 | 20:59 | 2019-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 3.0167 |  |  |  | H/T on voltage regulation vide SR-1850,NL-1717
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 138.6833 | [6 empty] | 744
81 | SR1L81 | NIZAMABAD-WARDHA 1 | 291.2 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
82 | SR1L82 | NIZAMABAD-WARDHA 2 | 291.2 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
83 | SR1L83 | VIJAYAWADA-VEMAGIRI PG 1 | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1L84 | VIJAYAWADA-VEMAGIRI PG 2 | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1L85 | VIJAYAWADA-VEMAGIRI PG 3 | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1L86 | KADAPA- CHITTOOR | 147.14 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
87 | SR1L87 | VEMAGIRI PG - SIMHADRI-I | 180.98 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
88 | SR1L88 | VEMAGIRI PG - SIMHADRI-II | 180.98 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1L89 | VEMAGIRI PG - VEMAGIRI AP - I | 38.41 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1L90 | VEMAGIRI PG - VEMAGIRI AP - II | 38.41 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
91 | SR1L91 | 400KV KADAPA - NP KUNTA - II | 68.69 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
92 | SR1L92 | 400KV KADAPA - NP KUNTA - III | 68.69 | SR-I |  | 2018-12-01 | 0:00 | 2018-12-22 | 17:59 |  |  |  | 0 | 0 | 0 | 521.9833 |  |  |  | H/T for bay extension works of kadapa-madhugiri 1&2 vide code SR1247,continued from last month |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 521.9833 | [6 empty] | 744
93 | SR1L93 | 765KV KURNOOL-KADAPA 1 | 203.89 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR1L94 | 765KV KURNOOL-KADAPA 2 | 203.89 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR1L93 | 765KV KADAPA-THIRUVALAM 1 | 245.76 | SR-I |  | 2018-12-01 | 0:00 | 2018-12-07 | 7:25 |  |  |  | 0 | 0 | 0 | 151.4167 |  |  |  | H/T on voltage regulation vide SR-1551,NL-1482,continued from last month |  | 100 | 744
[6 empty] | 2018-12-08 | 21:27 | 2018-12-10 | 9:30 |  |  |  | 0 | 0 | 0 | 36.05 |  |  |  | H/T on voltage regulation vide SR-452,NL-446.
[6 empty] | 2018-12-10 | 21:24 | 2018-12-18 | 7:15 |  |  |  | 0 | 0 | 0 | 177.85 |  |  |  | H/T on voltage regulation vide SR-544,NL-537
[6 empty] | 2018-12-20 | 21:30 | 2018-12-21 | 9:10 |  |  |  | 0 | 0 | 0 | 11.6667 |  |  |  | H/T on voltage regulation vide SR-1211,NL-1078
[6 empty] | 2018-12-28 | 20:36 | 2019-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 75.4 |  |  |  | H/T on voltage regulation vide SR-1706,NL-1553
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 452.3833
95 | SR1L94 | 765KV KADAPA-THIRUVALAM 2 | 245.76 | SR-I |  | 2018-12-07 | 21:25 | 2018-12-08 | 9:38 |  |  |  | 0 | 0 | 0 | 12.2167 |  |  |  | H/T on voltage regulation vide SR-407,NL-391. |  | 100 | 744
[6 empty] | 2018-12-18 | 20:10 | 2018-12-20 | 9:12 |  |  |  | 0 | 0 | 0 | 37.0333 |  |  |  | H/T on voltage regulation vide SR-1033,NL-940.
[6 empty] | 2018-12-21 | 18:13 | 2018-12-28 | 11:05 |  |  |  | 0 | 0 | 0 | 160.8667 |  |  |  | H/T on voltage regulation vide SR-1288,NL-1130
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 210.1167
96 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | 2018-12-18 | 10:53 | 2018-12-18 | 13:33 |  |  |  | 0 | 0 | 0 | 2.6667 |  |  |  | H/T for CSD tuning works vide SR-996, NL-923. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.6667 | [6 empty] | 744
97 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | 2018-12-19 | 10:00 | 2018-12-19 | 17:33 |  |  |  | 0 | 0 | 0 | 7.55 |  |  |  | H/T for CSD tuning works vide SR-1062, NL-974. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.55 | [6 empty] | 744
98 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
99 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
100 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
101 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
102 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
103 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
104 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
106 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
107 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
108 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
109 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
110 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- | 2018-12-20 | 11:46 | 2018-12-20 | 14:56 |  |  |  | 0 | 0 | 0 | 3.1667 |  |  |  | S/D availed by TSTRANSCO for attending hotspots vide SR-1166 |  | 98.7007 | 744
[6 empty] | 2018-12-04 | 10:09 | 2018-12-04 | 19:49 |  |  |  | 9.6667 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR12/159.
[6 empty] | Sub Total --> | [6 empty] | 9.6667 | 0 | 0 | 3.1667 | [6 empty] | 744
111 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
112 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
113 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
114 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
115 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | 2018-12-15 | 10:18 | 2018-12-15 | 12:34 |  |  |  | 0 | 0 | 0 | 2.2667 |  |  |  | S/D Availed by APTRANSCO vide code SR-857. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.2667 | [6 empty] | 744
116 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | 2018-12-15 | 13:40 | 2018-12-15 | 16:05 |  |  |  | 0 | 0 | 0 | 2.4167 |  |  |  | S/D Availed by APTRANSCO vide code SR-868. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.4167 | [6 empty] | 744
117 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | 2018-12-11 | 11:18 | 2018-12-11 | 12:42 |  |  |  | 1.4 | 0 | 0 | 0 |  |  |  | Emergency shutdown availed for attending oil leakage in R-Ph HV bushing vide SR-573. |  | 99.8118 | 744
[6 empty] | Sub Total --> | [6 empty] | 1.4 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
119 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
120 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
121 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
122 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
103 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
106 | SR1T30 | VEMAGIRI ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
107 | SR1T31 | VEMAGIRI ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
108 | SR1T32 | NIZAMABAD ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
109 | SR1T33 | NIZAMABAD ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
110 | SR1T34 | MAHESHWRAM ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
111 | SR1T35 | MAHESHWARAM ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
112 | SR1T36 | HYDERABAD ICT IV | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
113 | SR1T37 | GOOTY ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
114 | SR1T38 | KHAMMAM ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
115 | SR1T39 | WARANGAL ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
116 | SR1T40 | SRIKAKULAM 765/400kV ICT I | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
117 | SR1T41 | SRIKAKULAM 765/400kV ICT II | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1T42 | VIJAYAWADA ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1T42 | KADAPA ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1T42 | KADAPA GIS ICT I | 1500 | SR-I | -- | 2018-12-20 | 9:42 | 2018-12-20 | 23:08 |  |  |  | 0 | 0 | 0 | 13.4333 |  |  |  | H/T for Commissioning of CSD vide SR-1151, NL-1131 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.4333 | [6 empty] | 744
118 | SR1T42 | KADAPA GIS ICT II | 1500 | SR-I | -- | 2018-12-24 | 9:38 | 2018-12-24 | 18:54 |  |  |  | 0 | 0 | 0 | 9.2667 |  |  |  | H/T for CSD commissioning works vide SR-1419,NL-1269 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.2667 | [6 empty] | 744
119 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | 2018-12-08 | 10:11 | 2018-12-08 | 15:11 |  |  |  | 0 | 0 | 0 | 5 |  |  |  | H/T for damper fixing works in Reactor CB vide SR-432, NL-424 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5 | [6 empty] | 744
120 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [16 empty] | 744
121 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
122 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | [5 empty] | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
125 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
126 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
127 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
128 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
129 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
130 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
131 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
132 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
133 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
134 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
135 | SR1R17 | 765 KV SRIKAKULAM-VEMAGIRI 2 LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
136 | SR1R18 | 765 KV SRIKAKULAM-VEMAGIRI 1 LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
137 | SR1R19 | 330MVAR BUS REACTOR at SKLM | 330 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
138 | SR1R20 | VEMAGIRI 240MVAR BUS REACTOR-I | 240 | SR-I | -- | 2018-12-10 | 10:38 | 2018-12-13 | 21:23 |  |  |  | 0 | 0 | 0 | 82.75 |  |  |  | H/T on voltage regulation vide SR-516,NL-509 |  | 100 | 744
[6 empty] | 2018-12-22 | 7:07 | 2018-12-31 | 17:56 |  |  |  | 0 | 0 | 0 | 226.8167 |  |  |  | H/T on voltage regulation vide SR-1309,NL-1158
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 309.5667 | [6 empty] | 744
139 | SR1R21 | VEMAGIRI 240MVAR BUS REACTOR-II | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
140 | SR1R22 | VEMAGIRI 80MVAR BUS REACTOR | 80 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
141 | SR1R23 | MAHESHWARAM BUS REACTOR 1 | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
142 | SR1R24 | POLE-2 EAST REACTOR | 125 | SR-I | -- | 2018-12-01 | 0:00 | 2019-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 744 |  |  |  | H/T for voltage regulation vide code SR 757,continued from last month |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744 | [6 empty] | 744
143 | SR1R25 | VIJAYWADA BUS REACTOR 4 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
144 | SR1R26 | NAGARJUNA SAGAR BUS REACTOR II | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
145 | SR1R27 | WARDHA 1 LR AT NIZAMABAD | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
146 | SR1R28 | WARDHA 2 LR AT NIZAMABAD | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
147 | SR1R29 | SOLAPUR - RAICHUR -I LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
148 | SR1R30 | ANGUL - SRIKAKULAM - I LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
149 | SR1R31 | ANGUL - SRIKAKULAM - II LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
150 | SR1R32 | WARDHA - NIZAMABAD - I L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
151 | SR1R33 | WARDHA - NIZAMABAD - II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
152 | SR1R34 | HYDERABAD - GAJWEL LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
153 | SR1R35 | NELLORE - THIRUVALAM - I LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
154 | SR1R36 | NELLORE - THIRUVALAM - II LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
155 | SR1R37 | GOOTY - KURNOOL LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
156 | SR1R38 | GOOTY BUS REACTOR 2 | 125 | SR-I | -- | 2018-12-22 | 9:45 | 2018-12-23 | 21:31 |  |  |  | 0 | 0 | 0 | 35.7667 |  |  |  | H/T on voltage regulation vide SR-1319 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.7667 | [6 empty] | 744
157 | SR1R39 | NELLORE BUS REACTOR 2 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
158 | SR1R40 | NIZAMABAD 765KV BUS REACTOR 1 | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
159 | SR1R41 | NPS-GOOTY-1 L/R | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
160 | SR1R42 | NPS-GOOTY-2 L/R | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
161 | SR1R43 | SRIKAKULAM-ANGUL 1 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
162 | SR1R44 | SRIKAKULAM-ANGUL 2 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
163 | SR1R45 | VEMAGIRI-SRIKAKULAM1 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
164 | SR1R46 | VEMAGIRI-SRIKAKULAM2 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
165 | SR1R47 | VIJAYWADA BUS REACTOR 3 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
166 | SR1R48 | NIZAMABAD-WARDHA -I L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
167 | SR1R49 | NIZAMABAD-WARDHA -II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
168 | SR1R50 | MAHESHWARAM BUS REACTOR -II | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
169 | SR1R51 | MAHESHWARAM-NIZAMABAD-I L/R | 240 | SR-I | -- | 2018-12-01 | 0:00 | 2018-12-02 | 13:04 |  |  |  | 0 | 0 | 0 | 37.0667 |  |  |  | H/T for corona bell replacement works vide code SR1501,NL1449,continued from last month |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 37.0667 | [6 empty] | 744
170 | SR1R52 | MAHESHWARAM-NIZAMABAD-II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
171 | SR1R38 | NIZAMABAD-MAHESHWARAM I L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
172 | SR1R53 | NIZAMABAD-MAHESHWARAM II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
173 | SR1R54 | JEYPORE LR-1 AT GAJUWAKA | 80 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R55 | JEYPORE LR-2 AT GAJUWAKA | 80 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R56 | KURNOOL BUS REACTOR 2 | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R56 | KADAPA BUS REACTOR 2 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R56 | RAICHUR(NEW) BUS REACTOR 2 | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R56 | NELLORE PS BUS REACTOR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
175 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
176 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
177 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
178 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
179 | SR1S1 | STATCOM AT NPKUNTA | 200 | SR-I | -- | 2018-12-06 | 9:45 | 2018-12-08 | 0:17 |  |  |  | 0 | 0 | 0 | 38.5333 |  |  |  | H/T for STACOM tunning works vide SR-297 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 38.5333 | [6 empty] | 744
|  |  | Note in type of failure column please indicate following : | [9 empty] | 67.95 | 0 | 0.65 | 3971.4667
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse