## SOP
Standard of Performance data for the month of APRIL -2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2018-09-01 | 0:00 | 2018-09-03 | 15:13 | [6 empty] | 63.2167 |  |  |  | H/T under Voltage regulation vide code SR1316,Nl874,continued from last month | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2018-09-13 | 3:09 | 2018-09-25 | 9:09 | [6 empty] | 294 |  |  |  | H/T for Voltage regulation vide code SR520,NL451
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 357.2167 | [6 empty] | 744
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2018-09-25 | 22:13 | 2018-10-01 | 0:00 | [6 empty] | 121.7833 |  |  |  | H/T under Voltage regulation, SR09/1132,NL-879 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 121.7833 | [6 empty] | 744
3 | SR1L03 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2018-09-01 | 0:00 | 2018-09-10 | 18:39 | [6 empty] | 234.65 |  |  |  | Line Kept under Voltage regulation vide code SR1057,continued from last month |  | 100 | 744
[5 empty] | -- | 2018-09-24 | 20:09 | 2018-10-01 | 0:00 | [6 empty] | 147.85 |  |  |  | H/T under Voltage regulation, SR09/1046,NL-824 |  |  | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 382.5 | [6 empty] | 744
4 | SR1L04 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2018-09-10 | 18:46 | 2018-09-24 | 11:28 | [6 empty] | 328.7 |  |  |  | H/T for Voltage regulation vide code SR401,NL367 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 328.7 | [6 empty] | 744
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | 2018-09-25 | 8:21 | 2018-09-26 | 15:03 | [6 empty] | 30.7 |  |  |  | H/T under Voltage regulation, SR09/1052,NL-837 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 30.7 | [6 empty] | 744
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2018-09-26 | 18:57 | 2018-09-26 | 18:57 |  |  |  | -4.6565e-11 | [6 empty] | Autoreclosed sucessfully on B-N faultRCN: 118.3KM, 3.4kA ; KLN: M1: 2.67KM, 18kA & M2: 2.7KM, 18.2kA |  | 100 | 744
[6 empty] | 2018-09-02 | 17:57 | 2018-09-12 | 10:44 | [6 empty] | 232.7833 |  |  |  | H/T for Voltage Regulation vide code SR66,NL61
[6 empty] | 2018-09-17 | 1:48 | 2018-09-17 | 6:56 | [6 empty] | 5.1333 |  |  |  | H/T on Voltage regulation vide code SR636,NL562
[6 empty] | 2018-09-17 | 22:22 | 2018-09-18 | 6:56 | [6 empty] | 8.5667 |  |  |  | H/T on Voltage regulation vide code SR701,NL599
[6 empty] | 2018-09-17 | 22:22 | 2018-09-19 | 9:18 | [6 empty] | 34.9333 |  |  |  | H/T under Voltage regulation, SR09/703,NL-600
[6 empty] | 2018-09-21 | 21:54 | 2018-09-22 | 7:54 | [6 empty] | 10 |  |  |  | H/T under Voltage regulation, SR09/924,NL-734.
[6 empty] | 2018-09-23 | 20:20 | 2018-09-25 | 8:10 | [6 empty] | 35.8333 |  |  |  | H/T under Voltage regulation, SR09/1004,NL-789
[6 empty] | Sub Total --> | [6 empty] | -4.6565e-11 | 0 | 0 | 327.25 | [6 empty] | 744
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[5 empty] | -- | [11 empty] | N/A | N/A | N/A |  |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | [5 empty] | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | 2018-09-01 | 8:37 | 2018-09-01 | 20:07 | [6 empty] | 11.5 |  |  |  | H/T for Main2 relay retrofitting works under ADD CAP vide code SR06 |  | 100 | 744
[6 empty] | 2018-09-03 | 11:23 | 2018-09-03 | 12:45 |  |  |  | 1.3667 | [6 empty] | Line tripped on through fault on operation of DEF protection operation at Gooty end
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.5 | [6 empty] | 744
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | 2018-09-25 | 3:42 | 2018-09-25 | 3:47 | [5 empty] | 0.083333 |  |  |  |  | Tripped on Over Voltage at Gooty end.DT received at Raichur end |  | 100 | 744
[6 empty] | 2018-09-26 | 3:47 | 2018-09-26 | 7:53 | [6 empty] | 4.1 |  |  |  | Kept out on Voltage regulation,SR/1137
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 4.1 | [6 empty] | 744
16 | SR1L16 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
17 | SR1L17 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | [16 empty] | 100 | 744
[5 empty] | -- | [17 empty] | 744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | 2018-09-01 | 0:00 | 2018-09-03 | 9:40 | [6 empty] | 57.6667 |  |  |  | H/T under Voltage regulation, SR 08/657,continued from last month |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 57.6667 | [6 empty] | 744
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | 2018-09-17 | 14:39 | 2018-09-17 | 23:41 |  |  |  | 9.0333 | [6 empty] | H/T for CT replacement works vide code SR670 |  | 98.7858 | 744
[5 empty] | -- | 2018-09-26 | 22:37 | 2018-09-26 | 22:37 |  |  |  | 3.1045e-11 | [6 empty] | A/R successful on R-N fault,FC-9.948 KA,FL-28.265 KM from KMM end and FC-4.539 KA & FL-84.1KM from VJA end. |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 9.0333 | 0 | 0 | 0 | [6 empty] | 744
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | 2018-09-30 | 17:07 | 2018-09-30 | 17:07 |  |  |  | -8.5372e-11 | [6 empty] | line AR successful on B-N fault. Fault Details:at KLN end: M1:7.105KM,11.12KA;M2:3.522Km,Fc-6.107KA;Nanoor end: M1-1.37Km,19.90KA;M2:1.388KM,19.23KA |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | -8.5372e-11 | 0 | 0 | 0 | [6 empty] | 744
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | 2018-09-26 | 19:28 | 2018-09-26 | 19:28 |  |  |  | 6.5971e-11 | [6 empty] | Autoreclosed sucessfully on B-N fault M1: 4.09KM, 16.3kA ; M2: 4.23kM, 9.3kA at KLN and at KLN(AP) M1:5.789KM,11.90KA. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 6.5971e-11 | 0 | 0 | 0 | [6 empty] | 744
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | [16 empty] | 100 | 744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | [16 empty] | 100 | 744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | 2018-09-15 | 13:51 | 2018-09-15 | 15:03 |  |  |  | 1.2 | [6 empty] | Tripped on R-N fault. GTY end: FD: 251.20KM, FC:1.432kA; NPS end: FD: 40.06KM, FC:8.68kA |  | 99.8387 | 744
[6 empty] | 2018-09-25 | 14:30 | 2018-09-25 | 14:30 |  |  |  | -5.8207e-11 | [6 empty] | AR Successful on R-N fault. At GTY end: Dist:66.329KM,FC-5.3KA;NPS end: Dist-229.59KM,FC-2.691KA
[6 empty] | 2018-09-26 | 15:14 | 2018-09-26 | 15:14 |  |  |  | 6.2089e-11 | [6 empty] | Autoreclosed sucessfully on R-N fault ,GTY End: M-1: 38.58KM, 7.56kA & M-2: 39.28KM, 7.78kA ; NPS End: 254.6KM, 2.573kA
[6 empty] | Sub Total --> | [6 empty] | 1.2 | 0 | 0 | 0 | [6 empty] | 744
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | 2018-09-16 | 0:41 | 2018-09-16 | 9:02 |  |  |  | 8.35 | [6 empty] | Tripped on R-N fault,SPDR end: M1:17.2KM,12.2KA;M2:17.7KM,13.9KA; NLR end: M1:150.3KM,M2:147.7Km,.99KA.Line decapped in SR-2 portion |  | 98.8777 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 8.35 | 0 | 0 | 0 | [6 empty] | 744
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | 2018-09-21 | 16:44 | 2018-09-21 | 17:29 | [5 empty] | 0.75 |  |  |  |  | Line tripped due to O/V at KDP end & DT received at NSR end. |  | 100 | 744
[6 empty] | 2018-09-29 | 3:29 | 2018-10-01 | 0:00 | [6 empty] | 44.5167 |  |  |  | H/T for Voltage regulation vide code SR1353
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.75 | 44.5167 | [6 empty] | 744
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | 2018-09-28 | 8:42 | 2018-09-28 | 20:47 | [6 empty] | 12.0833 |  |  |  | H/T for HVDC raigarh-Pugulur line construction works vide code SR1289 |  | 100 | 744
[6 empty] | 2018-09-29 | 8:03 | 2018-09-29 | 16:53 | [6 empty] | 8.8333 |  |  |  | H/T for HVDC raigarh-Pugulur line construction works vide code SR1358
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 20.9167 | [6 empty] | 744
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | 2018-09-27 | 16:55 | 2018-09-27 | 16:55 |  |  |  | -3.8806e-11 | [6 empty] | Autoreclosed sucessfully on B-N fault ,NSR End: M1: 154.4KM, 2.255kA & M2: 154.7KM, 2.211kA ; VLR End: 17.9KM, 10.03kA. |  | 100 | 744
[6 empty] | 2018-09-27 | 22:13 | 2018-09-27 | 22:13 |  |  |  | -5.0445e-11 | [6 empty] | Autoreclosed sucessfully on B-N fault ,NSR End: M1: 164.08KM, 2.52kA & M2: 165.7.7KM, 2.54kA ; VLR End: M1:10.25KM, 13.07kA & M2: 10.4KM, 13.09kA. |  |  | 744
744
[6 empty] | Sub Total --> | [6 empty] | -8.9251e-11 | 0 | 0 | 0 | [6 empty] | 744
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | 2018-09-26 | 21:33 | 2018-09-26 | 22:23 | [5 empty] | 0.83333 | 0 |  |  |  | Tripped on over voltage at Raichur end. |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.83333 | 0 | [6 empty] | 744
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[5 empty] | -- | [17 empty] | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | 2018-09-09 | 3:23 | 2018-09-09 | 3:28 |  |  |  |  | 0.083333 | 0 |  |  |  |  | line AR successful on B-N fault at Hyderabad end. Tripped at Ramagundam only. Fault Details: M1:151.1Km,FC-3KA;M2:149.1Km,Fc-3.043KA;RDM end: M2-14.1Km,FC-16KA |  | 100 | 744
[6 empty] | 2018-09-09 | 3:28 | 2018-09-09 | 7:17 | [6 empty] | 3.8167 |  |  |  | Line Kept under Voltage regulation vide code SR345
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.083333 | 0 | 3.8167 | [6 empty] | 744
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | [17 empty] | 100 | 744
744
744
744
744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2018-09-26 | 8:26 | 2018-09-26 | 20:10 | [6 empty] | 11.7333 |  |  |  | Shutdown availed by TS Transco ,SR/1210 |  | 100 | 744
[6 empty] | 2018-09-26 | 18:10 | 2018-09-26 | 21:36 | [5 empty] | 3.4333 |  |  |  |  | Tripped on O/V at Malkaram end |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3.4333 | 11.7333 | [6 empty] | 744
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | 2018-09-02 | 20:55 | 2018-09-02 | 21:45 |  |  |  | 0.83333 | [6 empty] | Line tripped on Y-B fault. NSR end: FC-8.1KA,FL-57.9KM; RDM end: FC-2.8KA,FL-194KM |  | 99.888 | 744
[6 empty] | Sub Total --> | [6 empty] | 0.83333 | 0 | 0 | 0 | [6 empty] | 744
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | 2018-09-30 | 23:31 | 2018-09-30 | 23:31 |  |  |  | -3.8796e-12 | [6 empty] | line AR successful on Y-N fault. Fault Details: NSR end: M1:30.3KM,8.0KA & M2:30.459KM,8.27KA; |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2018-09-11 | 15:26 | 2018-09-11 | 17:46 |  |  |  | 2.3333 | [6 empty] | Tripped on B-N fault; VJA:FL-340KM,1.2KA; NLR end: 11.93KM,17.3KA |  | 99.6864 | 744
[6 empty] | Sub Total --> | [6 empty] | 2.3333 | 0 | 0 | 0 | [6 empty] | 744
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | [16 empty] | 100 | 744
744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
74 | SR1L74 | VEMAGIRI(PG) - GAZUWAKA | 165.454 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L75 | VIJAYAWADA - VEMAGIRI(PG) | 187.8 | SR-I |  | 2018-09-01 | 0:00 | 2018-09-05 | 7:41 | [6 empty] | 103.6833 |  |  |  | H/T under Voltage regulation vide code SR357,continued from last month |  | 99.2832 | 744
[6 empty] | 2018-09-06 | 10:52 | 2018-09-06 | 15:27 |  |  |  | 4.5833 | [6 empty] | Tripped on R-N fault. VJA end: FD: 149.4KM, FC:2.2kA; VMG end: FD: 33.7KM, FC:7.2kA
[6 empty] | 2018-09-07 | 11:57 | 2018-09-07 | 12:42 |  |  |  | 0.75 | [6 empty] | H/T for tree cutting works vide code SR09/302
[6 empty] | Sub Total --> | [6 empty] | 5.3333 | 0 | 0 | 103.6833 | [6 empty] | 744
76 | SR1L76 | MAHESHWARAM-KURNOOL AP | 174.996 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1L77 | NiZAMABAD-DICHPALLY 1 | 4.428 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1L78 | NiZAMABAD-DICHPALLY 2 | 4.428 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1L79 | NIZAMABAD-MAHESHWARAM 1 | 243.059 | SR-I |  | 2018-09-19 | 23:51 | 2018-09-25 | 10:37 | [6 empty] | 130.7667 |  |  |  | H/T under Voltage regulation, SR09/823,NL-664 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 130.7667 | [6 empty] | 744
80 | SR1L80 | NIZAMABAD-MAHESHWARAM 2 | 243.059 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
81 | SR1L81 | NIZAMABAD-WARDHA 1 | 291.2 | SR-I |  | 2018-09-22 | 10:08 | 2018-09-22 | 21:07 |  |  |  | 10.9833 | [6 empty] | S/D availed by WR-1 vide SR09/946 |  | 98.5237 | 744
[6 empty] | Sub Total --> | [6 empty] | 10.9833 | 0 | 0 | 0 | [6 empty] | 744
82 | SR1L82 | NIZAMABAD-WARDHA 2 | 291.2 | SR-I |  | 2018-09-17 | 17:47 | 2018-09-17 | 17:47 |  |  |  | -7.7618e-12 | [6 empty] | AR successful on B-N fault.At NZB end: distance:11.82Km,FC-8.145KA; M2:9.2KM,FC-8.45KA AT Wardha end: distance:M1;2.8KA;291.2KM; M2:281.4Ka;2.45KA |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | -7.7618e-12 | 0 | 0 | 0 | [6 empty] | 744
83 | SR1L83 | VIJAYAWADA-VEMAGIRI PG 1 | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1L84 | VIJAYAWADA-VEMAGIRI PG 2 | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1L85 | VIJAYAWADA-VEMAGIRI PG 3 | 187.8 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1L86 | KADAPA- CHITTOOR | 147.14 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
87 | SR1L87 | VEMAGIRI PG - SIMHADRI-I | 180.98 | SR-I |  | 2018-09-29 | 1:27 | 2018-10-01 | 0:00 | [6 empty] | 46.55 |  |  |  | H/T for Voltage regulation vide code SR1416 |  | 100 | 744
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 46.55 | [6 empty] | 744
88 | SR1L88 | VEMAGIRI PG - SIMHADRI-II | 180.98 | SR-I |  | 2018-09-15 | 10:25 | 2018-09-15 | 10:25 |  |  |  | 7.7611e-11 | [6 empty] | AR Successful on B-N fault.At VMG end: distance:158Km,FC-2.147KA; AT SMD end: distance:13.20Km,FC-7.20KA |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 7.7611e-11 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1L89 | VEMAGIRI PG - VEMAGIRI AP - I | 38.41 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1L90 | VEMAGIRI PG - VEMAGIRI AP - II | 38.41 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
91 | SR1L91 | 400KV KADAPA - NP KUNTA - II | 68.69 | SR-I | [17 empty] | 100 | 744
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
92 | SR1L92 | 400KV KADAPA - NP KUNTA - III | 68.69 | SR-I | [17 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
76 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | 2018-09-05 | 10:38 | 2018-09-05 | 19:10 |  |  |  | 8.5333 | [6 empty] | H/T for AMP works vide code SR09/187 |  | 98.853 | 744
[6 empty] | Sub Total --> | [6 empty] | 8.5333 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
80 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
81 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
82 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
83 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | 2018-09-23 | 11:04 | 2018-09-23 | 13:16 |  |  |  | 2.2 | [6 empty] | H/T on emergency for attending hotspot in Bushing vide code : SR09/996 |  | 99.7043 | 744
[6 empty] | Sub Total --> | [6 empty] | 2.2 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
87 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
88 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | 2018-09-20 | 10:04 | 2018-09-20 | 19:30 |  |  |  | 9.4333 | [6 empty] | S/D availed for AMP works vide SR09/833. |  | 98.7321 | 744
[6 empty] | Sub Total --> | [6 empty] | 9.4333 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- |  |  |  |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
91 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
92 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
93 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
94 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
95 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
96 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
97 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
98 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
99 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
100 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
101 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
102 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
103 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
106 | SR1T30 | VEMAGIRI ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
107 | SR1T31 | VEMAGIRI ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
108 | SR1T32 | NIZAMABAD ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
109 | SR1T33 | NIZAMABAD ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
110 | SR1T34 | MAHESHWRAM ICT I | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
111 | SR1T35 | MAHESHWARAM ICT II | 1500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
112 | SR1T36 | HYDERABAD ICT IV | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
113 | SR1T37 | GOOTY ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
114 | SR1T38 | KHAMMAM ICT III | 500 | SR-I | -- | 2018-09-19 | 10:03 | 2018-09-19 | 13:53 |  |  |  | 0 |  |  | 3.8333 |  |  |  | Shutdown availed for CSD tunning Works vide SR/797 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.8333 | [6 empty] | 744
115 | SR1T39 | WARANGAL ICT III | 500 | SR-I | -- | 2018-09-22 | 11:25 | 2018-09-22 | 14:17 |  |  |  | 0 |  |  | 2.8667 |  |  |  | Shutdown availed for CSD tunning Works vide SR/954 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.8667 | [6 empty] | 744
116 | SR1T40 | SRIKAKULAM 765/400kV ICT I | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
117 | SR1T41 | SRIKAKULAM 765/400kV ICT II | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1T42 | VIJAYAWADA ICT III | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
119 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
120 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [16 empty] | 744
121 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
122 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | [5 empty] | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | 2018-09-25 | 10:20 | 2018-09-25 | 21:45 | [6 empty] | 11.4167 |  |  |  | Bus Reactor Bay constructions works,SR/1063 NL/846 |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.4167 | [6 empty] | 744
124 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | [11 empty] | N/A | N/A | N/A |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
125 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
126 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
127 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
128 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
129 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | 2018-09-04 | 11:45 | 2018-09-06 | 23:29 | [6 empty] | 59.7333 |  |  |  | H/T for Voltage regulation vide code SR134 |  | 100 | 744
[6 empty] | 2018-09-12 | 9:31 | 2018-10-01 | 0:00 | [6 empty] | 446.4833 |  |  |  | H/T for Voltage regulation vide code SR485
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 506.2167 | [6 empty] | 744
130 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
131 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
132 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
133 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
134 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
135 | SR1R17 | 765 KV SRIKAKULAM-VEMAGIRI 2 LR | 240 | SR-I | -- | 2018-09-17 | 11:33 | 2018-09-17 | 14:28 |  |  |  | 2.9167 | [6 empty] | H/T for swapping of spare unit vide code SR662,NL580 |  | 99.608 | 744
[6 empty] | Sub Total --> | [6 empty] | 2.9167 | 0 | 0 | 0 | [6 empty] | 744
136 | SR1R18 | 765 KV SRIKAKULAM-VEMAGIRI 1 LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
137 | SR1R19 | 330MVAR BUS REACTOR at SKLM | 330 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
138 | SR1R20 | VEMAGIRI 240MVAR BUS REACTOR-I | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
139 | SR1R21 | VEMAGIRI 240MVAR BUS REACTOR-II | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
140 | SR1R22 | VEMAGIRI 80MVAR BUS REACTOR | 80 | SR-I | -- | 2018-09-27 | 10:37 | 2018-09-27 | 18:26 |  |  |  | 7.8167 | [6 empty] | S/D availed for AMP works vide SR09/1247. |  | 98.9494 | 744
[6 empty] | Sub Total --> | [6 empty] | 7.8167 | 0 | 0 | 0 | [6 empty] | 744
141 | SR1R23 | MAHESHWARAM BUS REACTOR 1 | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
142 | SR1R24 | POLE-2 EAST REACTOR | 125 | SR-I | -- | 2018-09-01 | 0:00 | 2018-10-01 | 0:00 | [6 empty] | 720 |  |  |  | H/T for voltage regulation vide code SR 757,continued from last month |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 720 | [6 empty] | 744
143 | SR1R25 | VIJAYWADA BUS REACTOR 4 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
144 | SR1R26 | NAGARJUNA SAGAR BUS REACTOR II | 125 | SR-I | -- | 2018-09-24 | 16:32 | 2018-09-24 | 17:20 |  |  |  | 0.8 | [6 empty] | H/T on emergency to rectify the burning wire(R-Ph turret CT) in Reactor MB vide code: SR09/1037 |  | 99.8925 | 744
[6 empty] | Sub Total --> | [6 empty] | 0.8 | 0 | 0 | 0 | [6 empty] | 744
145 | SR1R27 | WARDHA 1 LR AT NIZAMABAD | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
146 | SR1R28 | WARDHA 2 LR AT NIZAMABAD | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
147 | SR1R29 | SOLAPUR - RAICHUR -I LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
148 | SR1R30 | ANGUL - SRIKAKULAM - I LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
149 | SR1R31 | ANGUL - SRIKAKULAM - II LR | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
150 | SR1R32 | WARDHA - NIZAMABAD - I L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
151 | SR1R33 | WARDHA - NIZAMABAD - II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
152 | SR1R34 | HYDERABAD - GAJWEL LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
153 | SR1R35 | NELLORE - THIRUVALAM - I LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
154 | SR1R36 | NELLORE - THIRUVALAM - II LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
155 | SR1R37 | GOOTY - KURNOOL LR | 50 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
156 | SR1R38 | GOOTY BUS REACTOR 2 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
157 | SR1R39 | NELLORE BUS REACTOR 2 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
158 | SR1R40 | NIZAMABAD 765KV BUS REACTOR 1 | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
159 | SR1R41 | NPS-GOOTY-1 L/R | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
160 | SR1R42 | NPS-GOOTY-2 L/R | 63 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
161 | SR1R43 | SRIKAKULAM-ANGUL 1 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
162 | SR1R44 | SRIKAKULAM-ANGUL 2 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
163 | SR1R45 | VEMAGIRI-SRIKAKULAM1 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
164 | SR1R46 | VEMAGIRI-SRIKAKULAM2 L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
165 | SR1R47 | VIJAYWADA BUS REACTOR 3 | 125 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
166 | SR1R48 | NIZAMABAD-WARDHA -I L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
167 | SR1R49 | NIZAMABAD-WARDHA -II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
168 | SR1R50 | MAHESHWARAM BUS REACTOR -II | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
169 | SR1R51 | MAHESHWARAM-NIZAMABAD-I L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
170 | SR1R52 | MAHESHWARAM-NIZAMABAD-II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
171 | SR1R38 | NIZAMABAD-MAHESHWARAM I L/R | 240 | SR-I | -- | 2018-09-14 | 9:59 | 2018-09-14 | 11:44 |  |  |  | 1.75 | [6 empty] | H/T for swapping of spare unit vide code SR546,NL479 |  | 99.5677 | 744
[6 empty] | 2018-09-18 | 10:37 | 2018-09-18 | 12:05 |  |  |  | 1.4667 | [6 empty] | H/T for swapping of spare unit vide code SR546,NL479
[6 empty] | Sub Total --> | [6 empty] | 3.2167 | 0 | 0 | 0 | [6 empty] | 744
172 | SR1R53 | NIZAMABAD-MAHESHWARAM II L/R | 240 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
173 | SR1R54 | JEYPORE LR-1 AT GAJUWAKA | 80 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R55 | JEYPORE LR-2 AT GAJUWAKA | 80 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
175 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2018-09-26 | 10:15 | 2018-09-26 | 15:46 |  |  |  | 5.5167 | [6 empty] | Emergency S/D for attending Thyrister Redundency lost alarm, SR/1148, NL/840 |  | 99.2585 | 744
[6 empty] | Sub Total --> | [6 empty] | 5.5167 | 0 | 0 | 0 | [6 empty] | 744
176 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | [16 empty] | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
177 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
178 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
179 | SR1S1 | STATCOM AT NPKUNTA | 200 | SR-I | -- | [11 empty] | -- | -- | -- |  |  | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
|  |  | Note in type of failure column please indicate following : | [9 empty] | 79.1833 | 0.083333 | 5.1 | 3227.7333
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF MARCH 2017
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I FSC at CDP
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II FSC at CDP
27 |  | NSR II FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-2 at GTY
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VTPS LR at NLRAP
32 |  | VTPS LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA LR at NLRAP
33 |  | VJA LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VJA
34 |  | NLRAP LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VTPS
35 |  | NLRAP LR at VTPS | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
36 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
37 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
38 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
39 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
40 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
41 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0