## SOP
Standard of Performance data for the month of August-2015
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE | RESTORATION | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date and Time | Date and Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L1 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | 2015-08-21 11:02 | 2015-08-21 17:57 | -- | -- | -- |  |  |  | 6.9167 | N/A | N/A | N/A | Shut down availed by M/s TGTRANSCO for relay testing works at Gajwel end vide SRLDC code no. CR-08/471 | SRPC | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 6.9167
2 | SR1L2 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
3 | SR1L3 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
4 | SR1L4 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | 2015-08-01 10:21 | 2015-08-01 14:05 | -- | -- | -- |  |  |  | 3.7333 | N/A | N/A | N/A | S/D availed by M/s TSTRANCO for maintenance works at Malkaram S/S vide SRLDC code CR-08/10 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 3.7333
5 | SR1L5 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
6 | SR1L6 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
7 | SR1L7 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2015-08-19 08:20 | 2015-08-19 18:35 | -- | -- | -- |  |  |  | 10.25 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-08/393 |  | 100
[5 empty] | -- | 2015-08-20 07:35 | 2015-08-20 18:34 | -- | -- | -- |  |  |  | 10.9833 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-08/433
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 21.2333
8 | SR1L8 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
9 | SR1L9 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
10 | SR1L10 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
11 | SR1L11 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
12 | SR1L12 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
13 | SR1L13 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | 2015-08-20 08:44 | 2015-08-22 19:07 | -- | -- | -- |  |  |  | 58.3833 | N/A | N/A | N/A | Shut down availed by M/s TGTRANSCO for construction works of 400 kV Suryapet - Shankarpally D/C line vide SRLDC code no. CR-08/435 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 58.3833
14 | SR1L14 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | 2015-08-12 19:08 | 2015-08-12 20:12 | -- | -- | -- |  |  | 1.0667 |  | -- | -- | -- | Tripped on operation of O/V protn at KRNL end. DT recd at HYD end |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 1.0667 | 0
15 | SR1L15 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
16 | SR1L16 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
17 | SR1L17 | KHAMMAM - N'SAGAR | 144.577 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
18 | SR1L18 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
19 | SR1L19 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
20 | SR1L20 | KURNOOL(NEW) - GOOTY | 112.609 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
21 | SR1L21 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | 2015-08-22 13:14 | 2015-08-22 13:14 | -- | -- | -- |  |  |  |  | -- | -- | -- | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 75.98KM from NSG end. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
22 | SR1L22 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
23 | SR1L23 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | 2015-08-31 10:35 | 2015-09-01 | -- | -- | -- |  |  |  | 13.4167 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for checking of A/R scheme at RCR end vide SRLDC code no. CR-08/637 |  | 100
[5 empty] | -- | 2015-08-27 11:04 | 2015-08-27 18:52 | -- | -- | -- |  |  |  | 7.8 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for cheking of A/R scheme at RCR vide SRLDC code CR-08/592
[5 empty] | -- | 2015-08-10 09:49 | 2015-08-16 19:43 | -- | -- | -- |  |  |  | 153.9 | N/A | N/A | N/A | Shut down availed by M/s RTPS for retrofitting of numerical relays at RCR end vide SRLDC code CR-08/190
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 175.1167
24 | SR1L24 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
25 | SR1L25 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
26 | SR1L26 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2015-08-24 10:06 | 2015-08-24 17:58 | -- | -- | -- | 7.8667 |  |  |  | N/A | N/A | N/A | Shut down availed for replacement of damaged tension insulator strings at Loc. No. 396 vide SRLDC code CR-08/510 |  | 98.8978
[5 empty] | -- | 2015-08-20 20:53 | 2015-08-20 21:13 | -- | -- | -- | 0.33333 |  |  |  | N/A | N/A | N/A | Tripped on B-N fault at NLR end only. A/R successful at VJA end. FLR- 1150.2 km from VJA.
[6 empty] | Sub Total --> |  |  |  |  | 8.2 | 0 | 0 | 0
27 | SR1L27 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2015-08-18 12:17 | 2015-09-01 | -- | -- | -- |  |  |  | 323.7167 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-08/375 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 323.7167
28 | SR1L28 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | 2015-07-31 20:35 | 2015-08-18 11:53 | -- | -- | -- |  |  |  | 419.8833 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-07/840 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 419.8833
29 | SR1L29 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
30 | SR1L30 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
31 | SR1L31 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
32 | SR1L32 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
33 | SR1L33 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
34 | SR1L34 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
35 | SR1L35 | NELLORE - ALMATHY | 194.44 | SR-I | -- | 2015-07-27 12:14 | 2015-08-13 20:07 | -- | -- | -- |  |  |  | 308.1167 | -- | -- | -- | Shut down availed by M/s TNEB for stringing works of 400kV ALM-THVLM D/C lines vide SRLDC code CR-07/717 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 308.1167
|  | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
36 | SR1L36 | NELLORE - SIRIPERUMBUDUR | 189 | SR-I | -- | 2015-07-30 08:23 | 2015-08-08 21:37 | -- | -- | -- |  |  |  | 189.6167 | N/A | N/A | N/A | Shut down availed by M/s TNEB for stringing works of 400kV ALM-THVLM D/C lines vide SRLDC code CR-07/717 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 189.6167
37 | SR1L37 | ALMATHY - SIRIPERUMBUDUR | 75.973 | SR-I | -- | 2015-07-27 12:12 | 2015-08-13 20:07 | -- | -- | -- |  |  |  | 308.1167 | N/A | N/A | N/A | Shut down availed by M/s TNEB for stringing works of 400kV ALM-THVLM D/C lines vide SRLDC code CR-07/718 |  | 100
[5 empty] | -- | Sub Total --> |  | -- | -- | -- | 0 | 0 | 0 | 308.1167 | -- | -- | -- | --
|  | ALMATHY - THIRUVALAM I | 40.969 |  | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
|  | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
38 | SR1L38 | KURNOOL - GOOTY | 84.19 | SR-I | -- | 2015-08-08 07:53 | 2015-08-08 17:35 | -- | -- | -- |  |  |  | 9.7 | -- | -- | -- | Shut down availed for construction of Raichur-Kurnool (765 kV)-I lines vide SRLDC code CR-08/170 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 9.7
39 | SR1L39 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | 2015-08-07 16:43 | 2015-08-07 16:43 | -- | -- | -- |  |  |  |  | -- | -- | -- | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 04 KM from Gooty end. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
40 | SR1L40 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
41 | SR1L41 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
42 | SR1L42 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
43 | SR1L43 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
44 | SR1L44 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
45 | SR1L45 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
46 | SR1L46 | MEPL - NELLOREPS | 3.83 | SR-I | -- | 2015-08-21 07:40 | 2015-08-25 23:06 | -- | -- | -- |  |  |  | 111.4333 | N/A | N/A | N/A | Shut down availed by M/s MEPL for RTV Silicon rubber painting for gantry insulators at MEPL end vide SRLDC code no. CR-08/459 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 111.4333
47 | SR1L47 | SEPL - NELLOREPS | 3.83 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
48 | SR1L48 | GOOTY - NELLOREPS - I | 289.004 | SR-I | -- | 2015-07-01 10:10 | 2015-08-12 12:26 | -- | -- | -- |  |  |  | 276.4333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage vide msg no. CP-07/09A |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 276.4333
49 | SR1L49 | GOOTY - NELLOREPS - II | 289.004 | SR-I | -- | 2015-08-12 12:30 | 2015-09-01 | -- | -- | -- |  |  |  | 467.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-08/258 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 467.5
50 | SR1L50 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
51 | SR1L51 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
52 | SR1L52 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
53 | SR1L53 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
54 | SR1L54 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
55 | SR1L55 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
56 | SR1L56 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | 2015-08-02 09:18 | 2015-08-02 10:57 | -- | -- | -- | 1.65 |  |  |  | N/A | N/A | N/A | Tripped at Sholapur end only due to relay mal-operation at SLPR end. |  | 99.7782
[6 empty] | Sub Total --> |  |  |  |  | 1.65 | 0 | 0 | 0
57 | SR1L57 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
58 | SR1L58 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
59 | SR1L59 | KURNOOL(NEW) - RAICHUR(NEW) - II | 118.423 | SR-I | -- | 2015-08-12 08:10 | 2015-08-12 23:22 | -- | -- | -- |  |  |  | 15.2 | N/A | N/A | N/A | Shut down availed for construction works of 765 kV Raichur - Kurnool line-1 vide SRLDC code no. CR-08/239 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 15.2
60 | SR1L60 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2015-07-19 22:41 | 2015-08-19 10:19 | -- | -- | -- |  |  |  | 442.3167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage vide msg no. CP-07/596A |  | 99.7267
[5 empty] | -- | 2015-08-19 13:43 | 2015-08-19 15:45 | -- | -- | -- | 2.0333 |  |  |  | N/A | N/A | N/A | Tripped on operation of line reactor WTI protection at Kurnool end
[6 empty] | Sub Total --> |  |  |  |  | 2.0333 | 0 | 0 | 442.3167
61 | SR1L61 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2015-08-18 19:10 | 2015-09-01 | -- | -- | -- |  |  |  | 316.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-08/387 |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 316.8333
62 | SR1L62 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2015-08-20 21:12 | 2015-08-20 21:25 | -- | -- | -- |  |  | 0.21667 |  | N/A | N/A | N/A | Tripped on operation of O/V protection at TRVLM end. DT recd at KRNLend. |  | 100
[5 empty] | -- | 2015-08-20 21:25 | 2015-09-01 | -- | -- | -- |  |  |  | 266.5833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage vide msg no. CP-08/445
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.21667 | 266.5833
63 | SR1L63 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2015-07-29 22:45 | 2015-08-21 10:23 | -- | -- | -- |  |  |  | 490.3833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage vide msg no. CP-07/895 |  | 100
[5 empty] | -- | 2015-08-21 23:38 | 2015-08-21 23:45 | -- | -- | -- |  |  | 0.11667 |  | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Thiruvalam end. Direct trip signal received at Kurnool end.
[5 empty] | -- | 2015-08-21 23:45 | 2015-08-29 10:19 | -- | -- | -- |  |  |  | 178.5667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/476
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0.11667 | 668.95
64 | SR1L64 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | 2015-08-15 14:04 | 2015-08-15 14:52 | -- | -- | -- | 0.8 |  |  |  | N/A | N/A | N/A | Tripped on B-N fault.DLR=132 Kms from VJA end. |  | 98.9931
[5 empty] | -- | 2015-08-15 15:40 | 2015-08-15 20:40 | -- | -- | -- | 5 |  |  |  | N/A | N/A | N/A | Tripped on B-N fault.DLR=124.9 Kms from VJA end.
[6 empty] | Sub Total --> |  |  |  |  | 5.8 | 0 | 0 | 0
66 | SR1L65 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
66 | SR1T1 | CUDDAPAH ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
67 | SR1T2 | CUDDAPAH ICT II | 315 | SR-I | -- | 2015-08-13 09:27 | 2015-08-13 17:32 | -- | -- | -- | 8.0833 |  |  |  | -- | -- | -- | Shut down availed for AMP works vide SRLDC code no. CR-08/284 |  | 98.9135
[6 empty] | Sub Total --> |  |  |  |  | 8.0833 | 0 | 0 | 0
68 | SR1T3 | GAJUWAKA ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
69 | SR1T4 | GAZUWAKA ICT II | 315 | SR-I | -- | 2015-08-04 12:49 | 2015-08-04 13:31 | -- | -- | -- |  | 0.7 |  |  | -- | -- | -- | Tripped at 220 kV end only due to operation of busbar protection at 220 kV APTRANSCO S/S |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0.7 | 0 | 0
70 | SR1T5 | GOOTY ICT I | 315 | SR-I | -- | 2015-08-07 16:43 | 2015-08-07 17:17 | -- | -- | -- |  | 0.56667 |  |  | N/A | N/A | N/A | Tripped on operation of back up over current protection due to fault in down stream system of APTRANSCO. |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0.56667 | 0 | 0
71 | SR1T6 | GOOTY ICT II | 315 | SR-I | -- | 2015-08-10 09:27 | 2015-08-10 18:13 | -- | -- | -- | 8.7667 |  |  |  | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code CR-08/189 |  | 98.8217
[6 empty] | Sub Total --> |  |  |  |  | 8.7667 | 0 | 0 | 0
72 | SR1T7 | HYDERABAD ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
73 | SR1T8 | HYDERABAD ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
74 | SR1T9 | HYDERABAD ICT - III | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
75 | SR1T10 | KHAMMAM ICT I | 315 | SR-I | -- | 2015-08-21 10:46 | 2015-08-21 19:42 | -- | -- | -- | 8.9333 |  |  |  | -- | -- | -- | Shut down availed for replacement of B-Ph LA due to high THRC value vide SRLDC code no. CR-08/469 |  | 98.7993
[6 empty] | Sub Total --> |  |  |  |  | 8.9333 | 0 | 0 | 0
76 | SR1T11 | KHAMMAM ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
77 | SR1T12 | MUNIRABAD ICT I | 315 | SR-I | -- | 2015-08-19 13:03 | 2015-08-19 19:44 | -- | -- | -- |  |  |  | 6.6833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-08/412 |  | 100
[5 empty] | -- | 2015-08-20 10:07 | 2015-08-20 16:25 | -- | -- | -- |  |  |  | 6.3 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-08/441
[5 empty] | -- | 2015-08-21 09:59 | 2015-08-21 11:02 | -- | -- | -- |  |  |  | 1.05 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-08/464
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 14.0333
78 | SR1T13 | MUNIRABAD ICT II | 315 | SR-I | -- | 2015-08-20 10:45 | 2015-08-20 16:50 | -- | -- | -- |  |  |  | 6.0833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-08/444 |  | 100
[5 empty] | -- | 2015-08-21 10:00 | 2015-08-21 10:50 | -- | -- | -- |  |  |  | 0.83333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-08/465
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 6.9167
79 | SR1T14 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
80 | SR1T15 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
81 | SR1T16 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
82 | SR1T17 | VIJAYAWADA ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
83 | SR1T18 | VIJAYAWADA ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
84 | SR1T19 | WARANGAL ICT I | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
85 | SR1T20 | WARANGAL ICT II | 315 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
86 | SR1T21 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
87 | SR1T22 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
88 | SR1T23 | NELLOREPS ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
89 | SR1T24 | NELLOREPS ICT - III | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
90 | SR1T25 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
91 | SR1T26 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
92 | SR1R1 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
93 | SR1R2 | GOOTY BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
94 | SR1R3 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
95 | SR1R4 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
96 | SR1R5 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
97 | SR1R6 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2015-08-24 10:02 | 2015-08-24 17:01 | -- | -- | -- | 6.9833 |  |  |  | -- | -- | -- | Shut down availed for AMP works vide SRLDC code CR-08/513 |  | 99.0614
[6 empty] | Sub Total --> |  |  |  |  | 6.9833 | 0 | 0 | 0
98 | SR1R7 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
99 | SR1R8 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
100 | SR1R9 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
101 | SR1R10 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
102 | SR1R11 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
103 | SR1R12 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
104 | SR1R13 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
105 | SR1R14 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
106 | SR1R15 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
107 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
108 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
109 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
110 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- | -- | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> |  |  |  |  | 0 | 0 | 0 | 0
|  |  | Note in type of failure column please indicate following : | [7 empty] | 50.45 | 1.2667 | 1.4 | 4410.7333
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF AUGUST 2015
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I FSC at CDP
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II FSC at CDP
27 |  | NSR II FSC at CDP | 201.75 | SR1 | [13 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-2 at GTY
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
32 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
33 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
34 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
35 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
36 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
37 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0