## SOP
Standard of Performance data for the month of September-2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2016-09-01 | 0:00 | 2016-09-08 | 13:57 | -- | -- | -- |  |  |  | 181.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR08/437 | SRPC | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 181.95 | [6 empty] | 720
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2016-09-02 | 21:56 | 2016-09-02 | 21:56 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Line autoreclosed sucessfully on B-N fault. FL:297.9kms, 2.3kA from NPS end & 16.45kms, 10.43kA from KLN end. |  | 100 | 720
[5 empty] | -- | 2016-09-08 | 14:30 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 537.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/257 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 537.5 | [6 empty] | 720
3 | SR1L03 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | 2016-09-01 | 0:00 | 2016-09-03 | 10:40 | -- | -- | -- |  |  |  | 58.6667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR08/33 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 58.6667 | [6 empty] | 720
4 | SR1L04 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | 2016-09-02 | 21:56 | 2016-09-02 | 22:05 | -- | -- | -- |  |  | 0.15 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at KLN end. Direct Trip Signal received at Tiruvalam end |  | 100 | 720
[5 empty] | -- | 2016-09-02 | 22:05 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 673.9167 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.15 | 673.9167 | [6 empty] | 720
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2016-09-04 | 17:13 | 2016-09-05 | 9:20 | -- | -- | -- |  |  |  | 16.1167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/89 |  | 100 | 720
[5 empty] | -- | 2016-09-10 | 23:14 | 2016-09-11 | 6:57 | -- | -- | -- |  |  |  | 7.7167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/322 |  |  | 720
[5 empty] | -- | 2016-09-11 | 21:47 | 2016-09-12 | 7:10 | -- | -- | -- |  |  |  | 9.3833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/340 |  |  | 720
[5 empty] | -- | 2016-09-15 | 23:13 | 2016-09-16 | 7:33 | -- | -- | -- |  |  |  | 8.3333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/466 |  |  | 720
[5 empty] | -- | 2016-09-16 | 22:41 | 2016-09-17 | 7:01 | -- | -- | -- |  |  |  | 8.3333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/498 |  |  | 720
[5 empty] | -- | 2016-09-18 | 1:16 | 2016-09-18 | 6:58 | -- | -- | -- |  |  |  | 5.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/518 |  |  | 720
[5 empty] | -- | 2016-09-22 | 23:40 | 2016-09-23 | 5:49 | -- | -- | -- |  |  |  | 6.15 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/682 |  |  | 720
[5 empty] | -- | 2016-09-24 | 0:18 | 2016-09-24 | 7:06 | -- | -- | -- |  |  |  | 6.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/719 |  |  | 720
[5 empty] | -- | 2016-09-26 | 0:13 | 2016-09-26 | 7:02 | -- | -- | -- |  |  |  | 6.8167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/682 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 75.35 | [6 empty] | 720
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | 2016-09-14 | 15:43 | 2016-09-14 | 17:28 | -- | -- | -- |  |  | 1.75 |  | N/A | N/A | N/A | Tripped at Solapur end only on receipt of DT. Suspected DC Earthfault due to heavy rain and DT was sent from RCN end. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.75 | 0 | [6 empty] | 720
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | 2016-09-08 | 10:37 | 2016-09-08 | 17:07 | -- | -- | -- |  |  |  | 6.5 | N/A | N/A | N/A | Shutdown availed by M/s TANTRANSCO for maintenance works |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.5 | [6 empty] | 720
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | 2016-08-19 | 9:58 | 2016-08-19 | 18:01 | -- | -- | -- |  |  |  | 8.05 | N/A | N/A | N/A | Shutdown availed by M/s TANTRANSCO for maintenance works vide SRLDC code CR08/555 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.05 | [6 empty] | 720
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | 2016-09-25 | 7:12 | 2016-09-25 | 19:11 | -- | -- | -- |  |  |  | 11.9833 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/766 |  | 100 | 720
[5 empty] | -- | 2016-09-26 | 6:30 | 2016-09-26 | 18:57 | -- | -- | -- |  |  |  | 12.45 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/800 |  |  | 720
[5 empty] | -- | 2016-09-27 | 6:44 | 2016-09-27 | 18:38 | -- | -- | -- |  |  |  | 11.9 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/834 |  |  | 720
[5 empty] | -- | 2016-09-28 | 6:44 | 2016-09-28 | 18:36 | -- | -- | -- |  |  |  | 11.8667 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/834 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.2 | [6 empty] | 720
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | 2016-09-25 | 7:12 | 2016-09-25 | 19:12 | -- | -- | -- |  |  |  | 12 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/767 |  | 100 | 720
[5 empty] | -- | 2016-09-26 | 6:30 | 2016-09-26 | 18:58 | -- | -- | -- |  |  |  | 12.4667 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/800 |  |  | 720
[5 empty] | -- | 2016-09-27 | 6:44 | 2016-09-27 | 18:39 | -- | -- | -- |  |  |  | 11.9167 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/835 |  |  | 720
[5 empty] | -- | 2016-09-28 | 6:44 | 2016-09-28 | 18:36 | -- | -- | -- |  |  |  | 11.8667 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/835 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.25 | [6 empty] | 720
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | 2016-09-01 | 5:17 | 2016-09-01 | 6:16 | -- | -- | -- |  |  | 0.98333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at GTY end. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.98333 | 0 | [6 empty] | 720
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
16 | SR1L16 | GOOTY - TUMKUR - I | 208.6 | SR-I | -- | 2016-09-01 | 0:00 | 2016-09-03 | 0:30 | -- | -- | -- |  |  |  | 48.5 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  | 100 | 720
[5 empty] | -- | 2016-09-10 | 22:05 | 2016-09-19 | 10:31 | -- | -- | -- |  |  |  | 204.4333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/321 |  |  | 720
[5 empty] | -- | 2016-09-21 | 13:30 | 2016-09-23 | 14:55 | -- | -- | -- |  |  |  | 49.4167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/623 |  |  | 720
[5 empty] | -- | 2016-09-23 | 22:10 | 2016-09-27 | 9:42 | -- | -- | -- |  |  |  | 83.5333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/715 |  |  | 720
[5 empty] | -- | 2016-09-28 | 21:52 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 50.1333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/918 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 436.0167 | [6 empty] | 720
17 | SR1L17 | GOOTY - TUMKUR - II | 208.6 | SR-I | -- | 2016-09-01 | 5:17 | 2016-09-01 | 5:25 | -- | -- | -- |  |  | 0.13333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at GTY end. Direct Trip Signal received at Tumkur end |  | 100 | 720
[5 empty] | -- | 2016-09-01 | 5:25 | 2016-09-01 | 6:41 | -- | -- | -- |  |  |  | 1.2667 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[5 empty] | -- | 2016-09-02 | 21:56 | 2016-09-02 | 22:05 | -- | -- | -- |  |  | 0.15 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at GTY end. Direct Trip Signal received at TUMKUR end |  |  | 720
[5 empty] | -- | 2016-09-02 | 22:05 | 2016-09-03 | 14:25 | -- | -- | -- |  |  |  | 16.3333 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.28333 | 17.6 | [6 empty] | 720
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | 2016-09-26 | 2:18 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 117.7 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/796 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 117.7 | [6 empty] | 720
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | 2016-09-01 | 0:00 | 2016-09-27 | 15:55 | -- | -- | -- |  |  |  | 639.9167 | -- | -- | -- | Line kept open as per SRLDC instruction for voltage regulation in the system |  | 100 | 720
[5 empty] | -- | 2016-09-29 | 1:18 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 46.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/922 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 686.6167 | [6 empty] | 720
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | 2016-09-25 | 19:12 | 2016-09-25 | 20:39 | -- | -- | -- | 1.45 |  |  |  | N/A | N/A | N/A | Tripped on TEED Protection due to failure of Tie bay CT B Ph( Tie CT of Jeypore-1& Filter bay) |  | 99.7986 | 720
[6 empty] | Sub Total --> | [6 empty] | 1.45 | 0 | 0 | 0 | [6 empty] | 720
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | 2016-09-27 | 21:37 | 2016-09-27 | 21:37 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Line Autoreclosed successfully on R-N fault. FL: 0.915 kms, FC-11.620 kA from KMM end. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | 2016-09-17 | 16:26 | 2016-09-17 | 17:12 | -- | -- | -- | 0.76667 |  |  |  | N/A | N/A | N/A | Tripped due to failure of DC-DC converter in TEED2 Relay at VJA end. DT received at KMM end. |  | 99.8935 | 720
[5 empty] | -- | 2016-09-25 | 0:54 | 2016-09-25 | 1:05 | -- | -- | -- |  |  | 0.18333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at KMM end. Direct Trip Signal received at VJA end |  |  | 720
[5 empty] | -- | 2016-09-25 | 1:05 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 142.9167 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0.76667 | 0 | 0.18333 | 142.9167 | [6 empty] | 720
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2016-09-07 | 9:57 | 2016-09-07 | 10:15 | -- | -- | -- |  |  |  | 0.3 | N/A | N/A | N/A | Emergency shutdown availed by M/s RTPS for attending L/R oil leakage at their end vide SRLDC code CR09/203 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.3 | [6 empty] | 720
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | 2016-09-25 | 1:00 | 2016-09-25 | 1:10 | -- | -- | -- |  |  | 0.16667 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at HYD end. Direct Trip Signal received at MLK end |  | 100 | 720
[5 empty] | -- | 2016-09-25 | 1:10 | 2016-09-25 | 7:20 | -- | -- | -- |  |  |  | 6.1667 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 6.1667 | [6 empty] | 720
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | 2016-09-11 | 21:58 | 2016-09-28 | 10:24 | -- | -- | -- |  |  |  | 396.4333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/341 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 396.4333 | [6 empty] | 720
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | 2016-09-20 | 15:24 | 2016-09-20 | 18:14 | -- | -- | -- | 2.8333 |  |  |  | -- | -- | -- | Line tripped due to CB problem at SPDR end. DT received at NLR end. |  | 99.6065 | 720
[6 empty] | Sub Total --> | [6 empty] | 2.8333 | 0 | 0 | 0 | [6 empty] | 720
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | 2016-09-20 | 9:55 | 2016-09-20 | 15:22 | -- | -- | -- | 5.45 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR09/569 |  | 99.2431 | 720
[6 empty] | Sub Total --> | [6 empty] | 5.45 | 0 | 0 | 0 | [6 empty] | 720
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | 2016-09-06 | 19:52 | 2016-09-06 | 20:02 | -- | -- | -- | 0.16667 |  |  |  | N/A | N/A | N/A | Tripped on Y-N fault at KDP end only. A/R successful at NSR end. FL: 34.2kms, 4.4kA from KDP end |  | 99.9769 | 720
[6 empty] | Sub Total --> | [6 empty] | 0.16667 | 0 | 0 | 0 | [6 empty] | 720
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | 2016-09-26 | 23:10 | 2016-09-27 | 7:00 | -- | -- | -- |  |  |  | 7.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/828 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.8333 | [6 empty] | 720
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | 2016-09-28 | 10:37 | 2016-09-28 | 17:10 | -- | -- | -- |  |  |  | 6.55 | N/A | N/A | N/A | Shutdown availed M/s TSTRANSCO vide SRLDC code CR09/885 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.55 | [6 empty] | 720
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2016-09-20 | 9:02 | 2016-09-20 | 19:31 | -- | -- | -- |  |  |  | 10.4833 | -- | -- | -- | Shutdown availed by M/s NTPC RDM for attending A/R scheme problem at their end vide SRLDC code CR09/563 |  | 100 | 720
[5 empty] | -- | 2016-09-21 | 13:11 | 2016-09-21 | 18:37 | -- | -- | -- |  |  |  | 5.4333 | N/A | N/A | N/A | Shutdown availed by M/s NTPC RDM for attending hotspot at their end vide SRLDC code CR09/621 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 15.9167 | [6 empty] | 720
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | 2016-09-27 | 1:01 | 2016-09-27 | 2:27 | -- | -- | -- |  | 1.4333 |  |  | -- | -- | -- | Tripped on B-N fault at RDM end only. A/R successful at CPDR end. FL: 138kms, 1.084kA from CPDR. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.4333 | 0 | 0 | [6 empty] | 720
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | 2016-09-25 | 1:03 | 2016-09-25 | 6:52 | -- | -- | -- |  |  |  | 5.8167 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/762 |  | 100 | 720
[5 empty] | -- | 2016-09-25 | 22:10 | 2016-09-26 | 5:52 | -- | -- | -- |  |  |  | 7.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/792 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.5167 | [6 empty] | 720
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | 2016-09-21 | 23:29 | 2016-09-22 | 7:00 | -- | -- | -- |  |  |  | 7.5167 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/647 |  | 100 | 720
[5 empty] | -- | 2016-09-23 | 5:24 | 2016-09-23 | 5:24 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Line Autoreclosed successfully on Y-N fault. FL: 175.2kms, 3.126kA from RDM end. |  |  | 720
[5 empty] | -- | 2016-09-23 | 13:11 | 2016-09-23 | 13:11 | -- | -- | -- |  |  |  |  | N/A | N/A | N/A | Line Autoreclosed successfully on Y-N fault. FL: 175.2kms, 3.126kA from RDM end. |  |  | 720
[5 empty] | -- | 2016-09-29 | 1:19 | 2016-09-29 | 7:05 | -- | -- | -- |  |  |  | 5.7667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/921 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.2833 | [6 empty] | 720
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I | -- | 2016-09-25 | 1:00 | 2016-09-25 | 1:20 | -- | -- | -- |  |  | 0.33333 |  | -- | -- | -- | Line tripped on operation of Over Voltage protection at HYD end. Direct Trip Signal received at RDM end |  | 100 | 720
[5 empty] | -- | 2016-09-25 | 1:34 | 2016-09-25 | 1:40 | -- | -- | -- |  |  | 0.1 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at HYD end. Direct Trip Signal received at RDM end |  |  | 720
[5 empty] | -- | 2016-09-25 | 1:40 | 2016-09-25 | 6:30 | -- | -- | -- |  |  |  | 4.8333 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[5 empty] | -- | 2016-09-26 | 1:57 | 2016-09-26 | 2:31 | -- | -- | -- |  |  | 0.56667 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at HYD end. Direct Trip Signal received at RDM end |  |  | 720
[5 empty] | -- | 2016-09-26 | 3:22 | 2016-09-26 | 3:38 | -- | -- | -- |  |  | 0.26667 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at HYD end. |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.2667 | 4.8333 | [6 empty] | 720
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2016-09-08 | 9:17 | 2016-09-08 | 14:02 | -- | -- | -- |  |  |  | 4.75 | N/A | N/A | N/A | SD availed by TSTRANSCO for maintenance work at Malkaram end vide SRLDC code Cr09/249 |  | 100 | 720
[5 empty] | -- | 2016-09-14 | 1:08 | 2016-09-14 | 1:20 | -- | -- | -- |  |  | 0.2 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at MLK end. Direct Trip Signal received at RDM end |  |  | 720
[5 empty] | -- | 2016-09-14 | 1:20 | 2016-09-14 | 6:44 | -- | -- | -- |  |  |  | 5.4 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[5 empty] | -- | 2016-09-15 | 1:30 | 2016-09-15 | 1:40 | -- | -- | -- |  |  | 0.16667 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at MLK end. Direct Trip Signal received at RDM end |  |  | 720
[5 empty] | -- | 2016-09-15 | 1:40 | 2016-09-15 | 9:27 | -- | -- | -- |  |  |  | 7.7833 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[5 empty] | -- | 2016-09-25 | 0:30 | 2016-09-25 | 0:35 | -- | -- | -- |  |  | 0.083333 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at MLK end. Direct Trip Signal received at RDM end |  |  | 720
[5 empty] | -- | 2016-09-25 | 0:35 | 2016-09-25 | 7:47 | -- | -- | -- |  |  |  | 7.2 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[5 empty] | -- | 2016-09-26 | 1:56 | 2016-09-26 | 2:05 | -- | -- | -- |  |  | 0.15 |  | N/A | N/A | N/A | Line tripped on operation of Over Voltage protection at MLK end. Direct Trip Signal received at RDM end |  |  | 720
[5 empty] | -- | 2016-09-26 | 2:05 | 2016-09-26 | 5:36 | -- | -- | -- |  |  |  | 3.5167 | N/A | N/A | N/A | Line kept open as per SRLDC instruction for voltage regulation in the system |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.6 | 28.65 | [6 empty] | 720
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | 2016-09-13 | 0:07 | 2016-09-13 | 11:25 | -- | -- | -- |  |  |  | 11.3 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/382 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.3 | [6 empty] | 720
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | 2016-09-23 | 22:12 | 2016-09-24 | 7:42 | -- | -- | -- |  |  |  | 9.5 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR09/716 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.5 | [6 empty] | 720
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | 2016-09-12 | 12:03 | 2016-09-12 | 12:23 | -- | -- | -- |  | 0.33333 |  |  | -- | -- | -- | Line tripped at RDM end only. PLCC maloperation at RDM end |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.33333 | 0 | 0 | [6 empty] | 720
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | 2016-09-08 | 9:15 | 2016-09-08 | 13:22 | -- | -- | -- | 4.1167 |  |  |  | -- | -- | -- | Shutdown availed for fixing of jumper at Loc:AR-01 vide SRLDC Code CR09/246 |  | 99.4282 | 720
[6 empty] | Sub Total --> | [6 empty] | 4.1167 | 0 | 0 | 0 | [6 empty] | 720
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | 2016-09-06 | 16:43 | 2016-09-06 | 17:08 | -- | -- | -- |  | 0.41667 |  |  | -- | -- | -- | Tripped due to failure of Bus Reactor CB at Kalapaka Switchyard. Delayed fault clearence in APTRANSCO's Kalpaka Substation |  | 99.8471 | 720
[5 empty] | -- | 2016-09-30 | 6:38 | 2016-09-30 | 7:44 | -- | -- | -- | 1.1 |  |  |  | N/A | N/A | N/A | Tripped on maloperation of L/R NGR PRD at GWK end. DT received at VJA end. |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 1.1 | 0.41667 | 0 | 0 | [6 empty] | 720
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | 2016-09-24 | 11:34 | 2016-09-24 | 13:12 | -- | -- | -- |  |  | 1.6333 |  | -- | -- | -- | Spurious DT signal sent from VJA end due to DC E/F caused by Heavy Rains at VJA |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.6333 | 0 | [6 empty] | 720
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | 2016-09-15 | 10:16 | 2016-09-15 | 12:27 | -- | -- | -- |  |  |  | 2.1833 | N/A | N/A | N/A | Shutdown availed by M/s VTPS for commissioning of PMUs vide SRLDC code CR09/443 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.1833 | [6 empty] | 720
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | 2016-09-20 | 8:19 | 2016-09-20 | 21:47 | -- | -- | -- |  |  |  | 13.4667 | N/A | N/A | N/A | Shutdown availed for replacement of porcelain insulators with CLR insulators vide SRLDC code CR09/565 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.4667 | [6 empty] | 720
74 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
75 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
76 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
77 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
78 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
79 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | 2016-09-27 | 16:41 | 2016-09-27 | 18:48 | -- | -- | -- | 2.1167 |  |  |  | N/A | N/A | N/A | Shutdown availed for replacement of melted bolts on 71089B Bph isolator terminal connector vide SRLDC code CR09/854 |  | 99.706 | 720
[6 empty] | Sub Total --> | [6 empty] | 2.1167 | 0 | 0 | 0 | [6 empty] | 720
80 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
81 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
82 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | 2016-09-06 | 16:43 | 2016-09-06 | 17:21 | -- | -- | -- |  | 0.63333 |  |  | N/A | N/A | N/A | Tripped due to failure of Bus Reactor CB at Kalapaka Switchyard |  | 100 | 720
[5 empty] | -- | 2016-09-09 | 8:59 | 2016-09-09 | 11:24 | -- | -- | -- |  |  |  | 2.4167 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for RTV coating to the connected equipment vide SRLDC code CR09/281 |  |  | 720
[5 empty] | -- | 2016-09-28 | 23:05 | 2016-09-28 | 23:50 | -- | -- | -- |  | 0.75 |  |  | N/A | N/A | N/A | Tripped at 220kV side only on operation of Busbar protection at 220kV TSTRANSCO SS |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.3833 | 0 | 2.4167 | [6 empty] | 720
83 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | 2016-09-06 | 15:48 | 2016-09-06 | 18:39 | -- | -- | -- |  |  |  | 2.85 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for RTV coating to the connected equipment vide SRLDC code CR09/121 |  | 100 | 720
[5 empty] | -- | 2016-09-08 | 10:16 | 2016-09-08 | 11:36 | -- | -- | -- |  |  |  | 1.3333 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for RTV coating to the connected equipment vide SRLDC code CR09/252 |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.1833 | [6 empty] | 720
84 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | 2016-09-01 | 10:22 | 2016-09-01 | 18:02 | -- | -- | -- |  |  |  | 7.6667 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for attending hotspot at their end vide SRLDC code CR09/10 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.6667 | [6 empty] | 720
85 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
86 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | 2016-09-08 | 10:07 | 2016-09-08 | 18:26 | -- | -- | -- | 8.3167 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC Code: CR09/251 |  | 98.8389 | 720
[5 empty] | -- | 2016-09-21 | 19:10 | 2016-09-21 | 22:54 | -- | -- | -- |  | 3.7333 |  |  | N/A | N/A | N/A | Tripped at 220kV side only on operation of Busbar protection at 220kV TSTRANSCO SS |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 8.3167 | 3.7333 | 0 | 0 | [6 empty] | 720
87 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
88 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- | 2016-09-21 | 19:10 | 2016-09-21 | 22:56 | -- | -- | -- |  | 3.7667 |  |  | N/A | N/A | N/A | Tripped at 220kV side only on operation of Busbar protection at 220kV TSTRANSCO SS |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 3.7667 | 0 | 0 | [6 empty] | 720
89 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
90 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | 2016-09-06 | 10:08 | 2016-09-06 | 17:02 | -- | -- | -- | 6.9 |  |  |  | N/A | N/A | N/A | Shutdown availed for AMP works vide SRLDC code CR09/107 |  | 99.0417 | 720
[6 empty] | Sub Total --> | [6 empty] | 6.9 | 0 | 0 | 0 | [6 empty] | 720
91 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
92 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
93 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
94 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
95 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
96 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | 2016-09-12 | 10:18 | 2016-09-12 | 19:39 | -- | -- | -- |  |  |  | 9.35 | N/A | N/A | N/A | Shutdown availed for CSD commissioning works vide SRLDC code: CR09/359 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.35 | [6 empty] | 720
97 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
98 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | 2016-09-13 | 10:11 | 2016-09-13 | 11:44 | -- | -- | -- | 1.55 |  |  |  | N/A | N/A | N/A | Shutdown availed for installation of new PRD micro switch vide SRLDC code: CR09/388 |  | 99.7847 | 720
[6 empty] | Sub Total --> | [6 empty] | 1.55 | 0 | 0 | 0 | [6 empty] | 720
99 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
100 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | 2016-09-09 | 11:10 | 2016-09-09 | 13:13 | -- | -- | -- |  |  |  | 2.05 | N/A | N/A | N/A | Shutdown availed by M/s APTRANSCO for attending hotspot vide SRLDC code CR09/290 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.05 | [6 empty] | 720
101 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
102 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
103 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
104 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
105 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
106 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
107 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
108 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
109 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
110 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
111 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | 2016-09-15 | 6:04 | 2016-09-15 | 7:57 | -- | -- | -- |  |  | 1.8833 |  | N/A | N/A | N/A | Tripped on maloperation of PRD due to heavy rain. |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.8833 | 0 | [6 empty] | 720
112 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
113 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
114 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
115 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
116 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
117 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
118 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2016-09-01 | 0:00 | 2016-10-01 | 0:00 | -- | -- | -- |  |  |  | 720 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code: CR08/606 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 720 | [6 empty] | 720
119 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | 2016-09-25 | 19:12 | 2016-09-25 | 20:22 | -- | -- | -- | 1.17 |  |  |  | N/A | N/A | N/A | Pole-1 gone to Standby mode due to operation of Inter Zone prot |  | 99.3236 | 720
[5 empty] | -- | 2016-09-28 | 23:27 | 2016-09-29 | 3:09 | -- | -- | -- | 3.7 |  |  |  | N/A | N/A | N/A | Blocked due to tripping of CWD20Q52CB (Main Bay of East Bus Filter) on Hydraulic pressure low |  |  | 720
[6 empty] | Sub Total --> | [6 empty] | 4.87 | 0 | 0 | 0 | [6 empty] | 720
120 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
121 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
122 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
|  |  | Note in type of failure column please indicate following : | [9 empty] | 39.6367 | 11.0667 | 8.9 | 4314.8333
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse