## SOP
Standard of Performance data for the month of June-2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - I
ANNEXURE-A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | KURNOOL(NEW) - NELLOREPS - I | 302.303 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-02 | 20:29 |  |  |  | 0 | 0 | 2.8 | 0 |  |  |  | 765kV Kurnool-NPS Line-1 tripped on Zone-1 protection operation at Kurnool end due to jumper dislocation near isolators due to heavy gale winds | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 20:29 | 2019-06-03 | 9:41 |  |  |  | 0 | 0 | 0 | 13.2 |  |  |  | Line kept under LVRD vide SR-85 &NL-62
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 2.8 | 13.2 | [6 empty] | 744
2 | SR1L02 | KURNOOL(NEW) - NELLOREPS - II | 302.303 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-02 | 17:46 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped on O/V at Kurnool end | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 17:46 | 2019-06-02 | 20:35 |  |  |  | 0 | 0 | 0 | 2.8167 |  |  |  | Tripped on O/V at Kurnool end. kept under voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 2.8167 | [6 empty] | 744
3 | SR1L03 | KURNOOL(NEW) - TIRUVALUM - I | 355.01 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
4 | SR1L04 | KURNOOL(NEW) - TIRUVALUM - II | 355.01 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
5 | SR1L05 | RAICHUR(NEW) - KURNOOL(NEW) - I | 120.482 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-02 | 19:43 |  |  |  | 2.0333 | 0 | 0 | 0 |  |  |  | 765kV Raichur-Kurnool-1 line tripped on Y-N fault. A/R attempted successful at both ends but line tripped due to persisitng fault in A/R reclaim time. FD: 120Kms, FC 4.5kA from RCN end. FD 0Kms, FC: 5.5kA from Kurnool end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.4005 | 744
[6 empty] | 2019-06-03 | 9:51 | 2019-06-03 | 19:43 |  |  |  | 9.8667 | 0 | 0 | 0 |  |  |  | H/T vide code SR-114,NL-86 for AMP and insulator replacement works
[6 empty] | Sub Total --> | [6 empty] | 11.9 | 0 | 0 | 0 | [6 empty] | 744
6 | SR1L06 | RAICHUR(NEW) - KURNOOL(NEW) - II | 118.423 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-02 | 17:46 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped on O/V at Kurnool end | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 17:46 | 2019-06-02 | 19:57 |  |  |  | 0 | 0 | 0 | 2.1833 |  |  |  | Tripped on O/V at Kurnool end. kept under voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 2.1833 | [6 empty] | 744
7 | SR1L07 | RAICHUR(NEW) - SHOLAPUR - I | 207.754 | SR-I | -- | 2019-06-03 | 16:56 | 2019-06-03 | 16:56 |  |  |  | 1.5521e-11 | 0 | 0 | 0 |  |  |  | A/R successful on R-N fault (Fault details at Raichur end M1:213.3KM,2.3KA & M2:207.3KM,2.3KA) | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.1532 | 744
[6 empty] | 2019-06-09 | 5:16 | 2019-06-09 | 11:34 |  |  |  | 6.3 | 0 | 0 | 0 |  |  |  | H/T on emergency for attending hotspot in Line isolator at Sholapur end vide SR-466,NL-357,WR-712
[6 empty] | Sub Total --> | [6 empty] | 6.3 | 0 | 0 | 0 | [6 empty] | 744
8 | SR1L08 | ALMATHY - THIRUVALAM I | 40.969 |  | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
9 | SR1L09 | ALMATHY - THIRUVALAM II | 40.969 |  | -- | -- | -- | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
10 | SR1L10 | ALMATHY - VALLUR - I | 36.348 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
11 | SR1L11 | ALMATHY - VALLUR - II | 36.348 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
12 | SR1L12 | GAJWEL - HYDERABAD | 62.496 | SR-I | -- | 2019-06-11 | 11:11 | 2019-06-11 | 15:51 |  |  |  | 0 | 0 | 0 | 4.6667 |  |  |  | S/D availed by TSTRANSCO vide SRLDC code SR06/588. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.6667 | [6 empty] | 744
13 | SR1L13 | GOOTY - NELAMANGALA | 256.13 | SR-I | -- | 2019-06-22 | 4:06 | 2019-06-22 | 4:48 |  |  |  | 0 | 0 | 0.7 | 0 |  |  |  | Tripped at other end due to over voltage at NLM due to NLM-Hiryur line reactor failure as per NLM ss. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-22 | 4:48 | 2019-06-22 | 5:42 |  |  |  | 0 | 0 | 0 | 0.9 |  |  |  | H/T on voltage regulation vide SR-1379
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.7 | 0 | [6 empty] | 744
14 | SR1L14 | GOOTY - RAICHUR(NEW) - I | 128.7 | SR-I | -- | 2019-06-02 | 19:58 | 2019-06-02 | 19:58 |  |  |  | -5.0445e-11 | 0 | 0 | 0 |  |  |  | A/R successful on Y-N falut.RCR End:Dist.-146KM &FC-5.0KA | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | -5.0445e-11 | 0 | 0 | 0 | [6 empty] | 744
15 | SR1L15 | GOOTY - RAICHUR(NEW) - II | 128.7 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
16 | SR1L16 | GOOTY - PAVAGADA 1 | 208.621 | SR-I | -- | 2019-06-02 | 20:01 | 2019-06-02 | 20:01 |  |  |  | -6.2086e-11 | 0 | 0 | 0 |  |  |  | A/R successful on B-N falut.Gooty SS End:Dist.-15.55KM &FC-12.268KA | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | -6.2086e-11 | 0 | 0 | 0 | [6 empty] | 744
17 | SR1L17 | GOOTY - PAVAGADA 2 | 208.621 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
18 | SR1L18 | HYDERABAD - KURNOOL | 226.5 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
19 | SR1L19 | HYDERABAD - N'SAGAR | 155.264 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
20 | SR1L20 | JEYPORE - GAJUWAKA - I | 220 | SR-I | -- | 2019-06-21 | 17:00 | 2019-06-21 | 17:00 |  |  |  | 5.8207e-11 | 0 | 0 | 0 |  |  |  | A/R successful on RN fault.fault details GWK end: M1: 74KM, 1.28kA & M2: 66.8KM, 1.2kA | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-27 | 22:47 | 2019-06-27 | 23:37 |  |  |  | 0 | 0 | 0.83333 | 0 |  |  |  | AR. Successuful on R-N fault. Tripped on receipt of DT from Jeypore end. Fault details: GWK en: M1: FC-1.95 KA,FD-68.2 KM,M2: FC-1.87KA,FD-69.83 Km, Jeypore end: M1: FC-2.01 KA,Fd-119.2 Km,M2: FC-1.73KA,Fd-130.7KM. O/V at Jeypore end during dead time
[6 empty] | Sub Total --> | [6 empty] | 5.8207e-11 | 0 | 0.83333 | 0 | [6 empty] | 744
21 | SR1L21 | JEYPORE - GAJUWAKA - II | 220 | SR-I | -- | 2019-06-21 | 16:44 | 2019-06-21 | 16:44 |  |  |  | 6.2086e-11 | 0 | 0 | 0 |  |  |  | A/R successful on RN fault.fault details GWK end: M1: 65.7KM, 1.88kA & M2: 62.96KM, 1.6kA | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.9082 | 744
[6 empty] | 2019-06-27 | 16:52 | 2019-06-27 | 17:33 |  |  |  | 0.68333 | 0 | 0 | 0 |  |  |  | Line Tripped on Y-N fault. A/R is in NA mode for PID testing of Jeypore TLM
[6 empty] | Sub Total --> | [6 empty] | 0.68333 | 0 | 0 | 0 | [6 empty] | 744
22 | SR1L22 | KADAPA - NPKUNTA | 9.512 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
23 | SR1L23 | KHAMMAM - N'SAGAR I | 144.577 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
24 | SR1L24 | KHAMMAM - VIJAYAWADA | 114.775 | SR-I | -- | 2019-06-18 | 9:10 | 2019-06-18 | 19:33 |  |  |  | 10.3833 | 0 | 0 | 0 |  |  |  | H/T vide SR-1051 for AMP works | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
25 | SR1L25 | KURNOOL(PG) - GOOTY | 112.609 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
26 | SR1L26 | KURNOOL(AP) - GOOTY | 84.19 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
27 | SR1L27 | KURNOOL - KURNOOL(NEW) - I | 9.88 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
28 | SR1L28 | KURNOOL - KURNOOL(NEW) - II | 9.88 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
29 | SR1L29 | MAHBOOBNAGAR - RAICHUR | 73.68 | SR-I | -- | 2019-06-15 | 10:53 | 2019-06-15 | 18:03 |  |  |  | 0 | 0 | 0 | 7.1667 |  |  |  | Shutdown availed by TSTransco for Line works. Vide code: SR-891 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.1667 | [6 empty] | 744
30 | SR1L30 | MALKARAM - HYDERABAD | 27.87 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
31 | SR1L31 | NELLOREPS - GOOTY - I | 289.004 | SR-I | -- | 2019-06-01 | 0:00 | 2019-06-06 | 19:15 |  |  |  | 0 | 0 | 139.25 | 0 |  |  |  | line tripped on Y to B-N (Ph-Ph-G) fault. FD:81.07Kms, FC:8.17kA from GTY end. FD:205.5kms, FC:3.73 kms from NPS end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-21 | 10:07 | 2019-06-21 | 10:56 |  |  |  | 0 | 0 | 0 | 0.81667 |  |  |  | For ERS guy wire shifting to facilitate stringing
[6 empty] | 2019-06-28 | 10:34 | 2019-06-28 | 15:19 |  |  |  | 0 | 0 | 0 | 4.75 |  |  |  | H/T for line restoration works on permanent towers vide code SR 1823
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 139.25 | 5.5667 | [6 empty] | 744
32 | SR1L32 | NELLOREPS - GOOTY - II | 289.004 | SR-I | -- | 2019-06-01 | 0:00 | 2019-06-27 | 17:30 |  |  |  | 0 | 0 | 641.5 | 0 |  |  |  | line tripped on R to Y-N (Ph-Ph-G) fault. FD:84.15Kms, FC:8.226kA from GTY end. FD:198.35kms, FC:2.415 kms from NPS end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 641.5 | 0 | [6 empty] | 744
33 | SR1L33 | NELLOREPS - MEPL | 3.83 | SR-I | -- | 2019-06-13 | 10:17 | 2019-06-13 | 17:52 |  |  |  | 0 | 0 | 0 | 7.5833 |  |  |  | SD availed by MEPL vide code SR746 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.5833 | [6 empty] | 744
34 | SR1L34 | NELLOREPS - SEPL | 3.83 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
35 | SR1L35 | NELLOREPS - NCC - I | 33.58 | SR-I | -- | 2019-06-25 | 10:24 | 2019-06-26 | 21:58 |  |  |  | 0 | 0 | 0 | 35.5667 |  |  |  | H/T for LDP relay retrofitting works vide code SR1569 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.5667 | [6 empty] | 744
36 | SR1L36 | NELLOREPS - NCC - II | 32.73 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
37 | SR1L37 | NELLOREPS - NELLORE - I | 3.65 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
38 | SR1L38 | NELLOREPS - NELLORE - II | 3.65 | SR-I | -- | 2019-06-01 | 0:00 | 2019-06-01 | 12:56 |  |  |  | 0 | 0 | 0 | 12.9333 |  |  |  | Line under bypassed conditin at Nellore end,it is on single braeker . Tripped during Nellore -Thiruvalam 2 tripping | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.9333 | [6 empty] | 744
39 | SR1L39 | NELLORE - SIRIPERUMBUDUR I | 189 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
40 | SR1L40 | NELLORE - SIRIPERUMBUDUR II | 189 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-02 | 17:51 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | Tripped on O/V at Sriperumbudur end.Kept under LVRD vide SR-96 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 17:51 | 2019-06-04 | 8:50 |  |  |  | 0 | 0 | 0 | 38.9833 |  |  |  | Tripped on O/V at Sriperumbudur end.Kept under LVRD vide SR-96
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 38.9833 | [6 empty] | 744
41 | SR1L41 | NELLORE - TIRUVALUM - I | 172.964 | SR-I | -- | 2019-06-28 | 9:41 | 2019-06-28 | 20:14 |  |  |  | 10.55 | 0 | 0 | 0 |  |  |  | H/T for insulator replacement works vide code SR1813 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.582 | 744
[6 empty] | Sub Total --> | [6 empty] | 10.55 | 0 | 0 | 0 | [6 empty] | 744
42 | SR1L42 | NELLORE - TIRUVALUM - II | 172.964 | SR-I | -- | 2019-06-01 | 0:00 | 2019-06-01 | 12:56 |  |  |  | 12.9333 | 0 | 0 | 0 |  |  |  | Line tripped on R-B fault. Fault Details: Nellore end: FC:R-Ph-2.8KA, B-Ph-3.8kA Dist. 154.7km and Thiruvalam end: FC:19KA,Distance:21km. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 96.8548 | 744
[6 empty] | 2019-06-29 | 9:06 | 2019-06-29 | 19:34 |  |  |  | 10.4667 | 0 | 0 | 0 |  |  |  | H/T for insulator replacement Vide SR-1897, S/D availed by SR2
[6 empty] | Sub Total --> | [6 empty] | 23.4 | 0 | 0 | 0 | [6 empty] | 744
43 | SR1L43 | NELLOREPS - TPCIL - I | 32.73 | SR-I | -- | 2019-06-21 | 8:35 | 2019-06-21 | 19:28 |  |  |  | 0 | 0 | 0 | 10.8833 |  |  |  | H/T vide SR-1166 for distance relay retorfitting works | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.8833 | [6 empty] | 744
44 | SR1L44 | NELLOREPS - TPCIL - II | 32.73 | SR-I | -- | 2019-06-18 | 7:59 | 2019-06-18 | 20:46 |  |  |  | 0 | 0 | 0 | 12.7833 |  |  |  | H/T for distnce relay retorfitting works vide SR-1166 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-19 | 10:46 | 2019-06-20 | 7:03 |  |  |  | 0 | 0 | 0 | 20.2833 |  |  |  | H/T for LDP relay retorfitting works vide SR-1166
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33.0667 | [6 empty] | 744
45 | SR1L45 | N'SAGAR - KADAPA - I | 277.325 | SR-I | -- | 2019-06-07 | 9:31 | 2019-06-07 | 17:35 |  |  |  | 8.0667 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-383 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.9158 | 744
[6 empty] | Sub Total --> | [6 empty] | 8.0667 | 0 | 0 | 0 | [6 empty] | 744
46 | SR1L46 | N'SAGAR - KADAPA - II | 278.664 | SR-I | -- | 2019-06-06 | 10:04 | 2019-06-06 | 19:26 |  |  |  | 9.3667 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-314 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.741 | 744
[6 empty] | Sub Total --> | [6 empty] | 9.3667 | 0 | 0 | 0 | [6 empty] | 744
47 | SR1L47 | N'SAGAR - KURNOOL(NEW) | 264.954 | SR-I | -- | 2019-06-24 | 0:41 | 2019-06-24 | 3:06 |  |  |  | 2.4167 | 0 | 0 | 0 |  |  |  | Tripped due to NGR buchholz maloperation at N'Sagar end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.6752 | 744
[6 empty] | Sub Total --> | [6 empty] | 2.4167 | 0 | 0 | 0 | [6 empty] | 744
48 | SR1L48 | N'SAGAR - MAHBOOBNAGAR | 184.35 | SR-I | -- | 2019-06-02 | 16:40 | 2019-06-02 | 16:50 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | Line tripped on Over voltage stage-1 protn opern at Mahaboobnagar end | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 16:50 | 2019-06-03 | 12:41 |  |  |  | 0 | 0 | 0 | 19.85 |  |  |  | Tripped on O/V at Mehboobnagar SS end .Kept under LVRD vide SR-69 |  |  | 744
[6 empty] | 2019-06-13 | 11:07 | 2019-06-13 | 17:25 |  |  |  | 0 | 0 | 0 | 6.3 |  |  |  | S/D availed by TSTRANSCO for relay testing at MBNR vide SR754 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 26.15 | [6 empty] | 744
49 | SR1L49 | NPKUNTA - KOLAR | 9.512 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
50 | SR1L50 | RAICHUR - MUNIRABAD | 172.44 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
51 | SR1L51 | RAICHUR(NEW) - RAICHUR - I | 22.219 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
52 | SR1L52 | RAICHUR(NEW) - RAICHUR - II | 22.219 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
53 | SR1L53 | RAMAGUNDAM - CHANDRAPUR - I | 177.6 | SR-I | -- | 2019-06-03 | 19:21 | 2019-06-03 | 19:21 |  |  |  | 3.4924e-11 | 0 | 0 | 0 |  |  |  | A/R successful on B-N fault. Fault distance: 102.8 Kms from RDM. FD:63.1 Kms , FC: 2.5kA from Chnadrapur end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.5565 | 744
[5 empty] | -- | 2019-06-04 | 20:56 | 2019-06-05 | 0:14 |  |  |  | 3.3 | 0 | 0 | 0 |  |  |  | line tripped due to L/R protection maloperation at Chandrapur end. |  |  | 744
[5 empty] | -- | 2019-06-08 | 1:39 | 2019-06-08 | 9:48 |  |  |  | 0 | 0 | 0 | 8.15 |  |  |  | H/T on voltage regulation vide SR-432,NL-325,WR-617 |  |  | 744
[6 empty] | Sub Total --> | [6 empty] | 3.3 | 0 | 0 | 8.15 | [6 empty] | 744
54 | SR1L54 | RAMAGUNDAM - CHANDRAPUR - II | 177.6 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
55 | SR1L55 | RAMAGUNDAM - GAJWEL | 124.765 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
56 | SR1L56 | RAMAGUNDAM - HYDERABAD - III | 201.236 | SR-I | -- | 2019-06-02 | 13:26 | 2019-06-02 | 13:39 |  |  |  | 0.21667 | 0 | 0 | 0 |  |  |  | Tripped on R-N fault at Ramagundam end and holding at Hyderabad end.Hyderabad end:Dsit.139.082KM,FC-3.2KA | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.9709 | 744
[6 empty] | Sub Total --> | [6 empty] | 0.21667 | 0 | 0 | 0 | [6 empty] | 744
57 | SR1L57 | RAMAGUNDAM - HYDERABAD - IV | 201.236 | SR-I |  | 2019-06-11 | 12:27 | 2019-06-11 | 13:19 |  |  |  | 0.86667 | 0 | 0 | 0 |  |  |  | line tripped on YB fault.Dist:140.4KM(M1),138.2KM(M2) FC: Y PH 3.07KA(M1),3.02KA(M2), B-Ph 3.57KA(M1),3.58KA(M2) From Hyderabad end | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.8835 | 744
[6 empty] | Sub Total --> | [6 empty] | 0.86667 | 0 | 0 | 0 | [6 empty] | 744
58 | SR1L58 | RAMAGUNDAM - MALKARAM | 166.212 | SR-I | -- | 2019-06-03 | 7:10 | 2019-06-03 | 21:01 |  |  |  | 13.85 | 0 | 0 | 0 |  |  |  | H/T on emergency by NTPC Ramagundam | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.1384 | 744
[6 empty] | Sub Total --> | [6 empty] | 13.85 | 0 | 0 | 0 | [6 empty] | 744
59 | SR1L59 | RAMAGUNDAM - N'SAGAR - I | 267.2 | SR-I | -- | 2019-06-18 | 7:51 | 2019-06-19 | 19:39 |  |  |  | 0 | 0 | 0 | 35.8 |  |  |  | S/D availed by NTPC vide Sr06/367 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.8 | [6 empty] | 744
60 | SR1L60 | RAMAGUNDAM - N'SAGAR - II | 267.2 | SR-I | -- | 2019-06-20 | 9:06 | 2019-06-21 | 18:56 |  |  |  | 0 | 0 | 0 | 33.8333 |  |  |  | H/T for AMP vide SR-1240 on request of NTPC | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33.8333 | [6 empty] | 744
61 | SR1L61 | RAMAGUNDAM - WARANGAL | 98.803 | SR-I | -- | 2019-06-08 | 0:22 | 2019-06-12 | 8:49 |  |  |  | 0 | 0 | 0 | 104.45 |  |  |  | H/T on voltage regulation vide SR-428 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-21 | 2:31 | 2019-06-21 | 9:44 |  |  |  | 0 | 0 | 0 | 7.2167 |  |  |  | H/T on voltage regulation vide SR-1303
[6 empty] | 2019-06-21 | 23:43 | 2019-06-24 | 14:49 |  |  |  | 0 | 0 | 0 | 63.1 |  |  |  | H/T on voltage regulation vide SR-1374
[6 empty] | 2019-06-30 | 1:44 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 22.2667 |  |  |  | H/T for voltage regulation Vide SR-1955
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 197.0333 | [6 empty] | 744
62 | SR1L62 | SIMHADRI - GAJUWAKA - I | 13.233 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
63 | SR1L63 | SIMHADRI - GAJUWAKA - II | 13.272 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
64 | SR1L64 | VEMAGIRI - SIMHADRI - I | 193.326 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
65 | SR1L65 | VEMAGIRI - SIMHADRI - II | 193.326 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
66 | SR1L66 | VIJAYAWADA - GAJUWAKA | 316.899 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
67 | SR1L67 | VIJAYAWADA - NELLORE - I | 340 | SR-I | -- | 2019-06-01 | 3:17 | 2019-06-01 | 3:27 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | Line tripped on Over voltage stage-1 protn opern at Nellore end | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-01 | 3:27 | 2019-06-01 | 7:56 |  |  |  | 0 | 0 | 0 | 4.4833 |  |  |  | line kept out of service for voltage regulation vide SR-07, NL- 03
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 4.4833 | [6 empty] | 744
68 | SR1L68 | VIJAYAWADA - NELLORE - II | 340 | SR-I | -- | 2019-06-02 | 18:03 | 2019-06-02 | 19:03 |  |  |  | 0 | 0 | 1 | 0 |  |  |  | Tripped on O/V at Nellore end while charging 400KV Nellore-Sriperumbudur Line-2. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 0 | [6 empty] | 744
69 | SR1L69 | VIJAYAWADA-NELLORE(AP) | 330.393 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
70 | SR1L70 | VIJAYAWADA - VEMAGIRI - III | 195.21 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
71 | SR1L71 | VIJAYAWADA - VEMAGIRI - IV | 195.21 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
72 | SR1L72 | VTPS-NELLORE(AP) | 330.87 | SR-I | -- | 2019-06-28 | 10:23 | 2019-06-28 | 19:04 |  |  |  | 0 | 0 | 0 | 8.6833 |  |  |  | H/T on request of APTRANSCO vide cods SR1819 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.6833 | [6 empty] | 744
73 | SR1L73 | WARANGAL - KHAMMAM | 117.087 | SR-I | -- | 2019-06-12 | 9:41 | 2019-06-12 | 23:09 |  |  |  | 13.4667 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide Code SR-651 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.19 | 744
[6 empty] | Sub Total --> | [6 empty] | 13.4667 | 0 | 0 | 0 | [6 empty] | 744
74 | SR1L74 | VEMAGIRI(PG) - GAZUWAKA | 165.454 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
75 | SR1L75 | VIJAYAWADA - VEMAGIRI(PG) | 187.8 | SR-I |  | 2019-06-05 | 9:12 | 2019-06-05 | 13:52 |  |  |  | 4.6667 | 0 | 0 | 0 |  |  |  | Hant tripped for AMP vide code SR-262 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.3728 | 744
[6 empty] | 2019-06-09 | 16:20 | 2019-06-09 | 16:20 |  |  |  | -1.94e-11 | 0 | 0 | 0 |  |  |  | A/R successful on B-N fault.Vemagiri End:FC-2.38KA &Dist.-135.38KM
[6 empty] | Sub Total --> | [6 empty] | 4.6667 | 0 | 0 | 0 | [6 empty] | 744
76 | SR1L76 | MAHESHWARAM-KURNOOL AP | 174.996 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1L77 | NiZAMABAD-DICHPALLY 1 | 4.428 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1L78 | NiZAMABAD-DICHPALLY 2 | 4.428 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1L79 | NIZAMABAD-MAHESHWARAM 1 | 243.059 | SR-I |  | 2019-06-01 | 3:54 | 2019-06-04 | 11:04 |  |  |  | 0 | 0 | 0 | 79.1667 |  |  |  | H/T on voltage regulation vide SR-07, NL- 03 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.069 | 744
[6 empty] | 2019-06-04 | 11:06 | 2019-06-05 | 1:28 |  |  |  | 14.3667 | 0 | 0 | 0 |  |  |  | H/T on emergency due to hotspot observed in Line Bay
[6 empty] | 2019-06-08 | 1:24 | 2019-06-08 | 7:46 |  |  |  | 0 | 0 | 0 | 6.3667 |  |  |  | H/T on voltage regulation vide SR-430,NL-323
[6 empty] | Sub Total --> | [6 empty] | 14.3667 | 0 | 0 | 85.5333 | [6 empty] | 744
80 | SR1L80 | NIZAMABAD-MAHESHWARAM 2 | 243.059 | SR-I |  | 2019-06-04 | 11:06 | 2019-06-04 | 11:22 |  |  |  | 0.26667 | 0 | 0 | 0 |  |  |  | H/T on emergency due to hotspot observed in Line Bay | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.9642 | 744
[6 empty] | 2019-06-07 | 1:11 | 2019-06-07 | 11:03 |  |  |  | 0 | 0 | 0 | 9.8667 |  |  |  | H/T on voltage regulation vide SR-362
[6 empty] | 2019-06-09 | 17:38 | 2019-06-10 | 7:52 |  |  |  | 0 | 0 | 0 | 14.2333 |  |  |  | H/T on voltage regulation vide SR-485 &NL-364
[6 empty] | 2019-06-12 | 23:39 | 2019-06-19 | 10:30 |  |  |  | 0 | 0 | 0 | 154.85 |  |  |  | H/T on voltage regulation vide SR-485 &NL-364
[6 empty] | 2019-06-21 | 23:53 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 216.1167 |  |  |  | H/T on voltage regulation vide SR-1377 & NL-857
[6 empty] | Sub Total --> | [6 empty] | 0.26667 | 0 | 0 | 395.0667 | [6 empty] | 744
81 | SR1L81 | NIZAMABAD-WARDHA 1 | 291.2 | SR-I |  | 2019-06-04 | 16:54 | 2019-06-04 | 19:37 |  |  |  | 0 | 0 | 2.7167 | 0 |  |  |  | Line tripped on Y-N fault (Fault details at Nizamabad end:278.9KM,1.35KA.). Substation fault due to heavy whirl winds | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-07 | 15:28 | 2019-06-07 | 15:28 |  |  |  | -5.0448e-11 | 0 | 0 | 0 |  |  |  | A/R operated Successful at both ends on R-N fault (Fault details at Nizamabad end:278.6KM,1.448KA,Wardha end:1.5KM,23.9KA)
[6 empty] | 2019-06-04 | 16:54 | 2019-06-04 | 19:37 |  |  |  | 0 | 0 | 2.7167 | 0 |  |  |  | Line tripped on Y-N fault (Fault details at Nizamabad end:278.9KM,1.35KA.). Substation fault due to heavy whirl winds
[6 empty] | 2019-06-07 | 15:28 | 2019-06-07 | 15:28 |  |  |  | -5.0448e-11 | 0 | 0 | 0 |  |  |  | A/R operated Successful at both ends on R-N fault (Fault details at Nizamabad end:278.6KM,1.448KA,Wardha end:1.5KM,23.9KA)
[6 empty] | Sub Total --> | [6 empty] | -1.009e-10 | 0 | 5.4333 | 0 | [6 empty] | 744
82 | SR1L82 | NIZAMABAD-WARDHA 2 | 291.2 | SR-I |  | 2019-06-04 | 16:54 | 2019-06-04 | 19:37 |  |  |  | 0 | 0 | 2.7167 | 0 |  |  |  | Line tripped on Y-N fault (Fault details at Nizamabad end:278.9KM,1.35KA.). Substation fault due to heavy whirl winds | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-07 | 15:28 | 2019-06-07 | 15:28 |  |  |  | -5.0448e-11 | 0 | 0 | 0 |  |  |  | A/R operated Successful at both ends on R-N fault (Fault details at Nizamabad end:278.6KM,1.448KA,Wardha end:1.5KM,23.9KA)
[6 empty] | Sub Total --> | [6 empty] | -5.0448e-11 | 0 | 2.7167 | 0 | [6 empty] | 744
83 | SR1L83 | VIJAYAWADA-VEMAGIRI PG 1 | 187.8 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1L84 | VIJAYAWADA-VEMAGIRI PG 2 | 187.8 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1L85 | VIJAYAWADA-VEMAGIRI PG 3 | 187.8 | SR-I |  | 2019-06-09 | 15:42 | 2019-06-09 | 16:14 |  |  |  | 0.53333 | 0 | 0 | 0 |  |  |  | Tripped on Y-N fault;Vijayawada end:FC-2.603KA&Dist.-157.3KM | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.8118 | 744
[6 empty] | 2019-06-10 | 9:18 | 2019-06-10 | 10:10 |  |  |  | 0.86667 | 0 | 0 | 0 |  |  |  | Line tripped on L/R Differential protection operation at VJA end. DT send to VMGR end.
[6 empty] | Sub Total --> | [6 empty] | 1.4 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1L86 | KADAPA- CHITTOOR | 147.14 | SR-I |  | 2019-06-13 | 9:12 | 2019-06-13 | 11:56 |  |  |  | 2.7333 | 0 | 0 | 0 |  |  |  | H/T on emergency for tightning sag adjustment bolt at Loc102 vide SR739 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.6326 | 744
[6 empty] | Sub Total --> | [6 empty] | 2.7333 | 0 | 0 | 0 | [6 empty] | 744
87 | SR1L87 | VEMAGIRI PG - SIMHADRI-I | 180.98 | SR-I |  | 2019-06-21 | 8:25 | 2019-06-21 | 8:25 |  |  |  | 1.9403e-11 | 0 | 0 | 0 |  |  |  | A/R successful on BN fault.fault details at Vemagiri end:M1-22.79KM,9.709KA & M2-22.89KM,8.88KA | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.5116 | 744
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | 2019-06-22 | 9:46 | 2019-06-22 | 13:24 |  |  |  | 3.6333 | 0 | 0 | 0 |  |  |  | H/T for replacement of broken insulator vide SR-1397
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 3.6333 | 0 | 0 | 0 | [6 empty] | 744
88 | SR1L88 | VEMAGIRI PG - SIMHADRI-II | 180.98 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1L89 | VEMAGIRI PG - VEMAGIRI AP - I | 38.41 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
VEMAGIRI PG - SIMHADRI-I
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1L90 | VEMAGIRI PG - VEMAGIRI AP - II | 38.41 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
91 | SR1L91 | 400KV KADAPA - NP KUNTA - II | 68.69 | SR-I |  | 2019-06-01 | 0:00 | 2019-06-27 | 10:11 |  |  |  | 0 | 0 | 0 | 634.1833 |  |  |  | H/T vide code SR-850 for power regulation,continued from last month | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
|  | VEMAGIRI PG - SIMHADRI-I |  |  |  | Sub Total --> | [6 empty] | 0 | 0 | 0 | 634.1833 | [6 empty] | 744
92 | SR1L92 | 400KV KADAPA - NP KUNTA - III | 68.69 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
93 | SR1L93 | 765KV KADAPA-THIRUVALAM 1 | 245.7 | SR-I |  | 2019-06-02 | 23:23 | 2019-06-04 | 10:03 |  |  |  | 0 | 0 | 0 | 34.6667 |  |  |  | H/T on voltage regulation vide SR-102 &NL-75 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 34.6667 | [6 empty] | 744
94 | SR1L94 | 765KV KADAPA-THIRUVALAM 2 | 245.7 | SR-I |  | 2019-06-02 | 17:41 | 2019-06-02 | 17:46 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | tripped on operation of overvoltage stage-1 at kadapa end and DT receipt at TVLM end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 17:46 | 2019-06-02 | 23:09 |  |  |  | 0 | 0 | 0 | 5.3833 |  |  |  | tripped on operation of overvoltage stage-1 at kadapa end and DT receipt at TVLM end.. kept under voltage regulation
[6 empty] | 2019-06-23 | 2:53 | 2019-06-25 | 7:18 |  |  |  | 0 | 0 | 0 | 52.4167 |  |  |  | H/T on voltage regulation vide SR-1437 & NL-889
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 57.8 | [6 empty] | 744
95 | SR1L95 | 765KV KADAPA-KURNOOL 1 | 203.8 | SR-I | [16 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
96 | SR1L96 | 765KV KADAPA-KURNOOL 2 | 203.8 | SR-I |  | 2019-06-02 | 17:41 | 2019-06-02 | 17:46 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Tripped on operation of overvoltage stage-1 at Kurnool end and DT receipt at kadapa end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-02 | 17:46 | 2019-06-02 | 20:33 |  |  |  | 0 | 0 | 0 | 2.7833 |  |  |  | Tripped on operation of overvoltage stage-1 at Kurnool end and DT receipt at kadapa end.. kept under voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 2.7833 | [6 empty] | 744
97 | SR1L97 | 400KV NPKUNTA-HINDUPUR 1 |  | SR-I |  | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 720 |  |  |  | H/T on voltage regulation vide SR-717, continued from last month | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 720 | [6 empty] | 744
97 | SR1L98 | 400KV NPKUNTA-HINDUPUR 2 |  | SR-I |  | 2019-06-09 | 18:14 | 2019-06-09 | 18:24 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | Tripped on O/V at NPK end. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | 2019-06-09 | 18:24 | 2019-06-10 | 8:34 |  |  |  | 0 | 0 | 0 | 14.1667 |  |  |  | Line kept under LVRD vide SR-492 after tripping on O/V.
[6 empty] | 2019-06-26 | 9:47 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 110.2167 |  |  |  | Line H/T for voltage regulation vide SR/1634
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.16667 | 124.3833 | [6 empty] | 744
76 | SR1T01 | KURNOOL(NEW) ICT - I | 1500 | SR-I | -- | 2019-06-02 | 18:35 | 2019-06-02 | 19:48 |  |  |  | 1.2167 | 0 | 0 | 0 |  |  |  | H/T on emergency due to jumper hanging vide SR-75 &NL-55 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.8365 | 744
[6 empty] | Sub Total --> | [6 empty] | 1.2167 | 0 | 0 | 0 | [6 empty] | 744
77 | SR1T02 | KURNOOL(NEW) ICT - II | 1500 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-02 | 20:13 |  |  |  | 2.5333 | 0 | 0 | 0 |  |  |  | H/T on emergency due to jumper hanging | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.3996 | 744
[6 empty] | 2019-06-10 | 16:43 | 2019-06-10 | 18:39 |  |  |  | 1.9333 | 0 | 0 | 0 |  |  |  | H/T on emrgency to fix the V-string insulator vide SR-549&NL-394
[6 empty] | Sub Total --> | [6 empty] | 4.4667 | 0 | 0 | 0 | [6 empty] | 744
78 | SR1T03 | NELLOREPS ICT - II | 1500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
79 | SR1T04 | NELLOREPS ICT - III | 1500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
80 | SR1T05 | RAICHUR(NEW) ICT - I | 1500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
81 | SR1T06 | RAICHUR(NEW) ICT - II | 1500 | SR-I | -- | 2019-06-14 | 9:26 | 2019-06-14 | 13:20 |  |  |  | 3.9 | 0 | 0 | 0 |  |  |  | H/T For swapping with spare unit vide SR-812, NL-539 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.4758 | 744
[6 empty] | Sub Total --> | [6 empty] | 3.9 | 0 | 0 | 0 | [6 empty] | 744
82 | SR1T07 | CUDDAPAH ICT I | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
83 | SR1T08 | CUDDAPAH ICT II | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
84 | SR1T09 | GAJUWAKA ICT I | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
85 | SR1T10 | GAZUWAKA ICT II | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
86 | SR1T11 | GOOTY ICT I | 315 | SR-I | -- | -- | -- | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
87 | SR1T12 | GOOTY ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
88 | SR1T13 | HYDERABAD ICT - I | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
89 | SR1T14 | HYDERABAD ICT - II | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
90 | SR1T15 | HYDERABAD ICT - III | 315 | SR-I | -- |  |  |  |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
91 | SR1T16 | KHAMMAM ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
92 | SR1T17 | KHAMMAM ICT II | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
93 | SR1T18 | MUNIRABAD ICT I | 315 | SR-I | -- | 2019-06-24 | 20:50 | 2019-06-24 | 21:16 |  |  |  | 0 | 0.43333 | 0 | 0 |  |  |  | Tripped on Back up earth fault protection operated due to PT blast at Kalyani station | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.43333 | 0 | 0 | [6 empty] | 744
94 | SR1T19 | MUNIRABAD ICT II | 315 | SR-I | -- | 2019-06-03 | 2:14 | 2019-06-03 | 13:21 |  |  |  | 11.1167 | 0 | 0 | 0 |  |  |  | Tripped due to gasket at Bucholtz failed and Bucholtz operated. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.505 | 744
[6 empty] | 2019-06-24 | 20:50 | 2019-06-24 | 21:16 |  |  |  | 0 | 0.43333 | 0 | 0 |  |  |  | Tripped on Back up earth fault protection operated due to PT blast at Kalyani station
[6 empty] | Sub Total --> | [6 empty] | 11.1167 | 0.43333 | 0 | 0 | [6 empty] | 744
95 | SR1T20 | NAGARJUNASAGAR ICT - I | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
96 | SR1T21 | NAGARJUNASAGAR ICT - II | 315 | SR-I | -- | 2019-06-12 | 10:35 | 2019-06-12 | 13:24 |  |  |  | 0 | 0 | 0 | 2.8167 |  |  |  | S/D availed by APTRANSCO vide SRLDC code SR06/661. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.8051 | 744
[6 empty] | 2019-06-24 | 21:56 | 2019-06-24 | 23:23 |  |  |  | 1.45 | 0 | 0 | 0 |  |  |  | Tripped due to buchholz maloperation.
[6 empty] | Sub Total --> | [6 empty] | 1.45 | 0 | 0 | 2.8167 | [6 empty] | 744
97 | SR1T22 | NAGARJUNASAGAR ICT - III | 315 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
98 | SR1T23 | NPKUNTA ICT - I | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
99 | SR1T24 | NPKUNTA ICT - II | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
100 | SR1T25 | NPKUNTA ICT - III | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
101 | SR1T26 | VIJAYAWADA ICT I | 315 | SR-I | -- | 2019-06-16 | 6:15 | 2019-06-16 | 7:54 |  |  |  | 0 | 1.65 | 0 | 0 |  |  |  | Tripped at 220kV side due to CT failure(blast) in APTRANSCO switchyard leading to busbar protection operation at APTRANSCO. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.65 | 0 | 0 | [6 empty] | 744
102 | SR1T27 | VIJAYAWADA ICT II | 315 | SR-I | -- | 2019-06-16 | 6:15 | 2019-06-16 | 7:53 |  |  |  | 0 | 1.6333 | 0 | 0 |  |  |  | Tripped at 220kV side due to CT failure(blast) in APTRANSCO switchyard leading to busbar protection operation at APTRANSCO. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.6333 | 0 | 0 | [6 empty] | 744
103 | SR1T28 | WARANGAL ICT I | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
105 | SR1T29 | WARANGAL ICT II | 315 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
106 | SR1T30 | VEMAGIRI ICT I | 1500 | SR-I | -- | 2019-06-08 | 9:33 | 2019-06-08 | 19:21 |  |  |  | 9.8 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-446,NL-333 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.5125 | 744
[6 empty] | 2019-06-26 | 10:06 | 2019-06-26 | 11:22 |  |  |  | 1.2667 | 0 | 0 | 0 |  |  |  | H/T for Bushing oil sample vide code SR 1632 & NL 1029
[6 empty] | Sub Total --> | [6 empty] | 11.0667 | 0 | 0 | 0 | [6 empty] | 744
107 | SR1T31 | VEMAGIRI ICT II | 1500 | SR-I | -- | 2019-06-09 | 11:59 | 2019-06-09 | 17:34 |  |  |  | 5.5833 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-478,NL-360 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.0815 | 744
[6 empty] | 2019-06-26 | 11:42 | 2019-06-26 | 12:57 |  |  |  | 1.25 | 0 | 0 | 0 |  |  |  | H/T for Bushing oil sample vide code SR 1649 & NL 1035
[6 empty] | Sub Total --> | [6 empty] | 6.8333 | 0 | 0 | 0 | [6 empty] | 744
108 | SR1T32 | NIZAMABAD ICT I | 1500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
109 | SR1T33 | NIZAMABAD ICT II | 1500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
110 | SR1T34 | MAHESHWRAM ICT I | 1500 | SR-I | -- | 2019-06-24 | 10:06 | 2019-06-24 | 16:19 |  |  |  | 6.2167 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide code:SR-1484,NL-914 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.7746 | 744
[6 empty] | 2019-06-29 | 9:38 | 2019-06-29 | 12:32 |  |  |  | 2.9 | 0 | 0 | 0 |  |  |  | H/T for combination Changeover vide SR-1820 & NL-1200
[6 empty] | Sub Total --> | [6 empty] | 9.1167 | 0 | 0 | 0 | [6 empty] | 744
111 | SR1T35 | MAHESHWARAM ICT II | 1500 | SR-I | -- | 2019-06-28 | 10:19 | 2019-06-28 | 14:54 |  |  |  | 4.5833 | 0 | 0 | 0 |  |  |  | H/T for combination changeover vide code SR1820 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.384 | 744
[6 empty] | Sub Total --> | [6 empty] | 4.5833 | 0 | 0 | 0 | [6 empty] | 744
112 | SR1T36 | HYDERABAD ICT IV | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
113 | SR1T37 | GOOTY ICT III | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
114 | SR1T38 | KHAMMAM ICT III | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
115 | SR1T39 | WARANGAL ICT III | 500 | SR-I | -- | 2019-06-19 | 9:08 | 2019-06-19 | 18:22 |  |  |  | 9.2333 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-1147. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.759 | 744
[6 empty] | Sub Total --> | [6 empty] | 9.2333 | 0 | 0 | 0 | [6 empty] | 744
116 | SR1T40 | SRIKAKULAM 765/400kV ICT I | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
117 | SR1T41 | SRIKAKULAM 765/400kV ICT II | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
118 | SR1T42 | VIJAYAWADA ICT III | 500 | SR-I | -- | 2019-06-16 | 6:15 | 2019-06-16 | 7:22 |  |  |  | 0 | 1.1167 | 0 | 0 |  |  |  | Tripped at 220kV side due to CT failure(blast) in APTRANSCO switchyard leading to busbar protection operation at APTRANSCO. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.1167 | 0 | 0 | [6 empty] | 744
119 | SR1T43 | KADAPA ICT III | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
119 | SR1R01 | KURNOOL(NEW) BUS REACTOR | 240 | SR-I | -- | 2019-06-02 | 17:41 | 2019-06-03 | 1:04 |  |  |  | 0 | 0 | 7.3833 | 0 |  |  |  | Tripped on Differential protection operation due to dropper dislocations on heavy wind and rain. | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 7.3833 | 0 | [6 empty] | 744
120 | SR1R02 | NELLOREPS BUS REACTOR | 240 | SR-I | -- | 2019-06-27 | 9:52 | 2019-06-27 | 13:51 |  |  |  | 3.9833 | 0 | 0 | 0 |  |  |  | H/T for spare changeover vide code SR-1728,NL-1081 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.4646 | 744
[6 empty] | Sub Total --> | [6 empty] | 3.9833 | 0 | 0 | 0 | [6 empty] | 744
121 | SR1R03 | RAICHUR(NEW) BUS REACTOR | 240 | SR-I | -- | 2019-06-14 | 15:31 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 392.4833 |  |  |  | H/T on voltage regulation vide SR-843 NL 560 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 392.4833 | [6 empty] | 744
122 | SR1R04 | SHOLAPUR-I L/R AT RAICHUR(NEW) | 240 | SR-I | [5 empty] | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
123 | SR1R05 | SHOLAPUR-II L/R AT RAICHUR(NEW) | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
124 | SR1R06 | CUDDAPAH BUS REACTOR | 50 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
125 | SR1R07 | GOOTY BUS REACTOR | 63 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
126 | SR1R08 | GOOTY L/R AT NELAMANGALA END | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
127 | SR1R09 | HYDERABAD BUS REACTOR | 63 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
128 | SR1R10 | KHAMMAM BUS REACTOR | 50 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
129 | SR1R11 | MUNIRABAD BUS REACTOR | 63 | SR-I | -- | 2019-06-05 | 9:45 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 614.25 |  |  |  | Kept under voltage regulation vide code SR-270 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 614.25 | [6 empty] | 744
130 | SR1R12 | NAGARJUNASAGAR BUS REACTOR | 50 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
131 | SR1R13 | NELLORE BUS REACTOR | 80 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
132 | SR1R14 | NPKUNTA BUS REACTOR | 125 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
133 | SR1R15 | VIJAYAWADA BUS REACTOR | 63 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
134 | SR1R16 | VISAKHAPATNAM BUS REACTOR | 50 | SR-I | -- | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 720 |  |  |  | Line Kept under voltage regulation vide SR427, continued from last month | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 720 | [6 empty] | 744
135 | SR1R17 | 765 KV SRIKAKULAM-VEMAGIRI 2 LR | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
136 | SR1R18 | 765 KV SRIKAKULAM-VEMAGIRI 1 LR | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
137 | SR1R19 | 330MVAR BUS REACTOR at SKLM | 330 | SR-I | -- | 2019-06-17 | 12:03 | 2019-06-17 | 18:41 |  |  |  | 6.6333 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide SR-999 &NL-654 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.1084 | 744
[6 empty] | Sub Total --> | [6 empty] | 6.6333 | 0 | 0 | 0 | [6 empty] | 744
138 | SR1R20 | VEMAGIRI 240MVAR BUS REACTOR-I | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
139 | SR1R21 | VEMAGIRI 240MVAR BUS REACTOR-II | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
140 | SR1R22 | VEMAGIRI 80MVAR BUS REACTOR | 80 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
141 | SR1R23 | MAHESHWARAM BUS REACTOR 1 | 240 | SR-I | -- | 2019-06-14 | 9:38 | 2019-06-14 | 12:47 |  |  |  | 3.15 | 0 | 0 | 0 |  |  |  | H/T for AMP vide SR 816,NL 543 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.5766 | 744
[6 empty] | Sub Total --> | [6 empty] | 3.15 | 0 | 0 | 0 | [6 empty] | 744
142 | SR1R24 | POLE-2 EAST REACTOR | 125 | SR-I | -- | 2019-06-01 | 0:00 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 720 |  |  |  | H/T for voltage regulation vide code SR 757, continued from last month | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 720 | [6 empty] | 744
143 | SR1R25 | VIJAYWADA BUS REACTOR 4 | 125 | SR-I | -- | 2019-06-07 | 14:56 | 2019-06-07 | 16:57 |  |  |  | 0 | 0 | 0 | 2.0167 |  |  |  | H/T for CSD commissioning works vide code SR:405 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.0167 | [6 empty] | 744
144 | SR1R26 | NAGARJUNA SAGAR BUS REACTOR II | 125 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
145 | SR1R27 | WARDHA 1 LR AT NIZAMABAD | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
146 | SR1R28 | WARDHA 2 LR AT NIZAMABAD | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
147 | SR1R29 | SOLAPUR - RAICHUR -I LR | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
148 | SR1R30 | ANGUL - SRIKAKULAM - I LR | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
149 | SR1R31 | ANGUL - SRIKAKULAM - II LR | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
150 | SR1R32 | WARDHA - NIZAMABAD - I L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
151 | SR1R33 | WARDHA - NIZAMABAD - II L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
152 | SR1R34 | HYDERABAD - GAJWEL LR | 50 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
153 | SR1R35 | NELLORE - THIRUVALAM - I LR | 50 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
154 | SR1R36 | NELLORE - THIRUVALAM - II LR | 50 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
155 | SR1R37 | GOOTY - KURNOOL LR | 50 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
156 | SR1R38 | GOOTY BUS REACTOR 2 | 125 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
157 | SR1R39 | NELLORE BUS REACTOR 2 | 125 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
158 | SR1R40 | NIZAMABAD 765KV BUS REACTOR 1 | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
159 | SR1R40 | KADAPA BUS REACTOR -2 | 125 | SR-I | -- | 2019-06-06 | 9:48 | 2019-06-06 | 15:18 |  |  |  | 5.5 | 0 | 0 | 0 |  |  |  | H/T for spare combination chageover vide code SR-309 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 98.3759 | 744
[6 empty] | 2019-06-07 | 10:02 | 2019-06-07 | 16:37 |  |  |  | 6.5833 | 0 | 0 | 0 |  |  |  | H/T for spare combination chageover vide code SR-384,NL:273
[6 empty] | Sub Total --> | [6 empty] | 12.0833 | 0 | 0 | 0 | [6 empty] | 744
159 | SR1R41 | NPS-GOOTY-1 L/R | 63 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
160 | SR1R42 | NPS-GOOTY-2 L/R | 63 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
161 | SR1R43 | SRIKAKULAM-ANGUL 1 L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
162 | SR1R44 | SRIKAKULAM-ANGUL 2 L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
163 | SR1R45 | VEMAGIRI-SRIKAKULAM1 L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
164 | SR1R46 | VEMAGIRI-SRIKAKULAM2 L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
165 | SR1R47 | VIJAYWADA BUS REACTOR 3 | 125 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
166 | SR1R48 | NIZAMABAD-WARDHA -I L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
167 | SR1R49 | NIZAMABAD-WARDHA -II L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
168 | SR1R50 | MAHESHWARAM BUS REACTOR -II | 240 | SR-I | -- | 2019-06-12 | 13:47 | 2019-06-12 | 17:23 |  |  |  | 3.6 | 0 | 0 | 0 |  |  |  | H/T for AMP works vide Code SR-670 & NL-465 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.5161 | 744
[6 empty] | Sub Total --> | [6 empty] | 3.6 | 0 | 0 | 0 | [6 empty] | 744
169 | SR1R51 | NELLORE PS BUS REACTOR -II | 240 | SR-I | -- | 2019-06-06 | 14:17 | 2019-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 585.7167 |  |  |  | H/T on voltage regulation vide SR-330 | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 585.7167 | [6 empty] | 744
169 | SR1R51 | MAHESHWARAM-NIZAMABAD-I L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
170 | SR1R52 | MAHESHWARAM-NIZAMABAD-II L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
171 | SR1R38 | NIZAMABAD-MAHESHWARAM I L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
172 | SR1R53 | NIZAMABAD-MAHESHWARAM II L/R | 240 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
173 | SR1R54 | JEYPORE LR-1 AT GAJUWAKA | 80 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R55 | JEYPORE LR-2 AT GAJUWAKA | 80 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
174 | SR1R55 | RAICHUR BUS REACTOR 2 | 240 | SR-I | -- | 2019-06-11 | 9:37 | 2019-06-11 | 12:03 |  |  |  | 2.4333 | 0 | 0 | 0 |  |  |  | H/T vide code SR-577, NL-421 for checking of spare unit protection taking spare unit in service in place of R-Ph | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.6729 | 744
[6 empty] | Sub Total --> | [6 empty] | 2.4333 | 0 | 0 | 0 | [6 empty] | 744
175 | SR1B1 | GAJUWAKA BACK TO BACK POLE - I | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
176 | SR1B2 | GAJUWAKA BACK TO BACK POLE - II | 500 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
177 | SR1B3 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
178 | SR1B4 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-I | -- | -- |  | -- |  | -- | -- | -- | [8 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
179 | SR1S1 | STATCOM AT NPKUNTA | 200 | SR-I | -- | [15 empty] | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 100 | 744
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 744
|  |  | Note in type of failure column please indicate following : | [9 empty] | 231.5083 | 5.2667 | 802.6167 | 5580.9
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF MARCH 2017
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
GTY LR at NSR
1 |  | GTY LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWK I LR at VJA
2 |  | GWK I LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GWL LR at HYD
3 |  | GWL LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY I LR at GWK
4 |  | JEY I LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
JEY II LR at GWK
5 |  | JEY II LR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MBN LR at NSR
6 |  | MBN LR at NSR | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
MLK LR at HYD
7 |  | MLK LR at HYD | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR I LR at VJA
8 |  | NLR I LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLR II LR at VJA
9 |  | NLR II LR at VJA | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I LR at CDP
10 |  | NSR I LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II LR at CDP
11 |  | NSR II LR at CDP | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR LR at GTY
12 |  | NSR LR at GTY | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II ER at GWK
13 |  | POLE II ER at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
POLE II SR at GWK
14 |  | POLE II SR at GWK | 80 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RCR LR at MBD
15 |  | RCR LR at MBD | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM I LR at NSR
16 |  | RDM I LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
RDM II LR at NSR
17 |  | RDM II LR at NSR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH I LR at GWK
18 |  | SMH I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
SMH II LR at GWK
19 |  | SMH II LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at GWK
20 |  | VJA I LR at GWK | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA I LR at NLR
21 |  | VJA I LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA II LR at NLR
22 |  | VJA II LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG III LR at VJA
23 |  | VMG III LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VMG IV LR at VJA
24 |  | VMG IV LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
WGL LR at KMM
25 |  | WGL LR at KMM | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR I FSC at CDP
26 |  | NSR I FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NSR II FSC at CDP
27 |  | NSR II FSC at CDP | 201.75 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-1 at GTY
28 |  | FSC-1 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
FSC-2 at GTY
29 |  | FSC-2 at GTY | 181.5 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM1 LR at NLR
30 |  | TVLM1 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM2 LR at NLR
31 |  | TVLM2 LR at NLR | 50 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VTPS LR at NLRAP
32 |  | VTPS LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
VJA LR at NLRAP
33 |  | VJA LR at NLRAP | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VJA
34 |  | NLRAP LR at VJA | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NLRAP LR at VTPS
35 |  | NLRAP LR at VTPS | 63 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL I L/R AT NPS
36 |  | KURNOOL I L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
KURNOOL II L/R AT NPS
37 |  | KURNOOL II L/R AT NPS | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS I L/R AT KURNOOL
38 |  | NPS I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
NPS II L/R AT KURNOOL
39 |  | NPS II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM I L/R AT KURNOOL
40 |  | TVLM I L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
TVLM II L/R AT KURNOOL
41 |  | TVLM II L/R AT KURNOOL | 240 | SR1 |  | NO OUTAGES | [11 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0