## SOP
Standard of Performance data for the month of JUN-2021
Name of Transmission Licensee : POWERGRID SOUTHERN INTERCONNECTOR TRANSMISSION CORPORATION LIMITED
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR1L01 | SRIKAKULAM-GARIVIDI - I | 143.918 | SR-I |  | 2021-06-01 09:45 | 44348.4062 | 2021-06-01 19:10 | 44348.7986 | [6 empty] | 9.42 |  |  |  | Line S/D availed by M/s APTRANSCO | SRPC, SRPC/SE-I/PGTA/2014/10274/291, Dtd. 27.11.14 | 99.5858 | 720
[6 empty] | 2021-06-02 14:06 | 44349.5875 | 2021-06-02 14:36 | 44349.6083 |  |  |  |  | 0.5 | [5 empty] | Tripped on Y-N fault. A/R successful at Srikakulam end, tripped at Garividi end. Line is in service from Srikakulam end. outage is due to non-operation of A/R at Garivigi end.
[6 empty] | 2021-06-04 10:10 | 44351.4236 | 2021-06-04 13:09 | 44351.5479 |  |  |  | 2.98 |  |  | 0 |  |  |  | Emergency shutdown availed for damaged insulator replacement at Loc.345 (Y-Ph) vide SR-316
720
[6 empty] | Sub Total --> | [6 empty] | 2.98 | 0.5 | 0 | 9.42 | [6 empty] | 720
2 | SR1L02 | SRIKAKULAM-GARIVIDI - II | 143.918 | SR-I | -- | 2021-06-02 09:28 | 44349.3944 | 2021-06-02 20:40 | 44349.8611 | [6 empty] | 11.2 |  |  |  | Line S/D availed by M/s APTRANSCO for enabling &amp; configuration of under frequency settings in M1&amp;M2 relays at Garividi end vide SR-129 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.2 | [6 empty] | 720
3 | SR1L03 | KADAPA - MADHUGIRI - I | 243.349 | SR-I | -- | [16 empty] | 100 | 720
[5 empty] | -- | [17 empty] | 720
720
720
720
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
4 | SR1L04 | KADAPA - MADHUGIRI - II | 243.349 | SR-I | -- | 2021-06-04 03:18 | 44351.1375 | 2021-06-30 12:25 | 44377.5174 | [6 empty] | 633.12 |  |  |  | H/T under voltage regulation vide code SR-282 |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 633.12 | [6 empty] | 720
5 | SR1L05 | CHILAKALURIPETA - NARASARAOPETA - I | 29.844 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
6 | SR1L06 | CHILAKALURIPETA - NARASARAOPETA - II | 29.844 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
7 | SR1L07 | VEMAGIRI - CHILAKALURIPETA - I | 279.407 | SR-I | -- | 2021-06-05 18:21 | 44352.7646 | 2021-06-10 10:53 | 44357.4535 | [6 empty] | 112.53 |  |  |  | H/T under voltage regulation vide code:SR-06/427,NL-06/277 |  | 100 | 720
[6 empty] | 2021-06-11 08:28 | 44358.3528 | 2021-06-14 09:34 | 44361.3986 | [6 empty] | 73.1 |  |  |  | H/T under voltage regulation vide SR-960 NL-593
[6 empty] | 2021-06-26 | 19:53 | 2021-07-01 | 0:00 | [6 empty] | 100.1 |  |  |  | H/T under voltage Regulation vide SR-2633 NL-1539
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 285.73 | [6 empty] | 720
8 | SR1L08 | VEMAGIRI - CHILAKALURIPETA - II | 279.407 | SR-I | -- | 2021-06-10 23:35 | 44357.9826 | 2021-06-11 06:31 | 44358.2715 | [6 empty] | 6.93 |  |  |  | H/T under voltage regulation vide SR-947 NL-580 |  | 100 | 720
[6 empty] | 2021-06-14 16:20 | 44361.6806 | 2021-06-25 10:37 | 44372.4424 | [6 empty] | 258.28 |  |  |  | H/T under voltage regulation vide SR-1300, NL-780
720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 265.21 | [6 empty] | 720
9 | SR1L09 | CHILAKALURIPETA - KADAPA - I | 281.691 | SR-I | -- | 2021-06-01 17:34 | 44348.7319 | 2021-06-09 09:21 | 44356.3896 | [6 empty] | 183.78 |  |  |  | H/T under voltage regulation vide SR06/ 87,NL06/49. |  | 100 | 720
[6 empty] | 2021-06-23 18:17 | 44370.7618 | 2021-06-30 12:34 | 44377.5236 | [6 empty] | 162.28 |  |  |  | H/T under voltage regulation vide code SR-2277,NL-1322;
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 346.06 | [6 empty] | 720
10 | SR1L10 | CHILAKALURIPETA - KADAPA - II | 281.691 | SR-I | -- | 2021-06-01 | 0:00 | 2021-06-01 | 11:55 | [6 empty] | 11.9167 |  |  |  | Continued from Last Month Line kept under voltage regulation vide SR 1062 NL 458 |  | 100 | 720
[6 empty] | 2021-06-09 18:30 | 44356.7708 | 2021-06-23 07:23 | 44370.3076 | [6 empty] | 324.88 |  |  |  | H/T under Voltage regulation vide SR-833 NL-500 V
[5 empty] | -- | [17 empty] | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 336.7967 | [6 empty] | 720
11 | SR1T01 | CHILAKALURIPETA ICT - I | 1500 | SR-I | -- | 2021-06-23 07:50 | 44370.3264 | 2021-06-23 17:29 | 44370.7285 |  |  |  | 9.65 | [6 empty] | H/T For AMP works vide SR-2177 NL-1276 |  | 98.6597 | 720
[6 empty] | Sub Total --> | [6 empty] | 9.65 | 0 | 0 | 0 | [6 empty] | 720
12 | SR1T02 | CHILAKALURIPETA ICT - II | 1500 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
13 | SR1R01 | CHILAKALURIPETA BUS REACTOR - I | 240 | SR-I | -- | 2021-06-07 10:08 | 44354.4222 | 2021-06-07 18:40 | 44354.7778 | [6 empty] | 8.53 |  |  |  | H/T under voltage regulation vide SR-545, NL-365 |  | 100 | 720
[6 empty] | 2021-06-15 09:44 | 44362.4056 | 2021-06-15 16:37 | 44362.6924 | [6 empty] | 6.88 |  |  |  | H/T under voltage regulation vide SR-1361, NL-824
[6 empty] | 2021-06-21 09:25 | 44368.3924 | 2021-06-21 19:20 | 44368.8056 | [6 empty] | 9.92 |  |  |  | H/T under voltage regulation vide SR-1964,NL-1159.
[6 empty] | 2021-06-30 10:16 | 44377.4278 | 2021-06-30 17:28 | 44377.7278 | [6 empty] | 7.2 |  |  |  | H/T under voltage regulation vide code:SR-2894,NL-1793
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 32.53 | [6 empty] | 720
14 | SR1R02 | CHILAKALURIPETA BUS REACTOR - II | 240 | SR-I | -- | 2021-06-16 11:53 | 44363.4951 | 2021-06-16 17:25 | 44363.7257 | [6 empty] | 5.53 |  |  |  | H/T under voltage regulation vide SR-1508, NL-815 |  | 100 | 720
[6 empty] | 2021-06-22 06:54 | 44369.2875 | 2021-06-22 17:17 | 44369.7201 | [6 empty] | 10.38 |  |  |  | H/T under voltage regulation vide SR-2045/NL-1207
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 15.91 | [6 empty] | 720
15 | SR1R03 | KADAPA - I L/R @ C'PETA | 240 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
16 | SR1R04 | KADAPA - I I L/R @ C'PETA | 240 | SR-I | [5 empty] | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
17 | SR1R05 | VEMAGIRI - I L/R @ C'PETA | 240 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
18 | SR1R06 | VEMAGIRI - II L/R @ C'PETA | 240 | SR-I | -- | [16 empty] | 100 | 720
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | [6 empty] | 720
|  |  | Note in type of failure column please indicate following : | [9 empty] | 12.63 | 0.5 | 0 | 1935.9767
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## LR & FSC
EXCLUSIVE OUTAGE OF STATIC VAR COMPENSATOR/SERIESE COMPENSATOR/ LINE REACTORS FOR THE MONTH OF JUN-2021
Sl.No. | Unique ID of Transmission Element | Element Name | Description (Length/Nos./MVA/MVAR/MW/etc.) | Region | Type of Failure | Out Date and Time | Restoration Date and Time | Details of outage (No. of towers damaged, no. of insulator failed etc.) | Total outage (in Days) | Duration of Outage (Hrs) Attributable to |  |  |  | Restoration on Time as per Regulation 5(b) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm | Detailed Reason for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying Agency
[10 empty] | ISTS Licensee | Others | System constraint /Natural Calamity /Militancy | Deemed Available
NA
1 | [17 empty] | SRPC | 100%
GRAND TOTAL | [9 empty] | 0 | 0 | 0 | 0