## SOP
Standard of Performance data for the month of AUG -2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2013-08-29 | 8:30 | 2013-08-29 | 17:19 | -- | -- | -- | 0 | 0 | 0 | 8.8167 | N/A | N/A | N/A | Shut down availed by M/s KSEB to attend CVT oil leakage at Edappon end vide SRLDC code no. CR-08/875. | SRPC, SRPC/SE-I/PGTA/2014, Dtd. 06.01.14 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.8167
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2013-08-27 | 8:56 | 2013-08-28 | 18:51 | -- | -- | -- | 0 | 0 | 0 | 33.9167 | N/A | N/A | N/A | Shut down availed by M/s NTPC for overhauling of 220kV CB at Kayamkulam end vide SRLDC code no. CR-08/795. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33.9167
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2013-08-31 | 9:00 | 2013-09-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 15 | N/A | N/A | N/A | Shut down aviled by M/s NTPC for CB overhauling works at Kayamkulam end vide CPCC code no. CP-08/1314. |  | 100
[5 empty] | -- | 2013-09-25 | 9:32 | 2013-09-25 | 14:58 | -- | -- | -- | 0 | 0 | 0 | 5.4333 | N/A | N/A | N/A | Shut down availed by M/s KSEB for attending hot spots at Kundra SS vide SRLDC code no. CR-09/699.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 15
4 | SR2L4 | KAYAMKULAM - POLLAM - I | 47 | SR-II | -- | 2013-08-19 | 8:47 | 2013-08-20 | 21:07 | -- | -- | -- | 0 | 0 | 0 | 36.3333 | N/A | N/A | N/A | Shut down availed by M/s NTPC for over hauling of CB at Kayamkulam end vide SRLDC code no. CR-08/437. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 36.3333
5 | SR2L5 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2013-08-23 | 8:56 | 2013-08-24 | 18:56 | -- | -- | -- | 0 | 0 | 0 | 34 | N/A | N/A | N/A | Shut down availed by M/s NTPC for circuit breaker overhauling works at Kayamkulam end vide CPCC code no. CP-08/858. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 34
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2013-08-20 | 8:22 | 2013-08-20 | 18:20 | -- | -- | -- | 0 | 0 | 0 | 9.9667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for maintenance of 220 kV lower bus at Edamon end vide SRLDC code no. CR-08/477. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.9667
7 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | 2013-08-27 | 4:56 | 2013-08-27 | 4:56 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault due to heavy fog and pollution. FLR: 38.33 KM from Udumalpet end. |  | 100
[5 empty] | -- | 2013-08-27 | 13:48 | 2013-08-27 | 18:19 | -- | -- | -- | 0 | 0 | 4.5167 | 0 | N/A | N/A | N/A | Shut down availed for replacement of B-phase insulator DT string at loc. 112 which was damaged during successful auto reclosure on B-N fault due to heavy fog and pollution vide SRLDC code no. CR-08/813
[5 empty] | Insulator failure | 2013-08-29 | 2:57 | 2013-08-29 | 3:36 | -- | 1 | -- | 0 | 0 | 0.65 | 0 | N/A | N/A | N/A | Tripped due to decapping of one string of B-phase double tension insulator string at loc. 112 due to heavy fog and pollution.
[5 empty] | Insulator failure | 2013-08-30 | 9:17 | 2013-08-30 | 19:18 | -- | 1 | -- | 0 | 0 | 10.0167 | 0 | N/A | N/A | N/A | Shut down availed to replace the decapped tension isulator at Loc.No: 112 caused by heavy fog and pollution and for cleaning of insulators in heavily polluted area vide SRLDC code no. CR-08/914.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 15.1833 | 0
8 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | Insulator failure | 2013-08-29 | 2:57 | 2013-08-29 | 20:23 | -- | 1 | -- | 0 | 0 | 17.4333 | 0 | N/A | N/A | N/A | Tripped due to decapping of R-phase insulator at loc. 112 and B-phase insulator at loc. 90 due to heavy fog and pollution. |  | 100
[5 empty] | -- | 2013-08-31 | 8:59 | 2013-08-31 | 17:20 | -- | -- | -- | 0 | 0 | 8.35 | 0 | N/A | N/A | N/A | Shut down availed to replace the damaged insulator string at Loc.No: 90 caused by heavy fog and pollution and for cleaning of insulators in heavily polluted area vide SRLDC code no. CR-08/949.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 25.7833 | 0 | -- | -- | --
9 | SR2L10 | BANGALORE - SALEM | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
11 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
14 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
15 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
16 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | 2013-08-15 | 7:31 | 2013-08-16 | 13:31 | -- | -- | -- | 30 | 0 | 0 | 0 | N/A | N/A | N/A | Line tripped due to second stage low SF6 gas alaram in 403 bay R & Y-Phase bus duct at Bidadi (GIS) end. |  | 95.9677
[6 empty] | Sub Total --> | [6 empty] | 30 | 0 | 0 | 0 | -- | -- | --
17 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | 2013-08-14 | 10:19 | 2013-08-22 | 17:48 | -- | -- | -- | 199.4833 | 0 | 0 | 0 | N/A as per 5(b), Violation as per Regulation 5 (a) (iii) | N/A | N/A | Line tripped due to second stage low SF6 gas alaram in 402 bay Y-Phase bus duct at Bidadi (GIS) end. |  | 73.1877
[6 empty] | Sub Total --> | [6 empty] | 199.4833 | 0 | 0 | 0 | -- | -- | --
18 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | 2013-08-13 | 13:26 | 2013-08-13 | 13:53 | -- | -- | -- | 0 | 0 | 0 | 0.45 | N/A | N/A | N/A | Hand tripped for taking Line reactor at Sriperumbudur into service for voltage regulation as per SRLDC instructions vide code no. CR-08/294. |  | 100
[5 empty] | -- | 2013-08-16 | 13:52 | 2013-08-18 | 16:31 | -- | -- | -- | 0 | 0 | 0 | 50.65 | N/A | N/A | N/A | Shut down availed by M/s TNEB for Almathy - SV Chatram line crossing works vide SRLDC code no. CR-08/365.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.45 | -- | -- | --
19 | SR2L23 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | 2013-08-16 | 23:59 | 2013-08-17 | 0:04 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Chittoor end. Direct trip signal received at Cuddappa end. |  | 100
[5 empty] | -- | 2013-08-17 | 0:04 | 2013-08-17 | 6:57 | -- | -- | -- | 0 | 0 | 0 | 6.8833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/563.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.083333 | 0 | -- | -- | --
20 | SR2L24 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
21 | SR2L25 | GOOTY - BANGALORE | 301.667 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
22 | SR2L26 | HASSAN - MYSORE I | 95.875 | SR-II | -- | 2013-08-12 | 0:06 | 2013-08-12 | 6:47 | -- | -- | -- | 0 | 0 | 0 | 6.6833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/379. |  | 100
[5 empty] | -- | 2013-08-12 | 0:01 | 2013-08-12 | 0:06 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-14 | 2:01 | 2013-08-14 | 2:06 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-14 | 2:06 | 2013-08-14 | 6:54 | -- | -- | -- | 0 | 0 | 0 | 4.8 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/470.
[5 empty] | -- | 2013-08-18 | 22:48 | 2013-08-19 | 8:59 | -- | -- | -- | 0 | 0 | 0 | 10.1833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/426.
[5 empty] | -- | 2013-08-18 | 21:50 | 2013-08-18 | 22:16 | -- | -- | -- | 0 | 0 | 0.43333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-20 | 0:00 | 2013-08-20 | 0:05 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-20 | 0:05 | 2013-08-20 | 6:57 | -- | -- | -- | 0 | 0 | 0 | 6.8667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/678.
[5 empty] | -- | 2013-08-24 | 1:59 | 2013-08-24 | 2:04 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-24 | 23:59 | 2013-08-25 | 7:22 | -- | -- | -- | 0 | 0 | 0 | 7.3833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/959.
[5 empty] | -- | 2013-08-24 | 2:04 | 2013-08-24 | 6:44 | -- | -- | -- | 0 | 0 | 0 | 4.6667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/912.
[5 empty] | -- | 2013-08-24 | 23:55 | 2013-08-24 | 23:59 | -- | -- | -- | 0 | 0 | 0.066667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-27 | 23:52 | 2013-08-27 | 23:57 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
[5 empty] | -- | 2013-08-27 | 23:57 | 2013-08-28 | 6:49 | -- | -- | -- | 0 | 0 | 0 | 6.8667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/1105.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.91667 | 47.45 | -- | -- | --
23 | SR2L27 | HASSAN - MYSORE II | 95.875 | SR-II | Conductor snapping | 2013-08-29 | 7:39 | 2013-08-30 | 2:40 | -- | -- | -- | 19.0167 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-B fault due to Y-phase conductor snapping at loc. 61-62. |  | 97.444
[5 empty] | -- | 2013-08-30 | 2:40 | 2013-08-30 | 6:19 | -- | -- | -- | 0 | 0 | 0 | 3.65 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/1247.
[6 empty] | Sub Total --> | [6 empty] | 19.0167 | 0 | 0 | 3.65 | -- | -- | --
24 | SR2L28 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | 2013-08-25 | 9:59 | 2013-08-25 | 15:41 | -- | -- | -- | 0 | 0 | 0 | 5.7 | -- | -- | -- | Shut down availed by M/s KPTCL for maintenance works at Nelamangala end vide SRLDC code no. CR-08/734. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.7
25 | SR2L29 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2013-08-18 | 20:52 | 2013-08-19 | 1:30 | -- | -- | -- | 0 | 0 | 4.6333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end. |  | 100
[6 empty] | 2013-08-19 | 1:30 | 2013-08-19 | 6:23 | -- | -- | -- | 0 | 0 | 0 | 4.8833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/622.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 4.6333 | 4.8833
26 | SR2L30 | HOSUR-SALEM | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L32 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2013-08-17 | 23:21 | 2013-08-17 | 23:55 | -- | -- | -- | 0 | 0 | 0.56667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Narendra end. Direct trip signal received at Kaiga end. |  | 100
[5 empty] | -- | 2013-08-17 | 23:55 | 2013-08-18 | 7:10 | -- | -- | -- | 0 | 0 | 0 | 7.25 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/600.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.56667 | 7.25 | N/A | N/A | N/A
28 | SR2L33 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L34 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
30 | SR2L35 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2013-08-04 | 14:44 | 2013-08-05 | 15:50 | -- | -- | -- | 0 | 25.1 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N fault due to decapping of insulator at loc. no 202 (KPTCL portion of the line). |  | 100
[5 empty] | -- | 2013-08-16 | 6:47 | 2013-08-16 | 17:20 | -- | -- | -- | 0 | 10.55 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault with FLR:96.55 km from Kaiga end. Fault is in KPTCL portion of the line.
[5 empty] | -- | 2013-08-16 | 1:17 | 2013-08-16 | 6:47 | -- | -- | -- | 0 | 0 | 0 | 5.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/338.
[5 empty] | -- | 2013-08-16 | 17:20 | 2013-08-17 | 6:47 | -- | -- | -- | 0 | 0 | 0 | 13.45 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide KPTCL message dtd. 16.08.13.
[5 empty] | -- | 2013-08-17 | 6:47 | 2013-08-25 | 15:37 | -- | -- | -- | 0 | 200.8333 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault due to decapping of B-phase insulator at loc. 91 (KPTCL portion of the line).
[6 empty] | Sub Total --> | [6 empty] | 0 | 236.4833 | 0 | 18.95
31 | SR2L36 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | 2013-08-19 | 11:35 | 2013-08-19 | 11:38 | -- | -- | -- | 0 | 0 | 0 | 0.05 | N/A | N/A | N/A | Hand tripped for taking out Line reactor at Madurai end for voltage regulation as per SRLDC instructions vide code no. CR-08/447. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.05
32 | SR2L37 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L37A | KOLAR - CHENNAI | 219 | SR-II | -- | 2013-08-16 | 14:03 | 2013-08-18 | 18:26 | -- | -- | -- | 0 | 0 | 0 | 52.3833 | N/A | N/A | N/A | Shut down availed by M/s TNEB for Almathy - SV Chatram line crossing works vide SRLDC code no. CR-08/366. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 52.3833
34 | SR2L38 | KOLAR - HOODY - I | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
35 | SR2L39 | KOLAR - HOODY - II | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
36 | SR2L40 | KOLAR - HOSUR - I | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L41 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L43 | MADURAI - TUTICORIN 1 | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L44 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L45 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | 2013-08-23 | 8:25 | 2013-08-23 | 18:21 | -- | -- | -- | 0 | 0 | 0 | 9.9333 | N/A | N/A | N/A | Shut down availed for OPGW stringing works vide SRLDC code no. CR-08/627. |  | 100
[5 empty] | -- | 2013-08-29 | 22:37 | 2013-08-29 | 22:42 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Madurai end. Direct trip signal received at Thirunelveli end.
[5 empty] | -- | 2013-08-29 | 22:42 | 2013-08-30 | 9:46 | -- | -- | -- | 0 | 0 | 0 | 11.0667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/1241.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.9333
41 | SR2L46 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2013-08-26 | 6:51 | 2013-08-28 | 17:33 | -- | -- | -- | 0 | 0 | 0 | 58.7 | N/A | N/A | N/A | Shut down availed to carry out direct connection between Kudamkulam SS and Madurai SS vide SRLDC code no. CR-08/752. |  | 100
[5 empty] | -- | 2013-08-31 | 0:03 | 2013-09-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 23.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/947.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 82.65
42 | SR2L47 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-04 | 15:41 | -- | -- | -- | 0 | 0 | 0 | 87.6833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/776. |  | 100
[5 empty] | -- | 2013-08-11 | 23:22 | 2013-08-16 | 11:44 | -- | -- | -- | 0 | 0 | 0 | 108.3667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/258.
[5 empty] | -- | 2013-08-25 | 22:56 | 2013-08-26 | 7:50 | -- | -- | -- | 0 | 0 | 0 | 8.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/748.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 204.95
43 | SR2L48 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2013-08-16 | 22:52 | 2013-08-17 | 7:34 | -- | -- | -- | 0 | 0 | 0 | 8.7 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/379. |  | 100
[5 empty] | -- | 2013-08-26 | 23:30 | 2013-08-27 | 6:43 | -- | -- | -- | 0 | 0 | 0 | 7.2167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/791.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 15.9167
44 | SR2L49 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | 2013-08-15 | 16:08 | 2013-08-16 | 13:31 | -- | -- | -- | 21.3833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed to connect line from Nelamangala to Somanahalli by bypassing Bidadi SS for grid security vide SRLDC code no. CR-08/506. |  | 97.1259
[6 empty] | Sub Total --> | [6 empty] | 21.3833 | 0 | 0 | 0
45 | SR2L50 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | 2013-08-15 | 16:09 | 2013-08-16 | 13:53 | -- | -- | -- | 21.7333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed to connect line from Nelamangala to Somanahalli by bypassing Bidadi SS for grid security vide SRLDC code no. CR-08/507. |  | 92.4126
[5 empty] | -- | 2013-08-30 | 7:48 | 2013-08-31 | 18:31 | -- | -- | -- | 34.7167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed to replace the regid conductor with tulip contact in all 3 phases of outer bus duct in 407 bay vide SRLDC code no. CR-08/907.
[6 empty] | Sub Total --> | [6 empty] | 56.45 | 0 | 0 | 0
46 | SR2L51 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L52 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L53 | NEYVELI - BAHOOR | 52.5 | SR-II | Insulator failure | 2013-08-08 | 21:08 | 2013-08-09 | 6:41 | -- | 1 | -- | 0 | 0 | 9.55 | 0 | N/A | N/A | N/A | Tripped on B-N fault due to decapping of B-phase insulator at loc. 99 due to heavy lightning and thunderstorm. |  | 100
[5 empty] | -- | 2013-08-09 | 6:41 | 2013-08-09 | 13:30 | -- | -- | -- | 0 | 6.8167 | 0 | 0 | N/A | N/A | N/A | Charging delayed by Bahoor PED SS due to CB problem vide Message no. CP-08/309.
[6 empty] | Sub Total --> | [6 empty] | 0 | 6.8167 | 9.55 | 0
49 | SRL53 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | 2013-08-10 | 8:44 | 2013-08-10 | 15:36 | -- | -- | -- | 0 | 0 | 0 | 6.8667 | N/A | N/A | N/A | Shut down availed by M/S NLC for routine maintenance works at Neyveli end vide SRLDC code No: CR 08/229. |  | 100
[5 empty] | -- | 2013-08-27 | 10:03 | 2013-08-27 | 14:38 | -- | -- | -- | 0 | 0 | 0 | 4.5833 | N/A | N/A | N/A | Shut down availed by M/s PED for emergency maintenance works at Villianur end vide SRLDC code no. CR-08/803.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.45
50 | SR2L54 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | 2013-08-21 | 0:05 | 2013-08-21 | 1:20 | -- | -- | -- | 0 | 1.25 | 0 | 0 | N/A | N/A | N/A | Tripped at Neyveli TS-2 end only due to operation of busbar protection (Bus-I) at Neyveli Ts-2 end during hand tripping of unit 4 for maintenance works. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.25 | 0 | 0
51 | SR2L55 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2013-08-17 | 8:39 | 2013-08-17 | 15:59 | -- | -- | -- | 0 | 0 | 0 | 7.3333 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance worksat Neyveli TS II end vide SRLDC code no. CR-08/389. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.3333
52 | SR2L56 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | 2013-08-21 | 0:05 | 2013-08-21 | 1:42 | -- | -- | -- | 0 | 1.6167 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of busbar protection (Bus-I) at Neyveli Ts-2 end during hand tripping of unit 4 for maintenance works. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.6167 | 0 | 0
53 | SR2L57 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR2L58 | NEYVELI TS-I EXTENSION - TRICHY | 171.95 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L59 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
56 | SR2L60 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2013-08-21 | 0:05 | 2013-08-21 | 1:11 | -- | -- | -- | 0 | 1.1 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of busbar protection (Bus-I) at Neyveli Ts-2 end during hand tripping of unit 4 for maintenance works. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.1 | 0 | 0
57 | SR2L61 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
58 | SR2L62 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L63 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L64 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | 2013-08-24 | 9:55 | 2013-08-24 | 16:14 | -- | -- | -- | 0 | 0 | 0 | 6.3167 | N/A | N/A | N/A | Shut down availed by M/s TNEB for providing relay to implement islanding scheme at SV Chatram end vide SRLDC code no. CR-08/695. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.3167
61 | SR2L65 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | 2013-08-11 | 1:31 | 2013-08-11 | 1:59 | -- | -- | -- | 0 | 0 | 0.46667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Madurai end. Direct trip signal received at Pugalur end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.46667 | 0 | N/A | N/A | N/A
62 | SR2L66 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | 2013-08-11 | 1:31 | 2013-08-11 | 2:12 | -- | -- | -- | 0 | 0 | 0.68333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Madurai end. Direct trip signal received at Pugalur end. |  | 100
[5 empty] | -- | 2013-08-11 | 3:45 | 2013-08-11 | 9:28 | -- | -- | -- | 0 | 0 | 0 | 5.7167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/369.
[5 empty] | -- | 2013-08-11 | 3:22 | 2013-08-11 | 3:45 | -- | -- | -- | 0 | 0 | 0.38333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Madurai end. Direct trip signal received at Pugalur end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.68333 | 0
63 | SR2L67 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L68 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | 2013-08-21 | 9:00 | 2013-08-21 | 16:41 | -- | -- | -- | 7.6833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works and Y-Phase CVT replacement work at Salem end vide SRLDC code no. CR-08/530. |  | 98.9673
[6 empty] | Sub Total --> | [6 empty] | 7.6833 | 0 | 0 | 0
65 | SR2L70 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | 2013-08-13 | 13:04 | 2013-08-13 | 13:14 | -- | -- | -- | 0 | 0 | 0 | 0.16667 | N/A | N/A | N/A | Hand tripped for taking Line reactor at Sriperumbudur into service for voltage regulation as per SRLDC instructions vide code no. CR-08/292. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.16667
66 | SR2L71 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L72 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2013-08-29 | 16:11 | 2013-08-29 | 16:11 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 43.4 KM from Thirunelveli end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
68 | SR2L73 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2013-08-26 | 6:49 | 2013-08-28 | 17:33 | -- | -- | -- | 0 | 0 | 0 | 58.7333 | N/A | N/A | N/A | Shut down availed to carry out direct connection between Kudamkulam SS and Madurai SS vide SRLDC code no. CR-08/751. |  | 100
[5 empty] | -- | 2013-08-31 | 0:03 | 2013-09-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 23.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/947.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 82.6833
69 | SR2L74 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-21 | 17:28 | -- | -- | -- | 0 | 0 | 0 | 497.4667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/775. |  | 100
[5 empty] | -- | 2013-08-27 | 17:10 | 2013-08-27 | 18:45 | -- | -- | -- | 0 | 1.5833 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of direct trip signal from Kudamkulam end. Teed protection operated at Kudamkulam end.
[5 empty] | -- | 2013-08-29 | 16:11 | 2013-08-29 | 19:30 | -- | -- | -- | 0 | 3.3167 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of direct trip signal from Kudamkulam end. Teed protection operated at Kudamkulam end.
[5 empty] | -- | 2013-08-30 | 16:19 | 2013-08-31 | 17:10 | -- | -- | -- | 0 | 0 | 0 | 24.85 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for checking 87M2 and bus duct protection at Kudamkulam end vide KKNPP mail dated 30.08.13.
[5 empty] | -- | 2013-08-30 | 14:57 | 2013-08-30 | 16:19 | -- | -- | -- | 0 | 1.3667 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of direct trip signal from Kudamkulam end. Teed protection operated at Kudamkulam end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 6.2667 | 0 | 522.3167
70 | SR2L75 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L76 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
72 | SR2L77 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | 2013-08-23 | 8:17 | 2013-08-23 | 18:02 | -- | -- | -- | 0 | 0 | 0 | 9.75 | N/A | N/A | N/A | Shut down availed for OPGW stringing works vide SRLDC code no. CR-08/628. |  | 99.9933
[5 empty] | -- | 2013-08-30 | 16:20 | 2013-08-30 | 16:23 |  |  |  | 0.05 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped to take out line reactor at Trivandrum end.
[6 empty] | Sub Total --> | [6 empty] | 0.05 | 0 | 0 | 9.75
73 | SR2L78 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | 2013-08-19 | 10:03 | 2013-08-19 | 15:52 | -- | -- | -- | 5.8167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-08/444. |  | 99.2182
[6 empty] | Sub Total --> | [6 empty] | 5.8167 | 0 | 0 | 0
74 | SR2L79 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | 2013-08-16 | 10:05 | 2013-08-16 | 15:39 | -- | -- | -- | 5.5667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-08/359. |  | 99.2518
[5 empty] | -- | 2013-08-27 | 17:10 | 2013-08-27 | 17:10 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 105.6 KM from Thirunelveli end.
[6 empty] | Sub Total --> | [6 empty] | 5.5667 | 0 | 0 | 0
75 | SR2L80 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | 2013-08-16 | 3:52 | 2013-08-16 | 4:00 | -- | -- | -- | 0 | 0 | 0.13333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Udumalpet end. Direct trip signal received at Thirunelveli end. |  | 99.453
[5 empty] | -- | 2013-08-16 | 4:00 | 2013-08-16 | 6:28 | -- | -- | -- | 0 | 0 | 0 | 2.4667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/514.
[5 empty] | -- | 2013-08-17 | 10:10 | 2013-08-17 | 14:14 | -- | -- | -- | 4.0667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-08/390.
[5 empty] | -- | 2013-08-30 | 14:57 | 2013-08-30 | 15:18 | -- | -- | -- | 0 | 0 | 0.35 | 0 | N/A | N/A | N/A | Tripped on operation of over voltage protection while line CBs were attempting for auto-reclosure on B-N fault . FLR: 252.1 km from Udumalpet end.
[6 empty] | Sub Total --> | [6 empty] | 4.0667 | 0 | 0.48333 | 2.4667
76 | SR2L83 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L84 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L85 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L86 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | 2013-08-19 | 11:14 | 2013-08-19 | 11:19 | -- | -- | -- | 0 | 0 | 0 | 0.083333 | N/A | N/A | N/A | Hand tripped for taking Line reactor at Madurai into service for voltage regulation as per SRLDC instructions vide code no. CR-08/445. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.083333
80 | SR2L87 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L88 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | 2013-08-29 | 2:57 | 2013-08-29 | 3:45 | -- | -- | -- | 0.8 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on operation of Tie breaker LBB protection during Udumalpet-Arasur line - 2 tripping. |  | 99.8925
[6 empty] | Sub Total --> | [6 empty] | 0.8 | 0 | 0 | 0
82 | SR2L89 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L90 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR2L91 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | 2013-08-27 | 8:59 | 2013-08-30 | 19:28 | -- | -- | -- | 0 | 0 | 0 | 82.4833 | N/A | N/A | N/A | Shut down availed by M/s NTECL to arrest SF6 gas leakage in the isolator section at Vallur end vide SRLDC code no. CR-08/796. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 82.4833
85 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2013-08-04 | 9:45 | 2013-08-04 | 16:56 | -- | -- | -- | 0 | 0 | 0 | 7.1833 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for converting strung bus to rigid bus at 220kV Somanahalli SS vide SRLDC code no. CR-08/88. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.1833
89 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | 2013-08-04 | 9:24 | 2013-08-04 | 16:53 | -- | -- | -- | 7.4833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-08/87. |  | 98.9942
[6 empty] | Sub Total --> | [6 empty] | 7.4833 | 0 | 0 | 0
96 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | 2013-08-28 | 10:37 | 2013-08-28 | 15:12 | -- | -- | -- | 4.5833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-08/849. |  | 99.384
[6 empty] | Sub Total --> | [6 empty] | 4.5833 | 0 | 0 | 0
98 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | 2013-08-26 | 10:24 | 2013-08-26 | 17:54 | -- | -- | -- | 7.5 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works and bushing oil sample collection works vide SRLDC code no. CR-08/766. |  | 98.9919
[6 empty] | Sub Total --> | [6 empty] | 7.5 | 0 | 0 | 0
99 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | 2013-08-21 | 10:50 | 2013-08-21 | 14:14 | -- | -- | -- | 3.4 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending hot spot in 230KV isolator vide SRLDC code no. CR-08/546. |  | 99.543
[6 empty] | Sub Total --> | [6 empty] | 3.4 | 0 | 0 | 0
100 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | 2013-08-06 | 10:44 | 2013-08-06 | 10:57 | -- | -- | -- | 0.21667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-08/145. |  | 99.9485
[5 empty] | -- | 2013-08-13 | 10:07 | 2013-08-13 | 10:13 | -- | -- | -- | 0.1 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-08/283.
[5 empty] | -- | 2013-08-20 | 10:18 | 2013-08-20 | 10:22 | -- | -- | -- | 0.066667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-08/480.
[6 empty] | Sub Total --> | [6 empty] | 0.38333 | 0 | 0 | 0
104 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | 2013-08-20 | 15:08 | 2013-08-20 | 15:15 | -- | -- | -- | 0.11667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-08/490. |  | 99.9664
[5 empty] | -- | 2013-08-27 | 10:49 | 2013-08-27 | 10:57 | -- | -- | -- | 0.13333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-08/807.
[6 empty] | Sub Total --> | [6 empty] | 0.25 | 0 | 0 | 0
105 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [11 empty] | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | 2013-08-07 | 10:23 | 2013-08-07 | 14:48 | -- | -- | -- | 4.4167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-08/163. |  | 99.254
[5 empty] | -- | 2013-08-08 | 14:37 | 2013-08-08 | 15:45 |  |  |  | 1.1333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for restoration of ICT-2 from TNEB bus coupler breaker to 21752 breaker vide SRLDC code no. CR-08/205.
[6 empty] | Sub Total --> | [6 empty] | 5.55 | 0 | 0 | 0
107 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T36 | TRICHY ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T37 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T38 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T39 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T40 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T41 | UDUMALPET ICT - I | 315 | SR-II | -- | 2013-08-16 | 4:16 | 2013-08-16 | 5:21 | -- | -- | -- | 0 | 1.0833 | 0 | 0 | N/A | N/A | N/A | Tripped (220kV side only) due to operation of Bus Bar protection at 220KV Mywadi S/S of M/s TNEB. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.0833 | 0 | 0
125 | SR2T42 | UDUMALPET ICT - II | 315 | SR-II | -- | 2013-08-16 | 4:16 | 2013-08-16 | 5:28 | -- | -- | -- | 0 | 1.2 | 0 | 0 | N/A | N/A | N/A | Tripped (220kV side only) due to operation of Bus Bar protection at 220KV Mywadi S/S of M/s TNEB. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.2 | 0 | 0
126 | SR2T43 | UDUMALPET ICT - III | 315 | SR-II | -- | 2013-08-16 | 4:16 | 2013-08-16 | 5:21 | -- | -- | -- | 0 | 1.0833 | 0 | 0 | N/A | N/A | N/A | Tripped (220kV side only) due to operation of Bus Bar protection at 220KV Mywadi S/S of M/s TNEB. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.0833 | 0 | 0
127 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2013-08-01 | 7:14 | 2013-08-01 | 22:23 | -- | -- | -- | 0 | 0 | 0 | 15.15 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-02 | 7:14 | 2013-08-02 | 22:05 | -- | -- | -- | 0 | 0 | 0 | 14.85 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-03 | 7:22 | 2013-08-03 | 23:55 | -- | -- | -- | 0 | 0 | 0 | 16.55 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-05 | 8:30 | 2013-08-07 | 22:59 | -- | -- | -- | 0 | 0 | 0 | 62.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-08 | 8:29 | 2013-08-08 | 23:12 | -- | -- | -- | 0 | 0 | 0 | 14.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-09 | 8:18 | 2013-08-09 | 22:00 | -- | -- | -- | 0 | 0 | 0 | 13.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-10 | 9:54 | 2013-08-10 | 21:50 | -- | -- | -- | 0 | 0 | 0 | 11.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-13 | 12:34 | 2013-08-13 | 23:16 | -- | -- | -- | 0 | 0 | 0 | 10.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-14 | 8:46 | 2013-08-14 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 13.7833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-16 | 8:49 | 2013-08-16 | 21:42 | -- | -- | -- | 0 | 0 | 0 | 12.8833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-17 | 8:11 | 2013-08-17 | 21:51 | -- | -- | -- | 0 | 0 | 0 | 13.6667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-19 | 18:49 | 2013-08-19 | 23:00 | -- | -- | -- | 0 | 0 | 0 | 4.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 11:18 | 2013-08-20 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 11.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 9:01 | 2013-08-21 | 21:47 | -- | -- | -- | 0 | 0 | 0 | 12.7667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 7:27 | 2013-08-22 | 22:34 | -- | -- | -- | 0 | 0 | 0 | 15.1167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:20 | 2013-08-23 | 21:55 | -- | -- | -- | 0 | 0 | 0 | 13.5833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-24 | 19:06 | 2013-08-24 | 22:19 | -- | -- | -- | 0 | 0 | 0 | 3.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 8:33 | 2013-08-26 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 14.35 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 15:06 | 2013-08-27 | 23:20 | -- | -- | -- | 0 | 0 | 0 | 8.2333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-28 | 9:01 | 2013-08-29 | 23:14 | -- | -- | -- | 0 | 0 | 0 | 38.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-30 | 8:01 | 2013-08-31 | 0:06 | -- | -- | -- | 0 | 0 | 0 | 16.0833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-31 | 16:40 | 2013-08-31 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 5.4667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 342.6667
128 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-01 | 18:19 | -- | -- | -- | 0 | 0 | 0 | 18.3167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-02 | 6:50 | 2013-08-02 | 22:03 | -- | -- | -- | 0 | 0 | 0 | 15.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-03 | 7:13 | 2013-08-03 | 23:55 | -- | -- | -- | 0 | 0 | 0 | 16.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-08 | 8:36 | 2013-08-08 | 23:17 | -- | -- | -- | 0 | 0 | 0 | 14.6833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-09 | 8:20 | 2013-08-09 | 22:00 | -- | -- | -- | 0 | 0 | 0 | 13.6667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-10 | 9:51 | 2013-08-10 | 21:50 | -- | -- | -- | 0 | 0 | 0 | 11.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-13 | 11:06 | 2013-08-13 | 23:04 | -- | -- | -- | 0 | 0 | 0 | 11.9667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 11:19 | 2013-08-23 | 15:15 | -- | -- | -- | 0 | 0 | 0 | 75.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 17:53 | 2013-08-25 | 22:25 | -- | -- | -- | 0 | 0 | 0 | 52.5333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 8:15 | 2013-08-26 | 22:49 | -- | -- | -- | 0 | 0 | 0 | 14.5667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 16:03 | 2013-08-27 | 23:15 | -- | -- | -- | 0 | 0 | 0 | 7.2 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-28 | 8:53 | 2013-08-29 | 23:10 | -- | -- | -- | 0 | 0 | 0 | 38.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-30 | 7:46 | 2013-08-31 | 22:05 | -- | -- | -- | 0 | 0 | 0 | 38.3167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 329.3667
130 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2013-08-14 | 8:40 | 2013-08-14 | 22:24 | -- | -- | -- | 0 | 0 | 0 | 13.7333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2013-08-16 | 8:55 | 2013-08-16 | 17:07 | -- | -- | -- | 0 | 0 | 0 | 8.2 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.7333
132 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-04 | 23:26 | -- | -- | -- | 0 | 0 | 0 | 95.4333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-05 | 8:23 | 2013-08-11 | 23:26 | -- | -- | -- | 0 | 0 | 0 | 159.05 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-13 | 11:04 | 2013-08-13 | 23:06 | -- | -- | -- | 0 | 0 | 0 | 12.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-14 | 8:38 | 2013-08-16 | 22:13 | -- | -- | -- | 0 | 0 | 0 | 61.5833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-17 | 8:03 | 2013-08-17 | 21:48 | -- | -- | -- | 0 | 0 | 0 | 13.75 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-19 | 18:48 | 2013-08-19 | 22:57 | -- | -- | -- | 0 | 0 | 0 | 4.15 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 19:14 | 2013-08-20 | 22:11 | -- | -- | -- | 0 | 0 | 0 | 2.95 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 8:56 | 2013-08-21 | 21:33 | -- | -- | -- | 0 | 0 | 0 | 12.6167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 7:13 | 2013-08-22 | 22:28 | -- | -- | -- | 0 | 0 | 0 | 15.25 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:31 | 2013-08-24 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 37.4167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 8:18 | 2013-09-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 135.7 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 549.9333
132 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-03 | 18:30 | -- | -- | -- | 0 | 0 | 0 | 66.5 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-03 | 19:01 | 2013-08-04 | 0:11 | -- | -- | -- | 0 | 0 | 0 | 5.1667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-05 | 8:21 | 2013-08-05 | 22:21 | -- | -- | -- | 0 | 0 | 0 | 14 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-07 | 14:42 | 2013-08-09 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 55.4333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 19:23 | 2013-08-21 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 2.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 18:52 | 2013-08-22 | 22:34 | -- | -- | -- | 0 | 0 | 0 | 3.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:20 | 2013-08-25 | 22:31 | -- | -- | -- | 0 | 0 | 0 | 62.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 16:56 | 2013-08-26 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 5.95 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 215.2167
133 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2013-08-01 | 14:07 | 2013-08-01 | 22:41 | -- | -- | -- | 0 | 0 | 0 | 8.5667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-02 | 6:53 | 2013-08-02 | 22:03 | -- | -- | -- | 0 | 0 | 0 | 15.1667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-07 | 19:01 | 2013-08-07 | 22:15 | -- | -- | -- | 0 | 0 | 0 | 3.2333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-19 | 19:33 | 2013-08-19 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 3.35 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 11:30 | 2013-08-20 | 22:35 | -- | -- | -- | 0 | 0 | 0 | 11.0833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 19:21 | 2013-08-21 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 2.7833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 19:03 | 2013-08-22 | 22:39 | -- | -- | -- | 0 | 0 | 0 | 3.6 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:25 | 2013-08-23 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 14.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-24 | 19:03 | 2013-08-24 | 22:07 | -- | -- | -- | 0 | 0 | 0 | 3.0667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 19:17 | 2013-08-26 | 22:57 | -- | -- | -- | 0 | 0 | 0 | 3.6667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-29 | 19:18 | 2013-08-29 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 3.0333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 72.0167
134 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2013-08-01 | 7:02 | 2013-08-01 | 22:19 | -- | -- | -- | 0 | 0 | 0 | 15.2833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-05 | 8:20 | 2013-08-05 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 13.8 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-10 | 9:51 | 2013-08-10 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 12.3833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-16 | 8:46 | 2013-08-16 | 21:35 | -- | -- | -- | 0 | 0 | 0 | 12.8167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 10:51 | 2013-08-22 | 22:30 | -- | -- | -- | 0 | 0 | 0 | 11.65 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:29 | 2013-08-23 | 21:42 | -- | -- | -- | 0 | 0 | 0 | 13.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 8:14 | 2013-08-26 | 22:44 | -- | -- | -- | 0 | 0 | 0 | 14.5 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 15:48 | 2013-08-27 | 22:44 | -- | -- | -- | 0 | 0 | 0 | 6.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-28 | 8:50 | 2013-08-28 | 22:46 | -- | -- | -- | 0 | 0 | 0 | 13.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-29 | 8:45 | 2013-08-29 | 23:08 | -- | -- | -- | 0 | 0 | 0 | 14.3833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-30 | 9:12 | 2013-08-30 | 22:34 | -- | -- | -- | 0 | 0 | 0 | 13.3667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 142.2667
135 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2013-08-01 | 7:17 | 2013-08-01 | 22:15 | -- | -- | -- | 0 | 0 | 0 | 14.9667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2013-08-29 | 19:23 | 2013-08-29 | 23:13 | -- | -- | -- | 0 | 0 | 0 | 3.8333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 18.8
136 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2013-08-02 | 6:56 | 2013-08-02 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 15.2 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-07 | 19:06 | 2013-08-07 | 22:13 | -- | -- | -- | 0 | 0 | 0 | 3.1167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-17 | 8:09 | 2013-08-17 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 13.7833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-19 | 18:48 | 2013-08-19 | 22:52 | -- | -- | -- | 0 | 0 | 0 | 4.0667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 11:37 | 2013-08-20 | 22:31 | -- | -- | -- | 0 | 0 | 0 | 10.9 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 19:16 | 2013-08-21 | 22:11 | -- | -- | -- | 0 | 0 | 0 | 2.9167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 19:02 | 2013-08-22 | 22:45 | -- | -- | -- | 0 | 0 | 0 | 3.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:27 | 2013-08-23 | 22:52 | -- | -- | -- | 0 | 0 | 0 | 14.4167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-24 | 18:57 | 2013-08-24 | 22:09 | -- | -- | -- | 0 | 0 | 0 | 3.2 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 19:15 | 2013-08-26 | 22:46 | -- | -- | -- | 0 | 0 | 0 | 3.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-29 | 19:16 | 2013-08-29 | 22:22 | -- | -- | -- | 0 | 0 | 0 | 3.1 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 77.9333
138 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2013-08-01 | 7:15 | 2013-08-01 | 22:58 | -- | -- | -- | 0 | 0 | 0 | 15.7167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-02 | 7:03 | 2013-08-03 | 23:51 | -- | -- | -- | 0 | 0 | 0 | 40.8 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-16 | 8:53 | 2013-08-16 | 22:16 | -- | -- | -- | 0 | 0 | 0 | 13.3833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 19:15 | 2013-08-20 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 3.0833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 19:20 | 2013-08-21 | 21:37 | -- | -- | -- | 0 | 0 | 0 | 2.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 10:48 | 2013-08-22 | 22:37 | -- | -- | -- | 0 | 0 | 0 | 11.8167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:15 | 2013-08-23 | 22:49 | -- | -- | -- | 0 | 0 | 0 | 14.5667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 15:59 | 2013-08-27 | 22:46 | -- | -- | -- | 0 | 0 | 0 | 6.7833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-29 | 19:33 | 2013-08-29 | 23:13 | -- | -- | -- | 0 | 0 | 0 | 3.6667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 112.1
139 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | 2013-08-01 | 7:03 | 2013-08-04 | 23:19 | -- | -- | -- | 0 | 0 | 0 | 88.2667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-06 | 10:40 | 2013-08-09 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 83.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-17 | 12:38 | 2013-08-18 | 16:20 | -- | -- | -- | 0 | 0 | 0 | 27.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 19:04 | 2013-08-22 | 22:37 | -- | -- | -- | 0 | 0 | 0 | 3.55 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 8:31 | 2013-08-25 | 22:41 | -- | -- | -- | 0 | 0 | 0 | 62.1667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 15:07 | 2013-08-31 | 22:05 | -- | -- | -- | 0 | 0 | 0 | 102.9667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 368.05
140 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2013-08-02 | 6:41 | 2013-08-02 | 14:24 | -- | -- | -- | 0 | 0 | 0 | 7.7167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-07 | 18:57 | 2013-08-07 | 22:11 | -- | -- | -- | 0 | 0 | 0 | 3.2333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-19 | 19:29 | 2013-08-19 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 3.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 19:12 | 2013-08-21 | 21:38 | -- | -- | -- | 0 | 0 | 0 | 2.4333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 19:04 | 2013-08-22 | 22:35 | -- | -- | -- | 0 | 0 | 0 | 3.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 10:04 | 2013-08-23 | 22:50 | -- | -- | -- | 0 | 0 | 0 | 12.7667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-24 | 18:54 | 2013-08-24 | 22:06 | -- | -- | -- | 0 | 0 | 0 | 3.2 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 16:53 | 2013-08-26 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 6 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 42.2667
141 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2013-08-02 | 6:42 | 2013-08-02 | 14:27 | -- | -- | -- | 0 | 0 | 0 | 7.75 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-07 | 18:58 | 2013-08-07 | 22:15 | -- | -- | -- | 0 | 0 | 0 | 3.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-21 | 19:18 | 2013-08-21 | 21:43 | -- | -- | -- | 0 | 0 | 0 | 2.4167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-22 | 19:08 | 2013-08-22 | 22:38 | -- | -- | -- | 0 | 0 | 0 | 3.5 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 10:07 | 2013-08-23 | 22:56 | -- | -- | -- | 0 | 0 | 0 | 12.8167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-24 | 18:54 | 2013-08-24 | 22:10 | -- | -- | -- | 0 | 0 | 0 | 3.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 16:55 | 2013-08-26 | 22:57 | -- | -- | -- | 0 | 0 | 0 | 6.0333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.75
142 | SR2R17 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2013-08-23 | 19:05 | 2013-08-25 | 22:29 | -- | -- | -- | 0 | 0 | 0 | 51.4 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-26 | 8:16 | 2013-09-01 | 0:00 |  |  |  | 0 | 0 | 0 | 135.7333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 187.1333
143 | SR2R18 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
144 | SR2R19 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-04 | 22:46 | -- | -- | -- | 0 | 0 | 0 | 94.7667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 94.7667
145 | SR2R20 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-01 | 22:35 | -- | -- | -- | 0 | 0 | 0 | 22.5833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-02 | 7:16 | 2013-08-02 | 22:12 | -- | -- | -- | 0 | 0 | 0 | 14.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-07 | 19:01 | 2013-08-08 | 23:24 | -- | -- | -- | 0 | 0 | 0 | 28.3833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-19 | 19:30 | 2013-08-20 | 22:36 | -- | -- | -- | 0 | 0 | 0 | 27.1 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 12:08 | 2013-08-25 | 22:32 | -- | -- | -- | 0 | 0 | 0 | 58.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 16:54 | 2013-08-26 | 22:52 | -- | -- | -- | 0 | 0 | 0 | 5.9667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 15:53 | 2013-08-27 | 23:22 | -- | -- | -- | 0 | 0 | 0 | 7.4833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 164.85
146 | SR2R21 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2013-08-01 | 0:00 | 2013-08-01 | 22:35 | -- | -- | -- | 0 | 0 | 0 | 22.5833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-02 | 7:16 | 2013-08-02 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 14.9667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-07 | 19:02 | 2013-08-08 | 23:24 | -- | -- | -- | 0 | 0 | 0 | 28.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-20 | 19:13 | 2013-08-20 | 22:37 | -- | -- | -- | 0 | 0 | 0 | 3.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-23 | 12:09 | 2013-08-25 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 58.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-26 | 16:54 | 2013-08-26 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 5.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-08-27 | 15:54 | 2013-08-27 | 23:22 | -- | -- | -- | 0 | 0 | 0 | 7.4667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 141.1667
147 | SR2R22 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2013-08-23 | 19:07 | 2013-08-23 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 2.55 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-24 | 19:01 | 2013-08-24 | 21:56 |  |  |  | 0 | 0 | 0 | 2.9167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.55
148 | SR2R23 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2013-08-23 | 19:07 | 2013-08-23 | 21:43 | -- | -- | -- | 0 | 0 | 0 | 2.6 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-08-24 | 19:01 | 2013-08-24 | 21:57 |  |  |  | 0 | 0 | 0 | 2.9333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.6
149 | SR2R24 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | 2013-08-23 | 19:12 | 2013-09-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 196.8 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 196.8
150 | SR2R25 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2R26 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | 2013-08-30 | 10:41 | 2013-08-30 | 11:55 | -- | -- | -- | 1.2333 | 0 | 0 | 0 | N/A | N/A | N/A | Blocked due to pole-2 DC measuring unit problem at Talcher end. Pole I went into Metallic return mode. |  | 99.4534
[5 empty] | -- | 2013-08-31 | 10:17 | 2013-08-31 | 13:07 | -- | -- | -- | 2.8333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed to inspect the DC measuring circuit in pole-2 at Talcher end vide SRLDC code no. CR-08/951.
[6 empty] | Sub Total --> | [6 empty] | 4.0667 | 0 | 0 | 0
[22 empty] | 15048.4495 | 15048.4495 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse