## SOP
Standard of Performance data for the month of DEC -2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2013-12-19 | 13:30 | 2013-12-19 | 16:49 | -- | -- | -- | 0 | 0 | 0 | 3.3167 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacement of Y-Phase arm of bus coupler isolator at Edamon SS vide SRLDC code no. CR-12/557. | SRPC, SRPC/SE-I/PGTA/2014/1908 , Dtd. 03.03.2014 | 100
[5 empty] | -- | 2013-12-20 | 12:06 | 2013-12-20 | 12:26 | -- | -- | -- | 0 | 0.33333 | 0 | 0 | N/A | N/A | N/A | Line got tripped at Edamon end only on receipt of direct trip signal from Edappon end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.33333 | 0 | 3.3167
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2013-12-13 | 10:06 | 2013-12-13 | 11:17 | -- | -- | -- | 0 | 0 | 0 | 1.1833 | -- | -- | -- | -- |  | 100
[6 empty] | 2013-12-28 | 9:37 | 2013-12-28 | 17:37 |  |  |  | 0 | 0 | 0 | 8
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.1833
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
4 | SR2L4 | KAYAMKULAM - POLLAM - I | 47 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
5 | SR2L5 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
7 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
8 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
9 | SR2L10 | BANGALORE - SALEM | 79.756 | SR-II | -- | 2013-12-21 | 6:09 | 2013-12-21 | 16:44 | -- | -- | -- | 0 | 0 | 0 | 10.5833 | N/A | N/A | N/A | Shut down availed for construction of LILO works of 400KV Bangalore-Salem at Hosur SS vide SRLDC code no. CR-12/601. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.5833
10 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
11 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
14 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
15 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
16 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
17 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
18 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
19 | SR2L23 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | 2013-12-10 | 10:16 | 2013-12-10 | 14:44 | -- | -- | -- | 0 | 0 | 0 | 4.4667 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for modification of relay setting at Chittoor end vide SRLDC code no. CR-12/265. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.4667 | -- | -- | --
20 | SR2L24 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
21 | SR2L25 | GOOTY - BANGALORE | 301.667 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
22 | SR2L26 | HASSAN - MYSORE I | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
23 | SR2L27 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
24 | SR2L28 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L29 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2013-12-01 | 22:00 | 2013-12-01 | 22:19 | -- | -- | -- | 0 | 0 | 0.31667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end. |  | 100
[6 empty] | 2013-12-09 | 23:35 | 2013-12-10 | 0:15 | -- | -- | -- | 0 | 0 | 0.66667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.98333 | 0
26 | SR2L31 | HOSUR-SALEM | 251.664 | SR-II | -- | 2013-12-05 | 6:20 | 2013-12-06 | 17:33 | -- | -- | -- | 0 | 0 | 0 | 35.2167 | N/A | N/A | N/A | Shut down availed for 765 KV Salem - Madhugiri line crossing works at AP-40 & 41 vide SRLDC code no CR-12/109. |  | 100
[5 empty] | -- | 2013-12-23 | 6:18 | 2013-12-23 | 17:24 | -- | -- | -- | 0 | 0 | 0 | 11.1 | N/A | N/A | N/A | Shut down availed for stringing works of 765 KV Salem - Madhugiri S/C line vide SRLDC code no. CR-12/637.
[5 empty] | -- | 2013-12-24 | 6:04 | 2013-12-24 | 15:30 | -- | -- | -- | 0 | 0 | 0 | 9.4333 | N/A | N/A | N/A | Shut down availed for stringing works of 765KV Salem - Madhugiri S/C line vide SRLDC code no. CR-12/681.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 55.75
27 | SR2L32 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2013-12-01 | 23:12 | 2013-12-02 | 8:16 | -- | -- | -- | 0 | 0 | 0 | 9.0667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/14. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.0667
28 | SR2L33 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L34 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2013-12-01 | 23:49 | 2013-12-02 | 6:28 | -- | -- | -- | 0 | 0 | 0 | 6.65 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/16. |  | 100
[5 empty] | -- | 2013-12-05 | 15:38 | 2013-12-05 | 21:50 | -- | -- | -- | 0 | 0 | 0 | 6.2 | N/A | N/A | N/A | Emergency Shutdown availed by M/s KPTCL for CB testing at Guttur end vide SRLDC code no. CR-12/128.
[5 empty] | -- | 2013-12-05 | 21:50 | 2013-12-06 | 7:08 | -- | -- | -- | 0 | 0 | 0 | 9.3 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/167.
[5 empty] | -- | 2013-12-24 | 21:14 | 2013-12-24 | 22:38 | -- | -- | -- | 0 | 1.4 | 0 | 0 | N/A | N/A | N/A | Tripped due to 400 kV bus fault at KPTCL Guttur SS. Direct trip signal received at Kaiga SS.
[5 empty] | -- | 2013-12-24 | 22:38 | 2013-12-25 | 6:57 | -- | -- | -- | 0 | 0 | 0 | 8.3167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/1018.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.4 | 0 | 30.4667 | -- | -- | --
30 | SR2L35 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2013-12-06 | 10:38 | 2013-12-06 | 16:00 | -- | -- | -- | 0 | 0 | 0 | 5.3667 | N/A | N/A | N/A | Emergency Shut down availed by M/s KPTCL to arrest oil leakage in CB at Guttur end vide SRLDC code no. CR-12 /150. |  | 100
[5 empty] | -- | 2013-12-13 | 15:56 | 2013-12-13 | 20:10 | -- | -- | -- | 0 | 0 | 0 | 4.2333 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending oil leakage in CB at Guttur end vide SRLDC code no. CR-12/398.
[5 empty] | -- | 2013-12-24 | 21:14 | 2013-12-24 | 22:26 | -- | -- | -- | 0 | 1.2 | 0 | 0 | N/A | N/A | N/A | Tripped due to 400 kV bus fault at KPTCL Guttur SS. Direct trip signal received at Kaiga SS.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.2 | 0 | 9.6
31 | SR2L36 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
32 | SR2L37 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L37A | KOLAR - CHENNAI | 219 | SR-II | -- | 2013-12-01 | 0:00 | 2013-12-02 | 12:52 | -- | -- | -- | 0 | 0 | 0 | 36.8667 | N/A | N/A | N/A | Shut down availed for construction of 400 kV Chittoor - Thirivalam D/C line vide SRLDC code no CR-11/ 901. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 36.8667
34 | SR2L38 | KOLAR - HOODY - I | 51.067 | SR-II | -- | 2013-12-07 | 9:24 | 2013-12-07 | 13:33 | -- | -- | -- | 0 | 0 | 0 | 4.15 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Kolar end as per SRPC recommendation vide SRLDC code no CR-12/179. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.15
35 | SR2L39 | KOLAR - HOODY - II | 51.067 | SR-II | -- | 2013-12-04 | 14:20 | 2013-12-04 | 18:15 | -- | -- | -- | 0 | 0 | 0 | 3.9167 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Kolar end as per SRPC recommendation vide SRLDC code no CR-12/95. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.9167
36 | SR2L40 | KOLAR - HOSUR - I | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L41 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L43 | MADURAI - TUTICORIN 1 | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L44 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L45 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L46 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L47 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2013-12-03 | 23:29 | 2013-12-05 | 15:17 | -- | -- | -- | 0 | 0 | 0 | 39.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/82. |  | 100
[5 empty] | -- | 2013-12-10 | 23:26 | 2013-12-13 | 11:34 | -- | -- | -- | 0 | 0 | 0 | 60.1333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/298.
[5 empty] | -- | 2013-12-15 | 21:56 | 2013-12-24 | 10:15 | -- | -- | -- | 0 | 0 | 0 | 204.3167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/447.
[5 empty] | -- | 2013-12-24 | 21:14 | 2013-12-24 | 22:14 | -- | -- | -- | 0 | 1 | 0 | 0 | N/A | N/A | N/A | Tripped due to 400 kV bus fault at KPTCL Guttur SS. Direct trip signal received at Narendra SS.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 39.8
43 | SR2L48 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2013-12-24 | 21:14 | 2013-12-24 | 23:00 | -- | -- | -- | 0 | 1.7667 | 0 | 0 | N/A | N/A | N/A | Tripped due to 400 kV bus fault at KPTCL Guttur SS. Direct trip signal received at Narendra SS. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.7667 | 0 | 0
44 | SR2L49 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L50 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L51 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | 2013-12-06 | 11:07 | 2013-12-06 | 15:42 | -- | -- | -- | 0 | 0 | 0 | 4.5833 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Mysore end as per SRPC recommendation vide SRLDC code no CR-12/154. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.5833
47 | SR2L52 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | 2013-12-07 | 9:03 | 2013-12-07 | 15:14 | -- | -- | -- | 0 | 0 | 0 | 6.1833 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Mysore end as per SRPC recommendation vide SRLDC code no CR-12/178. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.1833
48 | SR2L53 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SRL53 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | 2013-12-09 | 8:10 | 2013-12-09 | 18:47 | -- | -- | -- | 0 | 0 | 0 | 10.6167 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 159 to 250 vide SRLDC code no. CR-12/229. |  | 100
[5 empty] | -- | 2013-12-10 | 8:14 | 2013-12-10 | 17:37 | -- | -- | -- | 0 | 0 | 0 | 9.3833 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 159 to 250 vide SRLDC code no. CR-12/260.
[5 empty] | -- | 2013-12-11 | 8:12 | 2013-12-11 | 17:43 | -- | -- | -- | 0 | 0 | 0 | 9.5167 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 159 to 250 vide SRLDC code no. CR-12/300.
[5 empty] | -- | 2013-12-12 | 8:33 | 2013-12-12 | 11:49 | -- | -- | -- | 0 | 0 | 0 | 3.2667 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 159 to 250 vide SRLDC code no. CR-12/336.
[5 empty] | -- | 2013-12-13 | 8:27 | 2013-12-13 | 18:57 | -- | -- | -- | 0 | 0 | 0 | 10.5 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 159 to 250 vide SRLDC code no. CR-12/385.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 43.2833
50 | SR2L54 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | 2013-12-12 | 15:16 | 2013-12-12 | 16:07 | -- | -- | -- | 0 | 0.85 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of Bus Bar protection (Bus-II) at Neyveli TS II end. DT received at Puducherry end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.85 | 0 | 0
51 | SR2L55 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
52 | SR2L56 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L57 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR2L58 | NEYVELI TS-I EXTENSION - TRICHY | 171.95 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L59 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2013-12-12 | 15:16 | 2013-12-12 | 16:12 | -- | -- | -- | 0 | 0.93333 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of Bus Bar protection (Bus-II) at Neyveli TS II end. DT received at Neyveli TS-1 expansion end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.93333 | 0 | 0
56 | SR2L60 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2013-12-26 | 8:34 | 2013-12-26 | 15:43 | -- | -- | -- | 0 | 0 | 0 | 7.15 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-12/765. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.15
57 | SR2L61 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | 2013-12-12 | 15:16 | 2013-12-12 | 16:15 | -- | -- | -- | 0 | 0.98333 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of Bus Bar protection (Bus-II) at Neyveli TS II end. DT received at Salem end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.98333 | 0 | 0
58 | SR2L62 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | 2013-12-03 | 7:14 | 2013-12-03 | 17:46 | -- | -- | -- | 0 | 0 | 0 | 10.5333 | -- | -- | -- | -- |  | 100
[5 empty] | -- | 2013-12-04 | 7:14 | 2013-12-04 | 17:40 | -- | -- | -- | 0 | 0 | 0 | 10.4333 | -- | -- | --
[5 empty] | -- | 2013-12-05 | 7:35 | 2013-12-05 | 17:42 | -- | -- | -- | 0 | 0 | 0 | 10.1167 | -- | -- | --
[5 empty] | -- | 2013-12-06 | 7:28 | 2013-12-06 | 17:45 | -- | -- | -- | 0 | 0 | 0 | 10.2833 | -- | -- | --
[5 empty] | -- | 2013-12-07 | 7:09 | 2013-12-07 | 17:07 | -- | -- | -- | 0 | 0 | 0 | 9.9667 | -- | -- | --
[5 empty] | -- | 2013-12-09 | 7:18 | 2013-12-09 | 17:05 | -- | -- | -- | 0 | 0 | 0 | 9.7833 | -- | -- | --
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.5333
59 | SR2L63 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | 2013-12-11 | 17:19 | 2013-12-11 | 17:53 | -- | -- | -- | 0.56667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-N (Ph-earth) transient fault during live line OPGW stringing works. FLR: 69 KM from Trichur end. |  | 99.9238
[6 empty] | Sub Total --> | [6 empty] | 0.56667 | 0 | 0 | 0
60 | SR2L64 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L65 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L66 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L67 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | 2013-12-09 | 10:11 | 2013-12-09 | 17:23 | -- | -- | -- | 7.2 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of Line reactor LAs at Udumalpet end vide SRLDC code no. CR-12/230. |  | 99.0323
[6 empty] | Sub Total --> | [6 empty] | 7.2 | 0 | 0 | 0
64 | SR2L68 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L70 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L71 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | 2013-12-11 | 8:39 | 2013-12-11 | 18:11 | -- | -- | -- | 0 | 0 | 0 | 9.5333 | N/A | N/A | N/A | Shut down availed by M/s KSEB for tightening of terminal glands of Bus I & II at Edamon SS vide SRLDC code no. CR-12/301. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.5333
67 | SR2L72 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2013-12-11 | 8:39 | 2013-12-11 | 18:12 | -- | -- | -- | 0 | 0 | 0 | 9.55 | N/A | N/A | N/A | Shut down availed by M/s KSEB for tightening of terminal glands of Bus I & II at Edamon SS vide SRLDC code no. CR-12/302. |  | 99.9731
[6 empty] | 2013-12-18 | 11:33 | 2013-12-18 | 11:45 | -- | -- | -- | 0.2 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Edamon end only during attending maintenance work of 220kV bus-2 at Thirunelveli SS.
[6 empty] | Sub Total --> | [6 empty] | 0.2 | 0 | 0 | 9.55
68 | SR2L73 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L74 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | 2013-12-25 | 23:05 | 2014-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 144.9167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/760. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 144.9167
70 | SR2L75 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2013-12-09 | 12:14 | 2013-12-23 | 11:46 | -- | -- | -- | 0 | 0 | 0 | 335.5333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/234. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 335.5333
71 | SR2L76 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | 2013-12-01 | 0:00 | 2013-12-09 | 12:12 | -- | -- | -- | 0 | 0 | 0 | 204.2 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message dtd. 20.11.13. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 204.2
72 | SR2L77 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L78 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L79 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR2L80 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L83 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L84 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L85 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L86 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L87 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L88 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR2L89 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L90 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | 2013-12-30 | 22:20 | 2013-12-30 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 4.84 kM from Kalivindapattu end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR2L91 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | 2013-12-01 | 0:00 | 2013-12-02 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 42.2333 | N/A | N/A | N/A | Shut down availed by M/s NTECL for attending gas leakage at isolator at Vallur GIS end vide SRLDC code no CR-11/ 873. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 42.2333
85 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | 2013-12-08 | 9:30 | 2013-12-08 | 15:09 | -- | -- | -- | 5.65 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-12/210. |  | 99.2406
[6 empty] | Sub Total --> | [6 empty] | 5.65 | 0 | 0 | 0
88 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2013-12-08 | 11:44 | 2013-12-08 | 11:56 | -- | -- | -- | 0 | 0.2 | 0 | 0 | N/A | N/A | N/A | Tripped (220KV side only) on operation of Busbar protection at 220KV Somanahalli KPTCL SS due to insulator flashover in 220KV Somanhalli - Harohalli line. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.2 | 0 | 0
89 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
104 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [11 empty] | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | 2013-12-15 | 8:43 | 2013-12-15 | 14:01 | -- | -- | -- | 5.3 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-12/430. |  | 99.2876
[6 empty] | Sub Total --> | [6 empty] | 5.3 | 0 | 0 | 0
109 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | 2013-12-12 | 8:46 | 2013-12-13 | 8:57 | -- | -- | -- | 24.1833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for rectification of oil mixing between main tank and OLTC tank vide SRLDC code no. CR-12/337. |  | 96.7496
[6 empty] | Sub Total --> | [6 empty] | 24.1833 | 0 | 0 | 0
113 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | 2013-12-24 | 9:48 | 2013-12-24 | 15:12 | -- | -- | -- | 5.4 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-12/695. |  | 99.2742
[6 empty] | Sub Total --> | [6 empty] | 5.4 | 0 | 0 | 0
114 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T36 | TRICHY ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T37 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T38 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T39 | TRIVANDRUM - ICT II | 315 | SR-II | -- | 2013-12-16 | 14:30 | 2013-12-16 | 14:48 | -- | -- | -- | 0.3 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending hotspot on 220 kV Y-phase CT terminal connector vide SRLDC code no. CR-12/467. |  | 99.9597
[6 empty] | Sub Total --> | [6 empty] | 0.3 | 0 | 0 | 0
123 | SR2T40 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T41 | UDUMALPET ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T42 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T43 | UDUMALPET ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2013-12-01 | 0:00 | 2013-12-01 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 22.3333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-02 | 9:28 | 2013-12-02 | 21:50 | -- | -- | -- | 0 | 0 | 0 | 12.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-03 | 9:44 | 2013-12-04 | 23:27 | -- | -- | -- | 0 | 0 | 0 | 37.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-05 | 6:49 | 2013-12-07 | 22:30 | -- | -- | -- | 0 | 0 | 0 | 63.6833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-08 | 9:36 | 2013-12-08 | 22:02 | -- | -- | -- | 0 | 0 | 0 | 12.4333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-09 | 8:51 | 2013-12-09 | 22:43 | -- | -- | -- | 0 | 0 | 0 | 13.8667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-10 | 14:20 | 2013-12-11 | 21:48 | -- | -- | -- | 0 | 0 | 0 | 31.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-12 | 9:05 | 2013-12-13 | 22:56 | -- | -- | -- | 0 | 0 | 0 | 37.85 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-14 | 7:35 | 2013-12-14 | 22:10 | -- | -- | -- | 0 | 0 | 0 | 14.5833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 9:20 | 2013-12-16 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 12.6833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-17 | 11:30 | 2013-12-17 | 23:12 | -- | -- | -- | 0 | 0 | 0 | 11.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-18 | 8:11 | 2013-12-22 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 109.8333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-23 | 7:05 | 2013-12-23 | 22:25 | -- | -- | -- | 0 | 0 | 0 | 15.3333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 8:12 | 2013-12-25 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 37.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-26 | 10:44 | 2013-12-28 | 23:17 | -- | -- | -- | 0 | 0 | 0 | 60.55 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-29 | 7:27 | 2013-12-29 | 22:09 | -- | -- | -- | 0 | 0 | 0 | 14.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-30 | 7:51 | 2013-12-30 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 15.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-31 | 7:26 | 2013-12-31 | 22:09 | -- | -- | -- | 0 | 0 | 0 | 14.7167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 538.7833
128 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2013-12-03 | 9:45 | 2013-12-04 | 23:15 | -- | -- | -- | 0 | 0 | 0 | 37.5 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-05 | 8:03 | 2013-12-05 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 14.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-06 | 8:54 | 2013-12-06 | 23:03 | -- | -- | -- | 0 | 0 | 0 | 14.15 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-07 | 7:05 | 2013-12-07 | 22:23 | -- | -- | -- | 0 | 0 | 0 | 15.3 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-08 | 9:35 | 2013-12-08 | 21:54 | -- | -- | -- | 0 | 0 | 0 | 12.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-09 | 8:08 | 2013-12-09 | 22:40 | -- | -- | -- | 0 | 0 | 0 | 14.5333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-10 | 14:10 | 2013-12-11 | 21:53 | -- | -- | -- | 0 | 0 | 0 | 31.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-12 | 9:03 | 2013-12-13 | 22:48 | -- | -- | -- | 0 | 0 | 0 | 37.75 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-14 | 7:30 | 2013-12-14 | 21:52 | -- | -- | -- | 0 | 0 | 0 | 14.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 9:23 | 2013-12-16 | 22:02 | -- | -- | -- | 0 | 0 | 0 | 12.65 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-17 | 11:21 | 2013-12-17 | 23:04 | -- | -- | -- | 0 | 0 | 0 | 11.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-18 | 8:07 | 2013-12-22 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 109.6167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-23 | 7:24 | 2013-12-23 | 22:10 | -- | -- | -- | 0 | 0 | 0 | 14.7667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 8:03 | 2013-12-25 | 22:05 | -- | -- | -- | 0 | 0 | 0 | 38.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-26 | 10:39 | 2013-12-26 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 11.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-28 | 8:27 | 2013-12-28 | 23:02 | -- | -- | -- | 0 | 0 | 0 | 14.5833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-29 | 8:27 | 2013-12-29 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 13.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-30 | 7:41 | 2013-12-30 | 22:43 | -- | -- | -- | 0 | 0 | 0 | 15.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-31 | 7:11 | 2013-12-31 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 14.75 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 447.9167
130 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2013-12-03 | 9:43 | 2013-12-15 | 21:59 | -- | -- | -- | 0 | 0 | 0 | 300.2667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-16 | 9:23 | 2013-12-17 | 23:03 | -- | -- | -- | 0 | 0 | 0 | 37.6667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-21 | 16:24 | 2013-12-23 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 53.7333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 8:05 | 2013-12-25 | 22:03 | -- | -- | -- | 0 | 0 | 0 | 37.9667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-26 | 12:54 | 2013-12-29 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 81.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-30 | 7:43 | 2013-12-30 | 22:44 | -- | -- | -- | 0 | 0 | 0 | 15.0167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-31 | 7:09 | 2014-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 16.85 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 542.5333
132 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2013-12-01 | 0:00 | 2013-12-02 | 21:58 | -- | -- | -- | 0 | 0 | 0 | 45.9667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-03 | 9:46 | 2013-12-04 | 23:24 | -- | -- | -- | 0 | 0 | 0 | 37.6333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-07 | 14:36 | 2013-12-11 | 22:12 | -- | -- | -- | 0 | 0 | 0 | 103.6 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-12 | 9:03 | 2013-12-13 | 22:55 | -- | -- | -- | 0 | 0 | 0 | 37.8667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 10:02 | 2013-12-16 | 22:07 | -- | -- | -- | 0 | 0 | 0 | 12.0833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-17 | 11:28 | 2013-12-22 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 130.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 9:36 | 2013-12-25 | 22:15 | -- | -- | -- | 0 | 0 | 0 | 36.65 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-26 | 10:40 | 2013-12-26 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 11.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-30 | 17:18 | 2013-12-30 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 5.6 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 421.3333
134 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2013-12-05 | 10:00 | 2013-12-05 | 22:19 | -- | -- | -- | 0 | 0 | 0 | 12.3167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-06 | 8:55 | 2013-12-06 | 23:02 | -- | -- | -- | 0 | 0 | 0 | 14.1167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-07 | 7:02 | 2013-12-07 | 22:18 | -- | -- | -- | 0 | 0 | 0 | 15.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-08 | 9:36 | 2013-12-08 | 21:52 | -- | -- | -- | 0 | 0 | 0 | 12.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-09 | 18:28 | 2013-12-09 | 22:39 | -- | -- | -- | 0 | 0 | 0 | 4.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-11 | 9:49 | 2013-12-11 | 21:46 | -- | -- | -- | 0 | 0 | 0 | 11.95 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-14 | 7:28 | 2013-12-14 | 21:55 | -- | -- | -- | 0 | 0 | 0 | 14.45 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 10:22 | 2013-12-16 | 21:52 | -- | -- | -- | 0 | 0 | 0 | 11.5 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-21 | 16:26 | 2013-12-22 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 29.3 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-23 | 7:00 | 2013-12-23 | 22:11 | -- | -- | -- | 0 | 0 | 0 | 15.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 8:03 | 2013-12-25 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 38.0167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-28 | 8:26 | 2013-12-28 | 23:02 | -- | -- | -- | 0 | 0 | 0 | 14.6 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-30 | 7:44 | 2013-12-30 | 22:43 | -- | -- | -- | 0 | 0 | 0 | 14.9833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 208.1333
135 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2013-12-05 | 8:05 | 2013-12-05 | 22:30 | -- | -- | -- | 0 | 0 | 0 | 14.4167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-06 | 8:57 | 2013-12-06 | 23:06 | -- | -- | -- | 0 | 0 | 0 | 14.15 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-11 | 9:49 | 2013-12-11 | 21:50 | -- | -- | -- | 0 | 0 | 0 | 12.0167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 40.5833
136 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2013-12-03 | 9:41 | 2013-12-04 | 23:22 | -- | -- | -- | 0 | 0 | 0 | 37.6833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-07 | 14:29 | 2013-12-11 | 22:09 | -- | -- | -- | 0 | 0 | 0 | 103.6667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 10:00 | 2013-12-16 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 12.0667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-17 | 11:26 | 2013-12-22 | 21:54 | -- | -- | -- | 0 | 0 | 0 | 130.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 9:45 | 2013-12-25 | 22:12 | -- | -- | -- | 0 | 0 | 0 | 36.45 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-26 | 10:37 | 2013-12-26 | 22:10 | -- | -- | -- | 0 | 0 | 0 | 11.55 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-30 | 17:06 | 2013-12-30 | 22:56 | -- | -- | -- | 0 | 0 | 0 | 5.8333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 337.7167
138 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2013-12-05 | 8:07 | 2013-12-13 | 23:01 | -- | -- | -- | 0 | 0 | 0 | 206.9 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-23 | 7:03 | 2013-12-23 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 15.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 9:33 | 2013-12-25 | 22:11 | -- | -- | -- | 0 | 0 | 0 | 36.6333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-26 | 12:52 | 2013-12-26 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 9.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-29 | 8:25 | 2013-12-29 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 13.6 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-31 | 7:10 | 2014-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 16.8333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 298.5167
139 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
140 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2013-12-26 | 12:56 | 2013-12-26 | 21:58 | -- | -- | -- | 0 | 0 | 0 | 9.0333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.0333
141 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2013-12-26 | 12:57 | 2013-12-26 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 9.1167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.1167
142 | SR2R17 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2013-12-07 | 7:03 | 2013-12-08 | 22:07 | -- | -- | -- | 0 | 0 | 0 | 39.0667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-09 | 18:29 | 2013-12-15 | 22:00 | -- | -- | -- | 0 | 0 | 0 | 147.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-23 | 7:24 | 2014-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 208.6 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 395.1833
143 | SR2R18 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
144 | SR2R19 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
145 | SR2R20 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2013-12-02 | 12:07 | 2013-12-02 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 9.9 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-04 | 10:08 | 2013-12-15 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 275.8 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 9:23 | 2013-12-23 | 22:09 | -- | -- | -- | 0 | 0 | 0 | 180.7667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 9:34 | 2014-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 182.4333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 648.9
146 | SR2R21 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2013-12-02 | 12:07 | 2013-12-02 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 9.9 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-12-04 | 10:08 | 2013-12-15 | 21:57 | -- | -- | -- | 0 | 0 | 0 | 275.8167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-16 | 9:23 | 2013-12-23 | 22:11 | -- | -- | -- | 0 | 0 | 0 | 180.8 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-12-24 | 9:36 | 2014-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 182.4 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 648.9167
147 | SR2R22 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2R23 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2R24 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
150 | SR2R25 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | 2013-12-31 | 3:55 | 2013-12-31 | 3:55 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 235.9 kM from Kolar end (Tower no. 3046). |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2R26 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
[22 empty] | 15093.4409 | 8398.9292 | 4194.5116 | 2300 | 200 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse