## SOP
Standard of Performance data for the month of December-2014
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | SRPC, SRPC/SE-I/PGTA/2014/195-211, Dtd. 14.01.15 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2014-12-04 | 9:12 | 2014-12-04 | 17:12 | -- | -- | -- | 0 | 0 | 0 | 8 | -- | -- | -- | Shut down availed by M/s KSEB for routine maintenance works at Edappon end vide SRLDC code no. CR-12/76. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | Insulator failure (Hilly area) | 2014-12-16 | 10:01 | 2014-12-16 | 17:00 | -- | 1 | -- | 0 | 0 | 0 | 6.9833 | N/A | N/A | N/A | Shut down availed by M/s KSEB for testing of busbar protection relay at Pallom SS vide SRLDC code no. CR-12/435. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.9833
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | -- | 2014-12-09 | 8:38 | 2014-12-09 | 17:46 | -- | -- | -- | 0 | 0 | 0 | 9.1333 | -- | -- | -- | Shut down availed by M/s KSEB for relay testing works at Punnapra end vide SRLDC code no. CR-12/178. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.1333
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | 2014-12-20 | 10:37 | 2014-12-20 | 14:03 | -- | -- | -- | 0 | 0 | 0 | 3.4333 | -- | -- | -- | Shut down availed by M/s KSEB for attending hot spots at Punnapra end vide SRLDC code no. CR-12/556. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.4333
8 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
9 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
11 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
15 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | 2014-12-21 | 10:17 | 2014-12-21 | 16:14 | -- | -- | -- | 0 | 0 | 0 | 5.95 | N/A | N/A | N/A | Shut down availed by M/s TNEB for enabling auto reclosure scheme at Siruseri end vide SRLDC code no. CR-12/586. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.95
16 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | 2014-12-21 | 16:19 | 2014-12-21 | 18:23 | -- | -- | -- | 0 | 0 | 0 | 2.0667 | -- | -- | -- | Shut down availed by M/s TNEB for enabling auto reclosure scheme at Siruseri end vide SRLDC code no. CR-12/590. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.0667
17 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
18 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
20 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- | 2014-12-01 | 0:00 | 2014-12-04 | 9:09 | -- | -- | -- | 0 | 0 | 0 | 81.15 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/858. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 81.15
21 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L22 | COASTAL ENERGEN-TUTICORIN JV TPS 1 | 36.304 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L23 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | 2014-12-10 | 4:05 | 2014-12-10 | 6:13 | -- | -- | -- | 0 | 0 | 0 | 2.1333 | -- | -- | -- | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/275. |  | 100
[6 empty] | 2014-12-10 | 3:57 | 2014-12-10 | 4:05 |  |  |  | 0 | 0 | 0.13333 | 0 |  |  |  | Line tripped on operation of over voltage protection at Chittoor end. Direct trip signal received at Cuddappa end.
[6 empty] | 2014-12-11 | 14:56 | 2014-12-11 | 17:38 |  |  |  | 0 | 0 | 0 | 2.7 |  |  |  | Shut down availed by M/s APTRANSCO to carry out relay testing work at Chittoor end vide SRLDC code no. CR-12/263.
[6 empty] | 2014-12-14 | 23:58 | 2014-12-15 | 0:10 |  |  |  | 0 | 0 | 0.2 | 0 |  |  |  | Line tripped on operation of over voltage protection at Chittoor end. Direct trip signal received at Cuddappa end.
[6 empty] | 2014-12-15 | 0:10 | 2014-12-15 | 7:04 |  |  |  | 0 | 0 | 0 | 6.9 |  |  |  | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/475.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.1333
24 | SR2L24 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L25 | GOOTY - BANGALORE | 301.667 | SR-II | -- | 2014-12-06 | 9:02 | 2014-12-06 | 18:11 | -- | -- | -- | 9.15 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works of line reactor & terminal equipments at Somanhalli SS vide SRLDC code no. CR-12/135. |  | 98.7702
[6 empty] | Sub Total --> | [6 empty] | 9.15 | 0 | 0 | 0
26 | SR2L26 | HASSAN - MYSORE I | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L27 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L28 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L29 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2014-12-19 | 2:01 | 2014-12-19 | 2:10 | -- | -- | -- | 0 | 0 | 0.15 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end. |  | 100
[5 empty] | -- | 2014-12-19 | 2:10 | 2014-12-19 | 6:57 | -- | -- | -- | 0 | 0 | 0 | 4.7833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/693.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.15 | 0
30 | SR2L30 | HOSUR-SALEM II | 125.325 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
31 | SR2L31 | HOSUR-SALEM | 126.339 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
32 | SR2L32 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L33 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
34 | SR2L34 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2014-12-22 | 8:21 | 2014-12-23 | 17:19 | -- | -- | -- | 0 | 0 | 0 | 32.9667 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for LA replacement work at Kaiga end vide SRLDC code no. CR-12/603. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 32.9667
35 | SR2L35 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2014-12-12 | 20:31 | 2014-12-12 | 20:45 | -- | -- | -- | 0 | 0 | 0.23333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Guttur end. Direct trip signal received at Kaiga end. |  | 100
[5 empty] | -- | 2014-12-12 | 20:45 | 2014-12-13 | 8:14 | -- | -- | -- | 0 | 0 | 0 | 11.4833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/398.
[5 empty] | -- | 2014-12-28 | 8:40 | 2014-12-29 | 14:40 | -- | -- | -- | 0 | 0 | 0 | 30 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for new bus reactor construction works at Guttur end vide SRLDC code no. CR-12/739.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.23333 | 41.4833
36 | SR2L36 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L37 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L38 | KOLAR - HOODY - I | 51.067 | SR-II | -- | 2014-12-13 | 9:07 | 2014-12-14 | 16:28 | -- | -- | -- | 0 | 0 | 0 | 31.35 | -- | -- | -- | Shut down availed by M/s KPTCL for construction of ICT-3 bays at Hoody end vide SRLDC code no. CR-12/342. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 31.35
39 | SR2L39 | KOLAR - HOODY - II | 51.067 | SR-II | -- | 2014-12-13 | 9:08 | 2014-12-14 | 21:22 | -- | -- | -- | 0 | 0 | 0 | 36.2333 | -- | -- | -- | Shut down availed by M/s KPTCL for construction of ICT-3 bays at Hoody end vide SRLDC code no. CR-12/343. |  | 100
[6 empty] | 2014-12-15 | 13:34 | 2014-12-15 | 19:57 |  |  |  | 0 | 0 | 0 | 6.3833 |  |  |  | Shut down availed by M/s KPTCL for completion of SCADA works at Hoody end vide SRLDC code no. CR-12/410.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 36.2333
40 | SR2L40 | KOLAR - HOSUR - I | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L41 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L42 | KOLAR - THIRUVALAM - I | 153.195 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
43 | SR2L43 | MADURAI - COASTAL ENERGEN 1 | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L44 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | 2014-12-13 | 23:46 | 2014-12-16 | 17:54 | -- | -- | -- | 0 | 0 | 0 | 66.1333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/366. |  | 100
[5 empty] | -- | 2014-12-30 | 7:05 | 2015-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 40.9167 | N/A | N/A | N/A | Shut down availed for construction works of LILO of 400KV Madurai - Tuticorin line-2 at Tuticorin PS vide SRLDC code no. CR-12/769.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 107.05
45 | SR2L45 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L46 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2014-12-01 | 0:00 | 2014-12-07 | 13:45 | -- | -- | -- | 0 | 0 | 0 | 157.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/763. |  | 100
[5 empty] | -- | 2014-12-11 | 0:25 | 2014-12-11 | 11:46 | -- | -- | -- | 0 | 0 | 0 | 11.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/241.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 169.1
47 | SR2L47 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2014-12-01 | 0:00 | 2014-12-05 | 7:30 | -- | -- | -- | 0 | 0 | 0 | 103.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/687. |  | 100
[5 empty] | -- | 2014-12-13 | 23:13 | 2014-12-15 | 8:39 | -- | -- | -- | 0 | 0 | 0 | 33.4333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/365.
[5 empty] | -- | 2014-12-16 | 0:02 | 2014-12-18 | 7:14 | -- | -- | -- | 0 | 0 | 0 | 55.2 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/426.
[5 empty] | -- | 2014-12-18 | 21:54 | 2014-12-19 | 9:59 | -- | -- | -- | 0 | 0 | 0 | 12.0833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/512.
[6 empty] | 2014-12-19 | 14:42 | 2014-12-19 | 16:56 |  |  |  | 0 | 0 | 0 | 2.2333 |  |  |  | Tripped on R-N fault during live line OPGW stringing works.
[6 empty] | 2014-12-24 | 22:06 | 2014-12-26 | 8:03 |  |  |  | 0 | 0 | 0 | 33.95 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/699.
[6 empty] | 2014-12-29 | 22:26 | 2014-12-30 | 10:08 |  |  |  | 0 | 0 | 0 | 11.7 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/768.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 204.2167
48 | SR2L48 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2014-12-05 | 22:46 | 2014-12-08 | 8:19 | -- | -- | -- | 0 | 0 | 0 | 57.55 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/128. |  | 100
[5 empty] | -- | 2014-12-19 | 21:47 | 2014-12-22 | 8:17 | -- | -- | -- | 0 | 0 | 0 | 58.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/545.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 116.05
49 | SR2L49 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR2L50 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L51 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
52 | SR2L52 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | 2014-12-11 | 0:44 | 2014-12-11 | 0:55 | -- | -- | -- | 0 | 0 | 0.18333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Nelamangala end. Direct trip signal received at Mysore end. |  | 100
[6 empty] | 2014-12-11 | 0:55 | 2014-12-11 | 7:45 |  |  |  | 0 | 0 | 0 | 6.8333 |  |  |  | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/320.
[6 empty] | 2014-12-15 | 0:55 | 2014-12-15 | 6:54 |  |  |  | 0 | 0 | 0 | 5.9833 |  |  |  | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/476.
[6 empty] | 2014-12-15 | 0:45 | 2014-12-15 | 0:55 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | Line tripped on operation of over voltage protection at Nelamangala end. Direct trip signal received at Mysore end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.18333 | 0
53 | SR2L53 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SRL53 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L54 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | 2014-12-15 | 9:13 | 2014-12-15 | 16:10 | -- | -- | -- | 0 | 0 | 0 | 6.95 | -- | -- | -- | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-12/393. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.95
56 | SR2L55 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2014-12-10 | 23:58 | 2014-12-11 | 0:10 | -- | -- | -- | 0 | 0 | 0.2 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Pugalur end. Direct trip signal received at Neyveli TS-2 end. |  | 100
[5 empty] | -- | 2014-12-11 | 0:10 | 2014-12-11 | 11:42 | -- | -- | -- | 0 | 0 | 0 | 11.5333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/318.
[5 empty] | -- | 2014-12-14 | 23:58 | 2014-12-15 | 0:28 | -- | -- | -- | 0 | 0 | 0.5 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Pugalur end.
[5 empty] | -- | 2014-12-15 | 2:10 | 2014-12-15 | 9:06 | -- | -- | -- | 0 | 0 | 0 | 6.9333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/477.
[5 empty] | -- | 2014-12-15 | 1:55 | 2014-12-15 | 2:10 | -- | -- | -- | 0 | 0 | 0.25 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Pugalur end. Direct trip signal received at Neyveli TS-2 end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.95 | 18.4667
57 | SR2L56 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
58 | SR2L57 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | 2014-12-28 | 9:51 | 2014-12-28 | 16:17 | -- | -- | -- | 0 | 0 | 0 | 6.4333 | N/A | N/A | N/A | Shut down availed for bay extension works under TANTRANSCO consultancy works at Pugalur end vide SRLDC code no. CR-12/741. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.4333
59 | SR2L58 | NEYVELI TS-I EXTENSION - TRICHY | 171.95 | SR-II | -- | 2014-12-17 | 8:47 | 2014-12-19 | 19:33 | -- | -- | -- | 0 | 0 | 0 | 58.7667 | -- | -- | -- | Shut down availed by M/s NLC for relay retrofitting works at Neyveli TS-I Exp SS vide SRLDC code no. CR-12/459. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 58.7667
60 | SR2L59 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2014-12-06 | 8:55 | 2014-12-06 | 16:03 | -- | -- | -- | 0 | 0 | 0 | 7.1333 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli end vide SRLDC code No. CR12/133. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.1333
61 | SR2L60 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L61 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L62 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L63 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L64 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L65 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | 2014-12-29 | 9:25 | 2014-12-30 | 12:41 | -- | -- | -- | 0 | 0 | 0 | 27.2667 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction works of 400 kV Karaikudi - Pugalur D/C line vide SRLDC code no. CR-12/758. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.2667
67 | SR2L66 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | 2014-12-17 | 0:15 | 2014-12-18 | 10:05 | -- | -- | -- | 0 | 0 | 0 | 33.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/453. |  | 100
[5 empty] | -- | 2014-12-21 | 18:46 | 2014-12-22 | 9:00 | -- | -- | -- | 0 | 0 | 0 | 14.2333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/595.
[6 empty] | 2014-12-29 | 9:24 | 2014-12-30 | 12:43 |  |  |  | 0 | 0 | 0 | 27.3167 |  |  |  | Shut down availed by M/s TNEB for construction works of 400 kV Karaikudi - Pugalur D/C line vide SRLDC code no. CR-12/759.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.0667
68 | SR2L67 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L68 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
70 | SR2L69 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L70 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
72 | SR2L71 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L72 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L73 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2014-12-01 | 0:00 | 2014-12-07 | 13:45 | -- | -- | -- | 0 | 0 | 0 | 157.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/763. |  | 100
[5 empty] | -- | 2014-12-11 | 0:25 | 2014-12-11 | 11:46 | -- | -- | -- | 0 | 0 | 0 | 11.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/241.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 169.1
75 | SR2L74 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L75 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L76 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | 2014-12-01 | 0:00 | 2014-12-10 | 17:50 | -- | -- | -- | 0 | 0 | 0 | 233.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/754. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 233.8333
78 | SR2L77 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L78 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L79 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L80 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR2L81 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II |  | 2014-12-10 | 1:20 | 2014-12-10 | 7:06 | -- | -- | -- | 0 | 0 | 0 | 5.7667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/273. |  | 100
[5 empty] | -- | 2014-12-10 | 1:08 | 2014-12-10 | 1:20 | -- | -- | -- | 0 | 0 | 0.2 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Kalivindapattu end. Direct trip signal received at Thiruvalam end.
[5 empty] | -- | 2014-12-13 | 0:55 | 2014-12-13 | 7:12 | -- | -- | -- | 0 | 0 | 0 | 6.2833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/332.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.2 | 12.05
83 | SR2L82 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | 2014-12-10 | 1:08 | 2014-12-10 | 1:20 | -- | -- | -- | 0 | 0 | 0.2 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Kalivindapattu end. Direct trip signal received at Thiruvalam end. |  | 100
[5 empty] | -- | 2014-12-10 | 1:20 | 2014-12-10 | 7:10 | -- | -- | -- | 0 | 0 | 0 | 5.8333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/273.
[6 empty] | 2014-12-21 | 0:34 | 2014-12-26 | 8:47 |  |  |  | 0 | 0 | 0 | 128.2167 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/582.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.2 | 5.8333
84 | SR2L83 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
85 | SR2L84 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2L85 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | 2014-12-15 | 13:55 | 2014-12-16 | 18:22 | -- | -- | -- | 0 | 0 | 0 | 28.45 | -- | -- | -- | Shut down availed by M/s TNEB for construction works 400 kV Karaikudi-Pugalur line vide SRLDC code no. CR-12/408. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 28.45
87 | SR2L86 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | 2014-12-15 | 13:42 | 2014-12-16 | 18:10 | -- | -- | -- | 0 | 0 | 0 | 28.4667 | -- | -- | -- | Shut down availed by M/s TNEB for construction works 400 kV Karaikudi-Pugalur line vide SRLDC code no. CR-12/409. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 28.4667
88 | SR2L87 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
89 | SR2L88 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | [17 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2L89 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2L90 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2L91 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | 2014-12-04 | 10:05 | 2014-12-04 | 16:13 | -- | -- | -- | 6.1333 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for collecting bushing oil samples vide SRLDC code no. CR-12/79. |  | 99.1756
[6 empty] | Sub Total --> | [6 empty] | 6.1333 | 0 | 0 | 0
94 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | 2014-12-05 | 9:23 | 2014-12-05 | 14:04 | -- | -- | -- | 4.6833 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for collecting bushing oil samples vide SRLDC code no. CR-12/111. |  | 99.3705
[6 empty] | 2014-12-22 | 16:45 | 2014-12-22 | 22:00 |  |  |  | 5.25 | 0 | 0 | 0 |  |  |  | Shut down availed to attend heavy oil leakage from 245 kV B-Phase bushing vide SRLDC code no. CR-12/622.
[6 empty] | Sub Total --> | [6 empty] | 4.6833 | 0 | 0 | 0
95 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | 2014-12-01 | 9:53 | 2014-12-01 | 13:55 | -- | -- | -- | 4.0333 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for bushing oil sampling works vide SRLDC code no. CR-12/04. |  | 99.4579
[6 empty] | Sub Total --> | [6 empty] | 4.0333 | 0 | 0 | 0
103 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
104 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | 2014-12-09 | 9:14 | 2014-12-09 | 16:34 | -- | -- | -- | 7.3333 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for AMP works vide SRLDC code no. CR-12/180. |  | 99.0143
[6 empty] | Sub Total --> | [6 empty] | 7.3333 | 0 | 0 | 0
109 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | 2014-12-15 | 10:32 | 2014-12-15 | 18:14 | -- | -- | -- | 7.7 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-12/399. |  | 98.9651
[6 empty] | Sub Total --> | [6 empty] | 7.7 | 0 | 0 | 0
113 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | 2014-12-20 | 10:38 | 2014-12-20 | 18:19 | -- | -- | -- | 7.6833 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for AMP works vide SRLDC code no. CR-12/557. |  | 98.9673
[6 empty] | Sub Total --> | [6 empty] | 7.6833 | 0 | 0 | 0
114 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | 2014-12-02 | 8:10 | 2014-12-02 | 21:33 | -- | -- | -- | 0 | 0 | 0 | 13.3833 | -- | -- | -- | Shut down availed for construction works related to extension of tertiary supply for redundant aux source vide SRLDC code no. CR-12/31. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.3833
115 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | 2014-12-20 | 9:26 | 2014-12-22 | 13:28 | -- | -- | -- | 52.0333 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for bushing replacement works vide SRLDC code no. CR-12/553. |  | 93.0063
[6 empty] | Sub Total --> | [6 empty] | 52.0333 | 0 | 0 | 0
125 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | 2014-12-20 | 16:51 | 2014-12-20 | 19:29 | -- | -- | -- | 2.6333 | 0 | 0 | 0 | -- | -- | -- | Tripped on operation of Buchholz relay. |  | 99.6461
[6 empty] | Sub Total --> | [6 empty] | 2.6333 | 0 | 0 | 0
126 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2T36 | TRICHY ICT - I | 315 | SR-II | -- | 2014-12-17 | 9:35 | 2014-12-17 | 18:57 | -- | -- | -- | 9.3667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-12/462. |  | 98.741
[6 empty] | Sub Total --> | [6 empty] | 9.3667 | 0 | 0 | 0
129 | SR2T37 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T38 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T39 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T40 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2T41 | UDUMALPET ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T42 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
135 | SR2T43 | UDUMALPET ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
136 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2014-12-01 | 9:14 | 2014-12-05 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 109.6667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-06 | 6:55 | 2014-12-08 | 0:11 | -- | -- | -- | 0 | 0 | 0 | 41.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-08 | 7:18 | 2014-12-10 | 22:00 | -- | -- | -- | 0 | 0 | 0 | 62.7 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-11 | 12:10 | 2014-12-11 | 21:29 | -- | -- | -- | 0 | 0 | 0 | 9.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-12 | 10:54 | 2014-12-12 | 22:00 | -- | -- | -- | 0 | 0 | 0 | 11.1 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-13 | 9:06 | 2014-12-13 | 23:02 | -- | -- | -- | 0 | 0 | 0 | 13.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-14 | 10:05 | 2014-12-14 | 21:25 | -- | -- | -- | 0 | 0 | 0 | 11.3333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-15 | 8:25 | 2014-12-16 | 23:25 | -- | -- | -- | 0 | 0 | 0 | 39 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-17 | 8:25 | 2014-12-18 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 37.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-19 | 6:59 | 2014-12-19 | 21:43 | -- | -- | -- | 0 | 0 | 0 | 14.7333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-20 | 8:37 | 2014-12-20 | 22:35 | -- | -- | -- | 0 | 0 | 0 | 13.9667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-22 | 9:49 | 2014-12-24 | 22:16 | -- | -- | -- | 0 | 0 | 0 | 60.45 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-26 | 7:30 | 2014-12-28 | 21:49 | -- | -- | -- | 0 | 0 | 0 | 62.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-30 | 8:27 | 2015-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 39.55 | N/A | N/A | N/A | H/T for voltage regulation |  | #VALUE!
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 526.65
137 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2014-12-02 | 11:49 | 2014-12-03 | 1:38 | -- | -- | -- | 0 | 0 | 0 | 13.8167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-03 | 9:34 | 2014-12-05 | 22:47 | -- | -- | -- | 0 | 0 | 0 | 61.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-06 | 6:48 | 2014-12-07 | 0:25 | -- | -- | -- | 0 | 0 | 0 | 17.6167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-07 | 7:40 | 2014-12-08 | 0:04 | -- | -- | -- | 0 | 0 | 0 | 16.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-08 | 7:27 | 2014-12-10 | 21:46 | -- | -- | -- | 0 | 0 | 0 | 62.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-11 | 11:59 | 2014-12-11 | 21:27 | -- | -- | -- | 0 | 0 | 0 | 9.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-12 | 11:07 | 2014-12-12 | 21:57 | -- | -- | -- | 0 | 0 | 0 | 10.8333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2014-12-13 | 9:08 | 2014-12-13 | 22:57 |  |  |  | 0 | 0 | 0 | 13.8167 |  |  |  | H/T for voltage regulation
[5 empty] | -- | 2014-12-15 | 8:20 | 2014-12-16 | 23:18 | -- | -- | -- | 0 | 0 | 0 | 38.9667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-17 | 8:24 | 2014-12-17 | 23:35 | -- | -- | -- | 0 | 0 | 0 | 15.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-18 | 7:07 | 2014-12-18 | 21:39 | -- | -- | -- | 0 | 0 | 0 | 14.5333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-19 | 6:56 | 2014-12-19 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 14.8 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-20 | 8:37 | 2014-12-20 | 22:28 | -- | -- | -- | 0 | 0 | 0 | 13.85 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-22 | 9:48 | 2014-12-24 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 60.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-26 | 7:19 | 2014-12-27 | 21:49 | -- | -- | -- | 0 | 0 | 0 | 38.5 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-30 | 8:26 | 2015-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 39.5667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 441.1
138 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
139 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
140 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2014-12-01 | 9:15 | 2014-12-03 | 1:36 | -- | -- | -- | 0 | 0 | 0 | 40.35 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-03 | 9:32 | 2014-12-05 | 22:48 | -- | -- | -- | 0 | 0 | 0 | 61.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-06 | 6:50 | 2014-12-12 | 21:55 | -- | -- | -- | 0 | 0 | 0 | 159.0833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-14 | 9:55 | 2014-12-16 | 23:20 | -- | -- | -- | 0 | 0 | 0 | 61.4167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-17 | 8:23 | 2014-12-18 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 37.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-19 | 6:47 | 2014-12-19 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 14.8833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-22 | 9:51 | 2014-12-24 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 60.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-26 | 7:21 | 2014-12-28 | 21:43 | -- | -- | -- | 0 | 0 | 0 | 62.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-30 | 8:27 | 2015-01-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 39.55 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 536.4167
141 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2014-12-01 | 0:00 | 2014-12-12 | 22:17 | -- | -- | -- | 0 | 0 | 0 | 286.2833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2014-12-15 | 12:15 | 2014-12-18 | 21:51 |  |  |  | 0 | 0 | 0 | 81.6 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-19 | 7:03 | 2014-12-19 | 22:03 |  |  |  | 0 | 0 | 0 | 15 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-20 | 9:56 | 2015-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 278.0667 |  |  |  | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 286.2833
143 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2014-12-03 | 10:30 | 2014-12-03 | 21:23 | -- | -- | -- | 0 | 0 | 0 | 10.8833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-12-09 | 8:18 | 2014-12-10 | 4:17 | -- | -- | -- | 0 | 0 | 0 | 19.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-12-11 | 12:05 | 2014-12-11 | 21:25 | -- | -- | -- | 0 | 0 | 0 | 9.3333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2014-12-13 | 9:05 | 2014-12-13 | 22:58 |  |  |  | 0 | 0 | 0 | 13.8833 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-19 | 6:46 | 2014-12-19 | 21:39 |  |  |  | 0 | 0 | 0 | 14.8833 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-23 | 12:24 | 2014-12-23 | 21:30 |  |  |  | 0 | 0 | 0 | 9.1 |  |  |  | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 40.2
144 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2014-12-03 | 10:33 | 2014-12-03 | 21:30 | -- | -- | -- | 0 | 0 | 0 | 10.95 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2014-12-09 | 8:11 | 2014-12-10 | 21:46 |  |  |  | 0 | 0 | 0 | 37.5833 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-16 | 9:28 | 2014-12-16 | 23:16 |  |  |  | 0 | 0 | 0 | 13.8 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-17 | 8:26 | 2014-12-17 | 23:33 |  |  |  | 0 | 0 | 0 | 15.1167 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-18 | 7:06 | 2014-12-18 | 22:00 |  |  |  | 0 | 0 | 0 | 14.9 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-23 | 12:26 | 2014-12-23 | 21:31 |  |  |  | 0 | 0 | 0 | 9.0833 |  |  |  | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.95
145 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2014-12-09 | 11:38 | 2014-12-12 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 82.6 | -- | -- | -- | H/T for voltage regulation |  | 100
[6 empty] | 2014-12-15 | 12:11 | 2014-12-18 | 21:47 |  |  |  | 0 | 0 | 0 | 81.6 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-19 | 6:58 | 2014-12-19 | 21:58 |  |  |  | 0 | 0 | 0 | 15 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-20 | 9:44 | 2015-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 278.2667 |  |  |  | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 82.6
147 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
150 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
152 | SR2R17 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2014-12-09 | 8:08 | 2014-12-12 | 21:56 | -- | -- | -- | 0 | 0 | 0 | 85.8 | -- | -- | -- | H/T for voltage regulation |  | 100
[6 empty] | 2014-12-15 | 9:36 | 2014-12-18 | 21:41 |  |  |  | 0 | 0 | 0 | 84.0833 |  |  |  | H/T for voltage regulation
[6 empty] | 2014-12-19 | 6:57 | 2015-01-01 | 0:00 |  |  |  | 0 | 0 | 0 | 305.05 |  |  |  | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 85.8
153 | SR2R18 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
154 | SR2R19 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
155 | SR2R20 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
156 | SR2R21 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
157 | SR2R22 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
158 | SR2R23 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2014-12-10 | 15:05 | 2014-12-10 | 15:59 | -- | -- | -- | 0.9 | 0 | 0 | 0 | -- | -- | -- | -- |  | 99.879
[6 empty] | Sub Total --> | [6 empty] | 0.9 | 0 | 0 | 0
159 | SR2R24 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
160 | SR2R25 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
161 | SR2R26 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | 2014-12-16 | 10:03 | 2014-12-16 | 10:21 | -- | -- | -- | 0.3 | 0 | 0 | 0 | -- | -- | -- | Blocked due to valve cooling fault at Kolar SS. |  | 99.9597
[6 empty] | Sub Total --> | [6 empty] | 0.3 | 0 | 0 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse
26