## SOP
Standard of Performance data for the month of FEB -2014
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2014-02-19 | 12:11 | 2014-02-19 | 15:18 | -- | -- | -- | 0 | 0 | 0 | 3.1167 | N/A | N/A | N/A | Shut down availed by M/s KSEB to attend hot spot in Bus coupler isolator at Edamon SS vide SRLDC code no. CR-02/489. | SRPC, SRPC/SE-I/PGTA/2014, Dtd. 27.03.2014 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.1167
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N/A | N/A | N/A | Shut down availed by M/s KSEB for monthly maintenance works at Edappon end vide SRLDC code no. CR-03/ 602. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2014-02-05 | 9:39 | 2014-02-05 | 17:01 | -- | -- | -- | 0 | 0 | 0 | 7.3667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting and maintenance works at Kundra SS vide SRLDC code no. CR-02/84. |  | 100
[5 empty] | -- | 2014-02-05 | 18:08 | 2014-02-06 | 16:42 | -- | -- | -- | 0 | 22.5667 | 0 | 0 | N/A | N/A | N/A | Line tripped due to flashover of B-Phase LA at 220KV Kundra SS.
[5 empty] | -- | 2014-02-17 | 7:42 | 2014-02-17 | 13:46 | -- | -- | -- | 0 | 0 | 0 | 6.0667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacement of LA at Kundra end vide SRLDC code no. CR-02/420.
[6 empty] | Sub Total --> | [6 empty] | 0 | 22.5667 | 0 | 13.4333
4 | SR2L4 | KAYAMKULAM - POLLAM - I | 47 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
5 | SR2L5 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2014-02-10 | 9:27 | 2014-02-10 | 17:17 | -- | -- | -- | 0 | 0 | 0 | 7.8333 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra end vide CPCC code no. CP-02/ 356. |  | 100
[5 empty] | -- | 2014-02-11 | 8:07 | 2014-02-11 | 16:01 | -- | -- | -- | 0 | 0 | 0 | 7.9 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra SS vide CPCC code no. CP-02/402.
[5 empty] | -- | 2014-02-12 | 9:23 | 2014-02-12 | 16:24 | -- | -- | -- | 0 | 0 | 0 | 7.0167 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra SS vide SRLDC code no. CR-02/283.
[5 empty] | -- | 2014-02-14 | 8:38 | 2014-02-14 | 17:51 | -- | -- | -- | 0 | 0 | 0 | 9.2167 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacement of LA at Kundra SS vide SRLDC code no. CR-02/337.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 31.9667
7 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
8 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | 2014-02-17 | 11:57 | 2014-02-17 | 12:01 | -- | -- | -- | 0.066667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped while charging of main CB after maitenance works due to maloperation of tie CB. |  | 99.9901
[6 empty] | Sub Total --> | [6 empty] | 0.066667 | 0 | 0 | 0 | -- | -- | --
9 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
11 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
14 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
15 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
16 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
17 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
18 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | 2014-02-15 | 7:09 | 2014-02-15 | 17:09 | -- | -- | -- | 0 | 0 | 0 | 10 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for construction works of 400KV Krishnapatnam - Chittoor line vide SRLDC code no. CR-02/372. |  | 100
[5 empty] | -- | 2014-02-21 | 10:26 | 2014-02-21 | 10:50 | -- | -- | -- | 0 | 0.4 | 0 | 0 | N/A | N/A | N/A | Line tripped at Chittoor (APTRANSCO SS) end only.
[5 empty] | -- | 2014-02-21 | 17:30 | 2014-02-21 | 17:40 | -- | -- | -- | 0 | 0.16667 | 0 | 0 | N/A | N/A | N/A | Line tripped at Chittoor (APTRANSCO SS) end only.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.56667 | 0 | 10 | -- | -- | --
19 | SR2L23 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | 2014-02-11 | 11:29 | 2014-02-11 | 11:43 | -- | -- | -- | 0 | 0.23333 | 0 | 0 | N/A | N/A | N/A | Tripped at Chittoor end only due to suspected PLCC mal operation at Chittoor SS. |  | 100
[5 empty] | -- | 2014-02-15 | 7:55 | 2014-02-15 | 17:31 | -- | -- | -- | 0 | 0 | 0 | 9.6 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for construction works of 400KV Krishnapatnam - Chittoor line vide SRLDC code no. CR-02/373.
[5 empty] | -- | 2014-02-26 | 6:26 | 2014-02-26 | 18:28 | -- | -- | -- | 0 | 0 | 0 | 12.0333 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for stringing works of 400 kV Krishnapatnam - Chittoor line vide SRLDC code no. CR-02/ 685.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.23333 | 0 | 21.6333 | -- | -- | --
20 | SR2L24 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
21 | SR2L25 | GOOTY - BANGALORE | 301.667 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
22 | SR2L26 | HASSAN - MYSORE I | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
23 | SR2L27 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
24 | SR2L28 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L29 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2014-02-09 | 5:22 | 2014-02-11 | 19:50 | -- | -- | -- | 0 | 62.4667 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N (Ph-earth) transient fault. FLR: 134 kM from Hassan end. Fault occured in KPTCL portion of the line. |  | 100
[5 empty] | -- | 2014-02-09 | 5:19 | 2014-02-09 | 5:19 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 163 kM from Hassan end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 62.4667 | 0 | 0
26 | SR2L30 | HOSUR-SALEM II | 125.325 | SR-II | -- | 2014-02-09 | 12:29 | 2014-02-09 | 13:27 | -- | -- | -- | 0.96667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to suspected PLCC maloperation at Hosur end. |  | 99.8562
[5 empty] | -- | 2014-02-18 | 8:54 | 2014-02-18 | 9:06 | -- | -- | -- | 0 | 0 | 0 | 0.2 | N/A | N/A | N/A | Hand tripped for taking out Line reactor at Salem end for voltage regulation as per SRLDC instructions vide code no. CR-02/456.
[6 empty] | Sub Total --> | [6 empty] | 0.96667 | 0 | 0 | 0.2
27 | SR2L31 | HOSUR-SALEM | 126.339 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L32 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L33 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
30 | SR2L34 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
31 | SR2L35 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2014-02-27 | 2:55 | 2014-02-27 | 3:49 | -- | -- | -- | 0 | 0.9 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of direct trip signal at Kaiga (NPCIL SS) end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.9 | 0 | 0
32 | SR2L36 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L37 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
34 | SR2L37A | KOLAR - CHENNAI | 219 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
35 | SR2L38 | KOLAR - HOODY - I | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
36 | SR2L39 | KOLAR - HOODY - II | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L40 | KOLAR - HOSUR - I | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L41 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L43 | MADURAI - TUTICORIN 1 | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L44 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L45 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L46 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2014-02-04 | 6:59 | 2014-02-08 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 107.25 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for cleaning of outdoor equipments at Kudamkulam end vide SRLDC code no. CR-02/51. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 107.25
43 | SR2L47 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2014-02-03 | 8:40 | 2014-02-03 | 19:49 | -- | -- | -- | 0 | 0 | 0 | 11.15 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/36. |  | 100
[5 empty] | -- | 2014-02-04 | 8:15 | 2014-02-04 | 20:01 | -- | -- | -- | 0 | 0 | 0 | 11.7667 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/53.
[5 empty] | -- | 2014-02-05 | 8:25 | 2014-02-05 | 20:22 | -- | -- | -- | 0 | 0 | 0 | 11.95 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/82.
[5 empty] | -- | 2014-02-06 | 8:23 | 2014-02-06 | 19:54 | -- | -- | -- | 0 | 0 | 0 | 11.5167 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/107.
[5 empty] | -- | 2014-02-07 | 8:27 | 2014-02-07 | 19:31 | -- | -- | -- | 0 | 0 | 0 | 11.0667 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/148.
[5 empty] | -- | 2014-02-08 | 8:11 | 2014-02-08 | 18:44 | -- | -- | -- | 0 | 0 | 0 | 10.55 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/177.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 68
44 | SR2L48 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2014-02-01 | 8:07 | 2014-02-01 | 19:46 | -- | -- | -- | 0 | 0 | 0 | 11.65 | -- | -- | -- | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/03. |  | 100
[5 empty] | -- | 2014-02-02 | 8:24 | 2014-02-02 | 19:59 |  |  |  | 0 | 0 | 0 | 11.5833 |  |  |  | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/20.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.2333
45 | SR2L49 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L50 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L51 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | 2014-02-16 | 15:59 | 2014-02-16 | 16:43 | -- | -- | -- | 0 | 0 | 0.73333 | 0 | N/A | N/A | N/A | Shut down availed for removing foreign object (Aluminium foil) hanging on B-Ph insulator from yoke plate at loc. No. 360 vide SRLDC code no. CR-02/399. |  | 100
[5 empty] | -- | 2014-02-16 | 14:02 | 2014-02-16 | 14:02 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault due to foreign object hanging on B-Ph insulatorat loc. No. 360.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.73333 | 0
48 | SR2L52 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | 2014-02-16 | 14:02 | 2014-02-16 | 14:28 | -- | -- | -- | 0 | 0 | 0.43333 | 0 | N/A | N/A | N/A | Tripped on operation of over voltage protection at Mysore end during auto reclosure of Line-I due to foreign object hanging on B-Ph insulator at loc. No. 360. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.43333 | 0
49 | SR2L53 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SRL53 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L54 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
52 | SR2L55 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2014-02-20 | 8:28 | 2014-02-20 | 16:18 | -- | -- | -- | 0 | 0 | 0 | 7.8333 | N/A | N/A | N/A | Shut down availed by M/s NLC for general maintenance works at Neyveli TS-II end vide SRLDC code no. CR-02/503. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.8333
53 | SR2L56 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | 2014-02-06 | 9:45 | 2014-02-09 | 23:08 | -- | -- | -- | 0 | 0 | 0 | 85.3833 | N/A | N/A | N/A | Shut down availed for providing inline tower DD+3 at loc No: 89 in place of DA+3 as a part of LILO scheme vide SRLDC code no. CR-02/115. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 85.3833
54 | SR2L57 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L58 | NEYVELI TS-I EXTENSION - TRICHY | 171.95 | SR-II | -- | 2014-02-03 | 8:10 | 2014-02-03 | 20:18 | -- | -- | -- | 0 | 0 | 0 | 12.1333 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/35. |  | 100
[5 empty] | -- | 2014-02-04 | 8:21 | 2014-02-04 | 18:59 | -- | -- | -- | 0 | 0 | 0 | 10.6333 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/54.
[5 empty] | -- | 2014-02-05 | 8:26 | 2014-02-05 | 19:58 | -- | -- | -- | 0 | 0 | 0 | 11.5333 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/83.
[5 empty] | -- | 2014-02-06 | 9:40 | 2014-02-09 | 22:50 | -- | -- | -- | 0 | 0 | 0 | 85.1667 | N/A | N/A | N/A | Shut down availed for providing inline tower DD+3 at loc No: 89 in place of DA+3 as a part of LILO scheme vide SRLDC code no. CR-02/114.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 119.4667
56 | SR2L59 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
57 | SR2L60 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
58 | SR2L61 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L62 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L63 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L64 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | 2014-02-16 | 6:02 | 2014-02-16 | 18:53 | -- | -- | -- | 0 | 0 | 0 | 12.85 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 172 to 271 vide SRLDC code no. CR-02/391. |  | 100
[5 empty] | -- | 2014-02-23 | 7:11 | 2014-02-23 | 18:58 | -- | -- | -- | 0 | 0 | 0 | 11.7833 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 172 to 271 vide SRLDC code no. CR-02/625.
[5 empty] | -- | 2014-02-24 | 7:11 | 2014-02-24 | 11:30 | -- | -- | -- | 0 | 0 | 0 | 4.3167 | N/A | N/A | N/A | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 172 to 271 vide SRLDC code no. CR-02/646.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 28.95
62 | SR2L65 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L66 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L67 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L68 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L70 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L71 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | 2014-02-11 | 8:27 | 2014-02-11 | 14:04 | -- | -- | -- | 0 | 0 | 0 | 5.6167 | N/A | N/A | N/A | Shut down availed by M/s KSEB for maintenance works at Edamon end vide SRLDC code no. CR-02/260. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.6167
68 | SR2L72 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2014-02-18 | 8:17 | 2014-02-18 | 16:25 | -- | -- | -- | 0 | 0 | 0 | 8.1333 | N/A | N/A | N/A | Shut down availed by M/s KSEB for maintenance of equipments at Edamon SS vide SRLDC code no. CR-02 /455. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.1333
69 | SR2L73 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2014-02-04 | 6:59 | 2014-02-08 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 107.25 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for cleaning of outdoor equipments at Kudamkulam end vide SRLDC code no. CR-02/51. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 107.25
70 | SR2L74 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L75 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2014-02-15 | 10:24 | 2014-02-15 | 17:44 | -- | -- | -- | 0 | 0 | 0 | 7.3333 | N/A | N/A | N/A | Shut down availed by M/s KKNPP for cleaning of wavetrap and CVT at Kudankulam end vide SRLDC code no. CR-02/375. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.3333
72 | SR2L76 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L77 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | 2014-02-06 | 6:31 | 2014-02-06 | 12:50 | -- | -- | -- | 0 | 0 | 6.3167 | 0 | N/A | N/A | N/A | Tripped on R-B fault due to heavy foggy weather condition. |  | 100
[5 empty] | -- | 2014-02-06 | 5:57 | 2014-02-06 | 6:18 |  |  |  | 0 | 0 | 0.35 | 0 | N/A | N/A | N/A | Tripped on R-Y fault due to heavy foggy weather condition.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 6.6667 | 0
74 | SR2L78 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | 2014-02-06 | 6:21 | 2014-02-06 | 6:21 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 106.1 kM from Thirunelveli end. |  | 99.9875
[5 empty] | -- | 2014-02-06 | 5:57 | 2014-02-06 | 5:57 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 44.4 kM from Thirunelveli end.
[5 empty] | -- | 2014-02-06 | 6:12 | 2014-02-06 | 6:12 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 91.9 kM from Thirunelveli end.
[5 empty] | -- | 2014-02-06 | 6:31 | 2014-02-06 | 6:31 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 55.1 kM from Thirunelveli end.
[5 empty] | -- | 2014-02-06 | 6:37 | 2014-02-06 | 12:58 | -- | -- | -- | 0 | 0 | 6.35 | 0 | N/A | N/A | N/A | Tripped on 3-phase fault due to heavy foggy weather condition.
[5 empty] | -- | 2014-02-06 | 6:04 | 2014-02-06 | 6:04 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 93.6 kM from Thirunelveli end.
[5 empty] | -- | 2014-02-20 | 9:56 | 2014-02-20 | 10:01 | -- | -- | -- | 0.083333 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Thurinelveli end only on receipt of direct trip signal while carrying out of NTAMC wiring works at Trivendrum end by M/s Areva.
[6 empty] | Sub Total --> | [6 empty] | 0.083333 | 0 | 6.35 | 0
75 | SR2L79 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L80 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L83 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L84 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | 2014-02-25 | 9:06 | 2014-02-25 | 14:20 | -- | -- | -- | 0 | 0 | 0 | 5.2333 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Kochi end as per SRPC recommendation vide SRLDC code no CR-02/669. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.2333
79 | SR2L85 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L86 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L87 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR2L88 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L89 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR2L90 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
85 | SR2L91 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | 2014-02-02 | 9:14 | 2014-02-02 | 9:42 | -- | -- | -- | 0.46667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-02/21. |  | 99.9306
[6 empty] | Sub Total --> | [6 empty] | 0.46667 | 0 | 0 | 0
89 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2014-02-02 | 9:59 | 2014-02-02 | 18:12 | -- | -- | -- | 0 | 0 | 0 | 8.2167 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for providing jumper to newly formed rigid bus at Somanahalli 220 kV SS vide SRLDC code no. CR-02/23. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.2167
90 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
104 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | 2014-02-14 | 10:44 | 2014-02-14 | 17:25 | -- | -- | -- | 6.6833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-02/347. |  | 99.0055
[6 empty] | Sub Total --> | [6 empty] | 6.6833 | 0 | 0 | 0
105 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | 2014-02-11 | 10:24 | 2014-02-11 | 10:35 | -- | -- | -- | 0.18333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-02/262. |  | 99.9405
[5 empty] | -- | 2014-02-17 | 14:26 | 2014-02-17 | 14:39 | -- | -- | -- | 0.21667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-02/436.
[6 empty] | Sub Total --> | [6 empty] | 0.4 | 0 | 0 | 0
106 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [11 empty] | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | 2014-02-09 | 9:09 | 2014-02-09 | 14:00 | -- | -- | -- | 4.85 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-02/213. |  | 99.2783
[6 empty] | Sub Total --> | [6 empty] | 4.85 | 0 | 0 | 0
109 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | 2014-02-26 | 16:05 | 2014-02-26 | 16:12 | -- | -- | -- | 0.11667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to suspected DC earth fault. |  | 99.9826
[6 empty] | Sub Total --> | [6 empty] | 0.11667 | 0 | 0 | 0
119 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T36 | TRICHY ICT - I | 315 | SR-II | -- | 2014-02-19 | 15:40 | 2014-02-19 | 15:50 | -- | -- | -- | 0.16667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped during carrying out of NTAMC wiring works by M/s Areva. |  | 99.9752
[6 empty] | Sub Total --> | [6 empty] | 0.16667 | 0 | 0 | 0
121 | SR2T37 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T38 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T39 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T40 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T41 | UDUMALPET ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T42 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T43 | UDUMALPET ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
129 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-02-16 | 17:11 | -- | -- | -- | 0 | 0 | 0 | 377.1833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-17 | 8:19 | 2014-03-01 | 0:00 |  |  |  | 0 | 0 | 0 | 279.6833
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 656.8666
130 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2014-02-08 | 8:19 | 2014-02-08 | 21:58 | -- | -- | -- | 0 | 0 | 0 | 13.65 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-10 | 7:12 | 2014-02-10 | 18:22 | -- | -- | -- | 0 | 0 | 0 | 11.1667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-11 | 7:15 | 2014-02-16 | 17:14 |  |  |  | 0 | 0 | 0 | 129.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-18 | 8:11 | 2014-02-18 | 23:07 |  |  |  | 0 | 0 | 0 | 14.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-19 | 7:19 | 2014-02-23 | 21:42 |  |  |  | 0 | 0 | 0 | 110.3833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-25 | 9:47 | 2014-02-27 | 22:12 |  |  |  | 0 | 0 | 0 | 60.4167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-28 | 9:42 | 2014-03-01 | 0:00 |  |  |  | 0 | 0 | 0 | 14.3 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 354.8333
131 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | 2014-02-08 | 8:14 | 2014-02-08 | 22:52 | -- | -- | -- | 0 | 0 | 0 | 14.6333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-10 | 15:19 | 2014-02-16 | 17:19 | -- | -- | -- | 0 | 0 | 0 | 146 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-18 | 8:26 | 2014-02-23 | 21:36 | -- | -- | -- | 0 | 0 | 0 | 133.1667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-25 | 9:48 | 2014-02-27 | 22:03 | -- | -- | -- | 0 | 0 | 0 | 60.25 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-28 | 9:30 | 2014-03-01 | 0:00 |  |  |  | 0 | 0 | 0 | 14.5 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 368.55
132 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
133 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | 2014-02-08 | 8:27 | 2014-02-12 | 22:24 | -- | -- | -- | 0 | 0 | 0 | 109.95 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-17 | 19:39 | 2014-02-18 | 23:11 | -- | -- | -- | 0 | 0 | 0 | 27.5333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-24 | 15:19 | 2014-02-27 | 22:18 | -- | -- | -- | 0 | 0 | 0 | 78.9833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 216.4667
134 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
135 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2014-02-01 | 9:38 | 2014-02-01 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 12.4333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-04 | 10:02 | 2014-02-05 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 35.6333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-06 | 10:35 | 2014-02-12 | 15:04 | -- | -- | -- | 0 | 0 | 0 | 148.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-12 | 15:35 | 2014-02-16 | 17:20 | -- | -- | -- | 0 | 0 | 0 | 97.75 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-17 | 8:16 | 2014-02-17 | 16:10 | -- | -- | -- | 0 | 0 | 0 | 7.9 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-18 | 8:06 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 255.9 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 558.1
136 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2014-02-01 | 9:44 | 2014-02-01 | 22:06 | -- | -- | -- | 0 | 0 | 0 | 12.3667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-04 | 10:03 | 2014-02-05 | 21:42 | -- | -- | -- | 0 | 0 | 0 | 35.65 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-08 | 8:13 | 2014-02-18 | 23:01 | -- | -- | -- | 0 | 0 | 0 | 254.8 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-19 | 7:17 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 232.7167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 535.5333
137 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
139 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
140 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | 2014-02-14 | 10:02 | 2014-02-16 | 17:30 | -- | -- | -- | 0 | 0 | 0 | 55.4667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 55.4667
141 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2014-02-10 | 15:22 | 2014-02-10 | 20:59 | -- | -- | -- | 0 | 0 | 0 | 5.6167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-14 | 15:34 | 2014-02-14 | 20:08 | -- | -- | -- | 0 | 0 | 0 | 4.5667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-15 | 12:09 | 2014-02-15 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 9.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-20 | 15:45 | 2014-02-20 | 22:08 | -- | -- | -- | 0 | 0 | 0 | 6.3833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 26.0833
142 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2014-02-10 | 15:26 | 2014-02-10 | 21:03 | -- | -- | -- | 0 | 0 | 0 | 5.6167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-14 | 15:31 | 2014-02-14 | 20:14 | -- | -- | -- | 0 | 0 | 0 | 4.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-15 | 12:11 | 2014-02-15 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 9.55 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-20 | 15:52 | 2014-02-20 | 22:13 | -- | -- | -- | 0 | 0 | 0 | 6.35 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 26.2333
143 | SR2R17 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
144 | SR2R18 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
145 | SR2R19 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2R20 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
147 | SR2R21 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2014-02-01 | 0:00 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
148 | SR2R22 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2014-02-05 | 14:25 | 2014-02-06 | 21:31 | -- | -- | -- | 0 | 0 | 0 | 31.1 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-07 | 10:13 | 2014-02-07 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 11.45 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-08 | 8:11 | 2014-02-08 | 21:51 | -- | -- | -- | 0 | 0 | 0 | 13.6667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-10 | 15:19 | 2014-02-10 | 20:50 | -- | -- | -- | 0 | 0 | 0 | 5.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-13 | 15:51 | 2014-02-13 | 20:32 | -- | -- | -- | 0 | 0 | 0 | 4.6833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-14 | 9:54 | 2014-02-14 | 21:22 | -- | -- | -- | 0 | 0 | 0 | 11.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-15 | 12:11 | 2014-02-16 | 13:37 | -- | -- | -- | 0 | 0 | 0 | 25.4333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-20 | 15:54 | 2014-02-21 | 21:46 | -- | -- | -- | 0 | 0 | 0 | 29.8667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-24 | 15:14 | 2014-02-24 | 23:16 | -- | -- | -- | 0 | 0 | 0 | 8.0333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 141.2167
149 | SR2R23 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2014-02-05 | 14:25 | 2014-02-06 | 21:33 | -- | -- | -- | 0 | 0 | 0 | 31.1333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-02-07 | 10:13 | 2014-02-07 | 21:41 | -- | -- | -- | 0 | 0 | 0 | 11.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-08 | 8:12 | 2014-02-08 | 21:51 | -- | -- | -- | 0 | 0 | 0 | 13.65 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-10 | 15:19 | 2014-02-10 | 20:51 | -- | -- | -- | 0 | 0 | 0 | 5.5333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-13 | 15:52 | 2014-02-13 | 20:34 | -- | -- | -- | 0 | 0 | 0 | 4.7 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-14 | 9:54 | 2014-02-14 | 21:23 | -- | -- | -- | 0 | 0 | 0 | 11.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-15 | 12:12 | 2014-02-16 | 13:38 | -- | -- | -- | 0 | 0 | 0 | 25.4333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-20 | 15:55 | 2014-02-21 | 21:46 | -- | -- | -- | 0 | 0 | 0 | 29.85 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-02-24 | 15:15 | 2014-02-24 | 23:16 | -- | -- | -- | 0 | 0 | 0 | 8.0167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 141.2667
150 | SR2R24 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | 2014-02-23 | 19:21 | 2014-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 124.65 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 124.65
151 | SR2R25 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
152 | SR2R26 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
[22 empty] | 15197.9463 | 15197.9463 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse