## SOP
Standard of Performance data for the month of March -2014
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2014-03-19 | 8:13 | 2014-03-19 | 13:07 | -- | -- | -- | 0 | 0 | 0 | 4.9 | N/A | N/A | N/A | Shut down availed by M/s KSEB for tightining clamps and connectors in KSEB portion at Edamon end vide SRLDC code no CR- 03/392. | SRPC, SRPC/SE-I/PGTA/2014, Dtd. 30.04.14 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.9
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2014-03-28 | 9:27 | 2014-03-28 | 18:02 | -- | -- | -- | 0 | 0 | 0 | 8.5833 | N/A | N/A | N/A | Shut down availed by M/s KSEB for monthly maintenance works at Edappon end vide SRLDC code no. CR-03/ 602. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.5833
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2014-03-01 | 12:49 | 2014-03-01 | 17:53 | -- | -- | -- | 0 | 0 | 0 | 5.0667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra end vide SRLDC code no. CR-03/07. |  | 100
[5 empty] | -- | 2014-03-03 | 9:06 | 2014-03-03 | 18:22 | -- | -- | -- | 0 | 0 | 0 | 9.2667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra SS vide SRLDC code no. CR-03/30.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 14.3333
4 | SR2L4 | KAYAMKULAM - POLLAM - I | 47 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
5 | SR2L5 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2014-03-07 | 9:07 | 2014-03-07 | 16:53 | -- | -- | -- | 0 | 0 | 0 | 7.7667 | N/A | N/A | N/A | Shut down availed by M/s NTPC for attending hot spot in wavetrap at Kayamkulam end vide SRLDC code no. CR-03/112. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.7667
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2014-03-04 | 9:04 | 2014-03-04 | 18:45 | -- | -- | -- | 0 | 0 | 0 | 9.6833 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra SS vide SRLDC code no. CR-03/48. |  | 100
[5 empty] | -- | 2014-03-05 | 8:32 | 2014-03-05 | 18:02 | -- | -- | -- | 0 | 0 | 0 | 9.5 | N/A | N/A | N/A | Shut down availed by M/s KSEB for painting works at Kundra end vide SRLDC code no. CR-03/74.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 19.1833
7 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | 2014-03-17 | 9:43 | 2014-03-17 | 21:04 | -- | -- | -- | 0 | 0 | 0 | 11.35 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/355. |  | 100
[5 empty] | -- | 2014-03-18 | 8:00 | 2014-03-18 | 18:43 | -- | -- | -- | 0 | 0 | 0 | 10.7167 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/374.
[5 empty] | -- | 2014-03-19 | 8:19 | 2014-03-19 | 18:43 | -- | -- | -- | 0 | 0 | 0 | 10.4 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/393.
[5 empty] | -- | 2014-03-20 | 8:14 | 2014-03-20 | 16:45 | -- | -- | -- | 0 | 0 | 0 | 8.5167 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/421.
[5 empty] | -- | 2014-03-21 | 8:00 | 2014-03-21 | 14:44 | -- | -- | -- | 0 | 0 | 0 | 6.7333 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/441.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 47.7167
8 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | 2014-03-22 | 8:01 | 2014-03-22 | 15:06 | -- | -- | -- | 0 | 0 | 0 | 7.0833 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/466. |  | 100
[5 empty] | -- | 2014-03-23 | 8:01 | 2014-03-23 | 14:10 | -- | -- | -- | 0 | 0 | 0 | 6.15 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/489.
[5 empty] | -- | 2014-03-24 | 7:55 | 2014-03-24 | 15:34 | -- | -- | -- | 0 | 0 | 0 | 7.65 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/507.
[5 empty] | -- | 2014-03-25 | 7:55 | 2014-03-25 | 14:08 | -- | -- | -- | 0 | 0 | 0 | 6.2167 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/531.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.1 | -- | -- | --
9 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
11 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
14 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
15 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
16 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
17 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
18 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | 2014-03-20 | 18:20 | 2014-03-20 | 18:50 | -- | -- | -- | 0 | 0.5 | 0 | 0 | N/A | N/A | N/A | Tripped at Chittoor (APTRANSCO SS) end only due to receipt of direct trip signal due to PLCC mal-operation at Chittoor end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.5 | 0 | 0 | -- | -- | --
19 | SR2L23 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
20 | SR2L24 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
21 | SR2L25 | GOOTY - BANGALORE | 301.667 | SR-II | -- | 2014-03-26 | 11:14 | 2014-03-26 | 11:49 | -- | -- | -- | 0 | 0 | 0 | 0.58333 | N/A | N/A | N/A | Hand tripped for taking out Line reactor at Bangalore end for voltage regulation as per SRLDC instructions vide code no. CR-03/565. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.58333 | -- | -- | --
22 | SR2L26 | HASSAN - MYSORE I | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
23 | SR2L27 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
24 | SR2L28 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L29 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L30 | HOSUR-SALEM II | 125.325 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L31 | HOSUR-SALEM | 126.339 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L32 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2014-03-28 | 15:52 | 2014-03-28 | 18:24 | -- | -- | -- | 0 | 0 | 0 | 2.5333 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for attending isolator allignment problem at Kaiga end vide SRLDC code no. CR-03/620. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.5333 | N/A | N/A | N/A
29 | SR2L33 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | 2014-03-29 | 13:48 | 2014-03-29 | 14:04 | -- | -- | -- | 0.26667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N (Ph-earth) transient fault. FLR: 89.4 kM from Narendra end. |  | 99.9641
[5 empty] | -- | 2014-03-29 | 14:04 | 2014-03-29 | 14:27 | -- | -- | -- | 0 | 0.38333 | 0 | 0 | N/A | N/A | N/A | Charging delayed by M/s NPCIL.
[6 empty] | Sub Total --> | [6 empty] | 0.26667 | 0.38333 | 0 | 0
30 | SR2L34 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
31 | SR2L35 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2014-03-16 | 17:30 | 2014-03-17 | 17:33 | -- | -- | -- | 0 | 24.05 | 0 | 0 | N/A | N/A | N/A | Tripped due to Y-Phase LA flashover at Kaiga (NPCIL SS) end. |  | 100
[5 empty] | -- | 2014-03-17 | 17:33 | 2014-03-19 | 14:30 | -- | -- | -- | 0 | 44.95 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR: 93.73 kM from Kaiga end. Fault occured in KPTCL portion of the line.
[5 empty] | -- | 2014-03-19 | 14:38 | 2014-03-19 | 21:56 | -- | -- | -- | 0 | 7.3 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault due to decapping of B- phase insulator at loc no 207 (KPTCL portion).
[6 empty] | Sub Total --> | [6 empty] | 0 | 76.3 | 0 | 0
32 | SR2L36 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L37 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
34 | SR2L37A | KOLAR - CHENNAI | 219 | SR-II | -- | 2014-03-25 | 7:38 | 2014-03-25 | 21:49 | -- | -- | -- | 0 | 0 | 0 | 14.1833 | N/A | N/A | N/A | Shut down availed for LILO works at Thiruvelam SS and line crossing of Nellore-Thiruvelam line vide SRLDC code no. CR-03/530. |  | 100
[5 empty] | -- | 2014-03-30 | 12:28 | 2014-03-31 | 0:53 | -- | -- | -- | 0 | 0 | 0 | 12.4167 | N/A | N/A | N/A | Shut down availed for LILO works at Thiruvelam SS vide SRLDC code no. CR-03/664.
[5 empty] | -- | 2014-03-31 | 9:27 | 2014-03-31 | 16:28 | -- | -- | -- | 0 | 0 | 0 | 7.0167 | N/A | N/A | N/A | Shut down availed for LILO works at Thiruvelam SS vide SRLDC code no. CR-03/683.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33.6167
35 | SR2L38 | KOLAR - HOODY - I | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
36 | SR2L39 | KOLAR - HOODY - II | 51.067 | SR-II | -- | 2014-03-12 | 10:11 | 2014-03-12 | 16:32 | -- | -- | -- | 6.35 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for line isolator & earthswitch allignment works at Hoody end vide SRLDC code no. CR-03/ 231. |  | 99.1465
[6 empty] | Sub Total --> | [6 empty] | 6.35 | 0 | 0 | 0
37 | SR2L40 | KOLAR - HOSUR - I | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L41 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L43 | MADURAI - TUTICORIN 1 | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L44 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L45 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L46 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2014-03-22 | 17:05 | 2014-03-23 | 0:15 | -- | -- | -- | 0 | 7.1667 | 0 | 0 | N/A | N/A | N/A | Tripped at Kudamkulam (NPCIL SS) end only due to CB problem. |  | 100
[5 empty] | -- | 2014-03-22 | 0:51 | 2014-03-22 | 2:59 | -- | -- | -- | 0 | 2.1333 | 0 | 0 | N/A | N/A | N/A | Tripped at Kudamkulam (NPCIL SS) end only.
[5 empty] | -- | 2014-03-23 | 0:15 | 2014-03-26 | 1:59 | -- | -- | -- | 0 | 0 | 0 | 73.7333 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for rectification of ground fault in control circuit of CBs at Kudamkulam end SRLDC code no. CR-03/488.
[6 empty] | Sub Total --> | [6 empty] | 0 | 9.3 | 0 | 73.7333
43 | SR2L47 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L48 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L49 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L50 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L51 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L52 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR2L53 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | 2014-03-21 | 10:52 | 2014-03-21 | 17:27 | -- | -- | -- | 0 | 0 | 0 | 6.5833 | N/A | N/A | N/A | Shut down availed by M/s PED for implementation of auto reclosure scheme at Bahoor SS vide SRLDC code no. CR-03/445. |  | 100
[5 empty] | -- | 2014-03-22 | 11:33 | 2014-03-22 | 13:40 | -- | -- | -- | 0 | 0 | 2.1167 | 0 | N/A | N/A | N/A | Tripped on R-N fault due to fire created by villagers under the line at loc. H3.
[5 empty] | -- | 2014-03-22 | 9:17 | 2014-03-22 | 10:45 | -- | -- | -- | 0 | 0 | 1.4667 | 0 | N/A | N/A | N/A | Tripped on R-N fault due to fire created by villagers under the line at loc. H3.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 3.5833 | 6.5833
50 | SRL53 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | 2014-03-01 | 8:24 | 2014-03-01 | 16:10 | -- | -- | -- | 0 | 0 | 0 | 7.7667 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli end vide SRLDC code no. CR-03/01. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.7667
51 | SR2L54 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | 2014-03-17 | 8:41 | 2014-03-17 | 16:03 | -- | -- | -- | 0 | 0 | 0 | 7.3667 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli end vide SRLDC code no. CR-03/354. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.3667
52 | SR2L55 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L56 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | 2014-03-11 | 8:33 | 2014-03-11 | 16:20 | -- | -- | -- | 0 | 0 | 0 | 7.7833 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli end vide SRLDC code no. CR-03 /200. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.7833
54 | SR2L57 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L58 | NEYVELI TS-I EXTENSION - TRICHY | 171.95 | SR-II | -- | 2014-03-24 | 5:11 | 2014-03-24 | 7:30 | -- | -- | -- | 0 | 2.3167 | 0 | 0 | N/A | N/A | N/A | Charging delayed by M/s NLC. |  | 97.3187
[5 empty] | -- | 2014-03-24 | 4:20 | 2014-03-24 | 5:11 | -- | -- | -- | 0 | 0.85 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault due to heavy fog. Auto reclosure unsucessful as DT received from Neyveli TS-1 Expansion end.
[5 empty] | Jumper cut | 2014-03-30 | 17:57 | 2014-03-31 | 13:47 | -- | -- | -- | 19.8333 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault due to B-phase jumper cut at loc. 37.
[5 empty] | -- | 2014-03-31 | 13:47 | 2014-03-31 | 14:55 | -- | -- | -- | 0 | 1.1333 | 0 | 0 | N/A | N/A | N/A | Charging delayed by M/s NLC.
[6 empty] | Sub Total --> | [6 empty] | 19.8333 | 4.3 | 0 | 0
56 | SR2L59 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2014-03-24 | 15:56 | 2014-03-24 | 17:19 | -- | -- | -- | 0 | 1.3833 | 0 | 0 | N/A | N/A | N/A | Charging delayed by Neyveli TS-I Expansion due to isolator problem. |  | 100
[5 empty] | Insulator decapping | 2014-03-24 | 5:24 | 2014-03-24 | 15:56 | -- | 1 | -- | 0 | 0 | 10.5333 | 0 | N/A | N/A | N/A | Tripped on Y-N fault due to decapping of Y-phase insulator at loc.505 due to heavy fog.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.3833 | 10.5333 | 0
57 | SR2L60 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2014-03-13 | 7:10 | 2014-03-13 | 19:14 | -- | -- | -- | 0 | 0 | 0 | 12.0667 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/252. |  | 100
[5 empty] | -- | 2014-03-14 | 7:04 | 2014-03-14 | 17:28 | -- | -- | -- | 0 | 0 | 0 | 10.4 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/281.
[5 empty] | -- | 2014-03-15 | 7:11 | 2014-03-15 | 17:35 | -- | -- | -- | 0 | 0 | 0 | 10.4 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/312.
[5 empty] | -- | 2014-03-16 | 7:09 | 2014-03-16 | 17:35 | -- | -- | -- | 0 | 0 | 0 | 10.4333 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/342.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 43.3
58 | SR2L61 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L62 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L63 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L64 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | 2014-03-29 | 8:41 | 2014-03-30 | 12:23 | -- | -- | -- | 0 | 0 | 0 | 27.7 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of Pugalur- Sholinganallur 400 kV D/C line vide SRLDC code no. CR-03/634. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.7
62 | SR2L65 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L66 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L67 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | 2014-03-04 | 15:21 | 2014-03-04 | 15:25 | -- | -- | -- | 0.066667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Udumalpet end only during NTAMC wiring works by M/s ALSTOM. |  | 99.991
[6 empty] | Sub Total --> | [6 empty] | 0.066667 | 0 | 0 | 0
65 | SR2L68 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L70 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | 2014-03-10 | 10:39 | 2014-03-10 | 14:47 | -- | -- | -- | 0 | 0 | 0 | 4.1333 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Sriperumbudur end as per SRPC recommendation vide SRLDC code no CR-03/170. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.1333
67 | SR2L71 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
68 | SR2L72 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L73 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2014-03-22 | 17:05 | 2014-03-23 | 0:15 | -- | -- | -- | 0 | 7.1667 | 0 | 0 | N/A | N/A | N/A | Tripped at Kudamkulam (NPCIL SS) end only due to CB problem. |  | 100
[5 empty] | -- | 2014-03-22 | 0:51 | 2014-03-22 | 2:59 | -- | -- | -- | 0 | 2.1333 | 0 | 0 | N/A | N/A | N/A | Tripped at Kudamkulam (NPCIL SS) end only.
[5 empty] | -- | 2014-03-23 | 0:15 | 2014-03-26 | 1:59 | -- | -- | -- | 0 | 0 | 0 | 73.7333 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for rectification of ground fault in control circuit of CBs at Kudamkulam end SRLDC code no. CR-03/488.
[6 empty] | Sub Total --> | [6 empty] | 0 | 9.3 | 0 | 73.7333
70 | SR2L74 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L75 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
72 | SR2L76 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L77 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L78 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR2L79 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L80 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L83 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L84 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L85 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L86 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L87 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | 2014-03-26 | 10:09 | 2014-03-26 | 14:44 | -- | -- | -- | 0 | 0 | 0 | 4.5833 | N/A | N/A | N/A | Shut down availed for configuring and testing of over voltage stage-I delay timing at Udumalpet end as per SRPC recommendation vide SRLDC code no CR-03/561. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.5833
82 | SR2L88 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L89 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | 2014-03-28 | 8:38 | 2014-03-28 | 17:55 | -- | -- | -- | 0 | 0 | 0 | 9.2833 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/601. |  | 100
[5 empty] | -- | 2014-03-29 | 7:15 | 2014-03-29 | 15:56 | -- | -- | -- | 0 | 0 | 0 | 8.6833 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/632.
[5 empty] | -- | 2014-03-30 | 7:05 | 2014-03-30 | 16:21 | -- | -- | -- | 0 | 0 | 0 | 9.2667 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-03/658.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.2333
84 | SR2L90 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
85 | SR2L91 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | 2014-03-19 | 23:42 | 2014-03-19 | 23:58 | -- | -- | -- | 0.26667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-03/413. |  | 99.9642
[6 empty] | Sub Total --> | [6 empty] | 0.26667 | 0 | 0 | 0
89 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2014-03-19 | 23:00 | 2014-03-19 | 23:34 | -- | -- | -- | 0.56667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-03/410. |  | 99.9238
[6 empty] | Sub Total --> | [6 empty] | 0.56667 | 0 | 0 | 0
90 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | 2014-03-23 | 9:26 | 2014-03-23 | 16:06 | -- | -- | -- | 6.6667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-03/490. |  | 99.1039
[6 empty] | Sub Total --> | [6 empty] | 6.6667 | 0 | 0 | 0
98 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | 2014-03-20 | 8:13 | 2014-03-22 | 10:40 | -- | -- | -- | 50.45 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of 245kV & 52kV bushings vide SRLDC code no CR-03/420. |  | 93.2191
[6 empty] | Sub Total --> | [6 empty] | 50.45 | 0 | 0 | 0
104 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [11 empty] | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T36 | TRICHY ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T37 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T38 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T39 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T40 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T41 | UDUMALPET ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T42 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2T43 | UDUMALPET ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
129 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
130 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
131 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2014-03-01 | 0:00 | 2014-03-01 | 21:52 | -- | -- | -- | 0 | 0 | 0 | 21.8667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-13 | 8:14 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 447.7667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 469.6333
132 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-03-01 | 21:45 | -- | -- | -- | 0 | 0 | 0 | 21.75 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-05 | 8:18 | 2014-03-07 | 22:17 | -- | -- | -- | 0 | 0 | 0 | 61.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-03-13 | 8:01 | 2014-03-26 | 21:57 | -- | -- | -- | 0 | 0 | 0 | 325.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-03-27 | 9:47 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 110.2167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 519.8833
133 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
134 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | 2014-03-14 | 10:20 | 2014-03-18 | 0:18 | -- | -- | -- | 0 | 0 | 0 | 85.9667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-18 | 9:39 | 2014-03-21 | 13:40 | -- | -- | -- | 0 | 0 | 0 | 76.0167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-03-24 | 8:45 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 183.25 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 345.2333
135 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
136 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-03-26 | 21:55 | -- | -- | -- | 0 | 0 | 0 | 621.9167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-27 | 8:20 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 111.6667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 733.5834
137 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2014-03-01 | 0:00 | 2014-03-01 | 21:45 | -- | -- | -- | 0 | 0 | 0 | 21.75 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-05 | 8:25 | 2014-03-07 | 22:24 | -- | -- | -- | 0 | 0 | 0 | 61.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-03-09 | 9:15 | 2014-03-10 | 22:49 | -- | -- | -- | 0 | 0 | 0 | 37.5667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-03-11 | 10:32 | 2014-03-18 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 157.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2014-03-18 | 9:34 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 326.4333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 605.2
138 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
139 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
140 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
141 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | 2014-03-07 | 11:02 | 2014-03-18 | 0:15 | -- | -- | -- | 0 | 0 | 0 | 253.2167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-27 | 8:24 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 111.6 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 364.8167
142 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2014-03-14 | 10:09 | 2014-03-14 | 23:06 | -- | -- | -- | 0 | 0 | 0 | 12.95 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-24 | 17:03 | 2014-03-26 | 20:51 | -- | -- | -- | 0 | 0 | 0 | 51.8 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 64.75
143 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2014-03-14 | 10:10 | 2014-03-14 | 23:10 | -- | -- | -- | 0 | 0 | 0 | 13 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-24 | 17:06 | 2014-03-26 | 20:55 | -- | -- | -- | 0 | 0 | 0 | 51.8167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 64.8167
144 | SR2R17 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
145 | SR2R18 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | 2014-03-26 | 9:13 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 134.7833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 134.7833
146 | SR2R19 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | 2014-03-26 | 9:12 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 134.8 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 134.8
147 | SR2R20 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-03-13 | 0:21 | -- | -- | -- | 0 | 0 | 0 | 288.35 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-13 | 7:59 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 448.0167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 736.3667
148 | SR2R21 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2014-03-01 | 0:00 | 2014-03-13 | 0:21 | -- | -- | -- | 0 | 0 | 0 | 288.35 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2014-03-13 | 7:59 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 448.0167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 736.3667
149 | SR2R22 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2014-03-26 | 10:26 | 2014-03-28 | 0:40 | -- | -- | -- | 0 | 0 | 0 | 38.2333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 38.2333
150 | SR2R23 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2014-03-26 | 10:27 | 2014-03-28 | 0:41 | -- | -- | -- | 0 | 0 | 0 | 38.2333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 38.2333
151 | SR2R24 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | 2014-03-01 | 0:00 | 2014-04-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
152 | SR2R25 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | 2014-03-25 | 15:47 | 2014-03-25 | 15:58 | -- | -- | -- | 0.18333 | 0 | 0 | 0 | N/A | N/A | N/A | Blocked due to fire detection system operated at Talcher end. Emergency switch-off signal received at kolar end. Pole II came on Metallic Return mode. |  | 99.9754
[6 empty] | Sub Total --> | [6 empty] | 0.18333 | 0 | 0 | 0
153 | SR2R26 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse