## SOP
Standard of Performance data for the month of NOV -2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2013-11-22 | 19:04 | 2013-11-22 | 19:29 | -- | -- | -- | 0 | 0.41667 | 0 | 0 | N/A | N/A | N/A | Charging delayed by M/s KSEB. | SRPC, SRPC/SE-I/PGTA/2014/1908, Dtd. 03.03.2014 | 99.9189
[5 empty] | -- | 2013-11-22 | 18:44 | 2013-11-22 | 19:04 | -- | -- | -- | 0.33333 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N (Ph-earth) transient fault. FLR : 24.7 KM from Edamon end.
[5 empty] | -- | 2013-11-25 | 10:31 | 2013-11-25 | 15:51 | -- | -- | -- | 0 | 0 | 0 | 5.3333 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacement of damaged R-Phase dropper of upper bus at Edamon end vide SRLDC code no. CR-11/757.
[5 empty] | -- | 2013-11-25 | 18:49 | 2013-11-25 | 19:04 | -- | -- | -- | 0.25 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N (Ph-earth) transient fault. FLR: 8.8 Km from Edamon end.
[5 empty] | -- | 2013-11-30 | 10:01 | 2013-11-30 | 17:31 | -- | -- | -- | 0 | 0 | 0 | 7.5 | N/A | N/A | N/A | Shut down availed by M/s KSEB for repairing auto reclose relay at Edamon end end vide SRLDC code no CR-11/904.
[6 empty] | Sub Total --> | [6 empty] | 0.58333 | 0.41667 | 0 | 12.8333
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2013-11-01 | 8:36 | 2013-11-01 | 17:52 | -- | -- | -- | 0 | 0 | 0 | 9.2667 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/06. |  | 100
[5 empty] | -- | 2013-11-03 | 9:09 | 2013-11-03 | 18:09 | -- | -- | -- | 0 | 0 | 0 | 9 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/41.
[5 empty] | -- | 2013-11-04 | 8:02 | 2013-11-04 | 18:05 | -- | -- | -- | 0 | 0 | 0 | 10.05 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/71.
[5 empty] | -- | 2013-11-06 | 9:13 | 2013-11-06 | 19:00 | -- | -- | -- | 0 | 0 | 0 | 9.7833 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/132.
[5 empty] | -- | 2013-11-08 | 7:06 | 2013-11-08 | 16:40 | -- | -- | -- | 0 | 0 | 0 | 9.5667 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/240.
[5 empty] | -- | 2013-11-09 | 7:26 | 2013-11-09 | 17:04 | -- | -- | -- | 0 | 0 | 0 | 9.6333 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/277.
[5 empty] | -- | 2013-11-11 | 7:14 | 2013-11-11 | 16:53 | -- | -- | -- | 0 | 0 | 0 | 9.65 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/339.
[5 empty] | -- | 2013-11-12 | 7:34 | 2013-11-12 | 17:05 | -- | -- | -- | 0 | 0 | 0 | 9.5167 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/385.
[5 empty] | -- | 2013-11-14 | 7:25 | 2013-11-14 | 16:39 | -- | -- | -- | 0 | 0 | 0 | 9.2333 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/448.
[5 empty] | -- | 2013-11-15 | 8:04 | 2013-11-15 | 17:13 | -- | -- | -- | 0 | 0 | 0 | 9.15 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/482.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 94.85
4 | SR2L4 | KAYAMKULAM - POLLAM - I | 47 | SR-II | -- | 2013-11-29 | 9:39 | 2013-11-29 | 15:27 | -- | -- | -- | 0 | 0 | 0 | 5.8 | N/A | N/A | N/A | Shut down availed by M/s NTPC for modification of M-2 relay at Kayamkulam end vide SRLDC code no CR-11/ 875. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.8
5 | SR2L5 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2013-11-02 | 16:00 | 2013-11-02 | 16:35 | -- | -- | -- | 0 | 0.58333 | 0 | 0 | N/A | N/A | N/A | Tripped at NTPC Kayamkulam end only on R-N (Ph-earth) transient fault. Tripping information delayed by NTPC Kayamkulam SS. |  | 99.6733
[6 empty] | 2013-11-02 | 16:35 | 2013-11-02 | 16:39 | -- | -- | -- | 0.066667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N (Ph-earth) transient fault. FLR: 21.7 KM from Kayamkulam end. Auto reclosure successful at Pallom end.
[6 empty] | 2013-11-07 | 10:45 | 2013-11-07 | 13:02 | -- | -- | -- | 2.2833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for TLM works vide SRLDC code no. CR-11/190.
[6 empty] | Sub Total --> | [6 empty] | 2.35 | 0.58333 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2013-11-01 | 8:33 | 2013-11-01 | 17:49 | -- | -- | -- | 0 | 0 | 0 | 9.2667 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/07. |  | 100
[5 empty] | -- | 2013-11-03 | 9:09 | 2013-11-03 | 18:03 | -- | -- | -- | 0 | 0 | 0 | 8.9 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/42.
[5 empty] | -- | 2013-11-04 | 8:03 | 2013-11-04 | 17:56 | -- | -- | -- | 0 | 0 | 0 | 9.8833 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/72.
[5 empty] | -- | 2013-11-06 | 9:10 | 2013-11-06 | 19:19 | -- | -- | -- | 0 | 0 | 0 | 10.15 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/133.
[5 empty] | -- | 2013-11-08 | 7:10 | 2013-11-08 | 16:36 | -- | -- | -- | 0 | 0 | 0 | 9.4333 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/241.
[5 empty] | -- | 2013-11-09 | 7:25 | 2013-11-09 | 17:02 | -- | -- | -- | 0 | 0 | 0 | 9.6167 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/278.
[5 empty] | -- | 2013-11-11 | 7:12 | 2013-11-11 | 16:47 | -- | -- | -- | 0 | 0 | 0 | 9.5833 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/340.
[5 empty] | -- | 2013-11-12 | 7:36 | 2013-11-12 | 17:03 | -- | -- | -- | 0 | 0 | 0 | 9.45 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/386.
[5 empty] | -- | 2013-11-14 | 7:24 | 2013-11-14 | 16:38 | -- | -- | -- | 0 | 0 | 0 | 9.2333 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/449.
[5 empty] | -- | 2013-11-15 | 8:05 | 2013-11-15 | 17:12 | -- | -- | -- | 0 | 0 | 0 | 9.1167 | N/A | N/A | N/A | Shut down availed for installation of OPGW in KSEB LILO portion under Microwave replacement project vide SRLDC code no. CR-11/483.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 94.6333
7 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
8 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
9 | SR2L10 | BANGALORE - SALEM | 79.756 | SR-II | -- | 2013-11-23 | 7:11 | 2013-11-23 | 19:32 | -- | -- | -- | 0 | 0 | 0 | 12.35 | N/A | N/A | N/A | Shut down availed for construction of 765 kV Madhugiri-Salem line vide SRLDC code no. CR-11/717. |  | 100
[5 empty] | -- | 2013-11-24 | 6:58 | 2013-11-24 | 18:28 | -- | -- | -- | 0 | 0 | 0 | 11.5 | N/A | N/A | N/A | Shut down availed for construction of 765 kV Madhugiri-Salem line vide SRLDC code no. CR-11/ 735.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.35
10 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
11 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
14 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | 2013-11-09 | 10:05 | 2013-11-09 | 18:11 | -- | -- | -- | 0 | 0 | 0 | 8.1 | N/A | N/A | N/A | Shut down availed by M/s TNEB for attending strand cut in 230 KV Eastern bus vide SRLDC code no. CR-11/282. |  | 100
[5 empty] | -- | 2013-11-18 | 12:48 | 2013-11-18 | 13:40 | -- | -- | -- | 0 | 0 | 0 | 0.86667 | N/A | N/A | N/A | Shut down availed by M/s TNEB to change existing power supply unit into modified version of power supply unit at Siruseri end vide SRLDC code no. CR-11/563.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.1 | -- | -- | --
15 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | 2013-11-09 | 10:05 | 2013-11-09 | 18:13 | -- | -- | -- | 0 | 0 | 0 | 8.1333 | N/A | N/A | N/A | Shut down availed by M/s TNEB for attending strand cut in 230 KV Eastern bus vide SRLDC code no. CR-11/283. |  | 100
[5 empty] | -- | 2013-11-18 | 13:50 | 2013-11-18 | 15:33 | -- | -- | -- | 0 | 0 | 0 | 1.7167 | N/A | N/A | N/A | Shut down availed by M/s TNEB to change existing power supply unit into modified version of power supply unit at Siruseri end vide SRLDC code no. CR-11/568.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.1333 | -- | -- | --
16 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
17 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
18 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | 2013-11-08 | 10:17 | 2013-11-08 | 14:20 | -- | -- | -- | 0 | 0 | 0 | 4.05 | N/A | N/A | N/A | Shut down availed by M/s APTRANSCO for relay testing works at Chittor end vide SRLDC code no. CR-11/246. |  | 100
[5 empty] | -- | 2013-11-14 | 6:55 | 2013-11-14 | 21:13 | -- | -- | -- | 0 | 0 | 0 | 14.3 | N/A | N/A | N/A | Shut down availed for construction works of 400 kV Nellore - Tiruvalam D/C line vide SRLDC code no. CR-11/447.
[5 empty] | -- | 2013-11-30 | 12:08 | 2013-11-30 | 12:27 | -- | -- | -- | 0 | 0 | 0 | 0.31667 | N/A | N/A | N/A | Hand tripped for taking out Line reactor at Sriperumbudur for voltage regulation as per SRLDC instructions vide code no. CR-11/908.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.05 | -- | -- | --
19 | SR2L23 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
20 | SR2L24 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
21 | SR2L25 | GOOTY - BANGALORE | 301.667 | SR-II | -- | 2013-11-05 | 2:39 | 2013-11-05 | 2:39 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 133 KM from Gooty end. |  | 100
[5 empty] | -- | 2013-11-25 | 7:06 | 2013-11-25 | 18:41 | -- | -- | -- | 0 | 0 | 0 | 11.5833 | N/A | N/A | N/A | Shut down availed for construction of 400 kV Gooty -Madhugiri line vide SRLDC code no. CR-11/ 749.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0 | -- | -- | --
22 | SR2L26 | HASSAN - MYSORE I | 95.875 | SR-II | -- | 2013-11-06 | 7:03 | 2013-11-06 | 17:58 | -- | -- | -- | 10.9167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for rectification of defects in the transmission line vide SRLDC code no. CR-11/123. |  | 96.5463
[5 empty] | -- | 2013-11-07 | 6:05 | 2013-11-07 | 20:02 | -- | -- | -- | 13.95 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for rectification of defects in the transmission line vide SRLDC code no. CR-11/175.
[6 empty] | Sub Total --> | [6 empty] | 24.8667 | 0 | 0 | 0 | -- | -- | --
23 | SR2L27 | HASSAN - MYSORE II | 95.875 | SR-II | -- | 2013-11-03 | 14:07 | 2013-11-05 | 14:35 | -- | -- | -- | 0 | 0 | 0 | 48.4667 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-11/53. |  | 100
[5 empty] | -- | 2013-11-03 | 14:02 | 2013-11-03 | 14:07 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Hassan end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.4667 | -- | -- | --
24 | SR2L28 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L29 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L30 | HOSUR-SALEM | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L32 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L33 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | 2013-11-20 | 23:46 | 41600 | 7:15 | -- | -- | -- | 0 | 0 | 0 | 31.4833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/652. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 31.4833
29 | SR2L34 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2013-11-03 | 13:47 | 2013-11-03 | 18:37 | -- | -- | -- | 0 | 4.8333 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR: 92.82 KM from Kaiga end. Fault occured in KPTCL portion of the line. |  | 100
[5 empty] | -- | 2013-11-04 | 10:32 | 2013-11-04 | 11:09 | -- | -- | -- | 0 | 0.61667 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR: 93.37 KM from Kaiga end. Fault occured in KPTCL portion of the line.
[5 empty] | -- | 2013-11-07 | 0:18 | 2013-11-07 | 12:41 | -- | -- | -- | 0 | 0 | 0 | 12.3833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/173.
[5 empty] | -- | 2013-11-22 | 23:04 | 2013-11-29 | 10:44 | -- | -- | -- | 0 | 0 | 0 | 155.6667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/712.
[6 empty] | Sub Total --> | [6 empty] | 0 | 5.45 | 0 | 168.05 | -- | -- | --
30 | SR2L35 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2013-11-02 | 23:53 | 2013-11-06 | 8:07 | -- | -- | -- | 0 | 0 | 0 | 80.2333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/35. |  | 100
[5 empty] | -- | 2013-11-07 | 22:16 | 2013-11-08 | 6:48 | -- | -- | -- | 0 | 0 | 0 | 8.5333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/226.
[5 empty] | -- | 2013-11-08 | 10:27 | 2013-11-08 | 18:00 | -- | -- | -- | 0 | 0 | 0 | 7.55 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for Y- phase CVT replacement works at Guttur end vide SRLDC code no. CR-11/247.
[5 empty] | -- | 2013-11-08 | 18:00 | 2013-11-09 | 7:35 | -- | -- | -- | 0 | 0 | 0 | 13.5833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide KPTCL message dtd. 08.11.2013.
[5 empty] | -- | 2013-11-09 | 22:21 | 2013-11-10 | 9:40 | -- | -- | -- | 0 | 0 | 0 | 11.3167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/318.
[5 empty] | -- | 2013-11-10 | 23:43 | 2013-11-18 | 8:41 | -- | -- | -- | 0 | 0 | 0 | 176.9667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/436.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 298.1833
31 | SR2L36 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
32 | SR2L37 | KOLAR - BANGALORE | 97.391 | SR-II | -- | 2013-11-22 | 9:05 | 2013-11-22 | 17:03 | -- | -- | -- | 7.9667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of line reactor LAs at Bangalore end vide SRLDC code no. CR-11/ 688. |  | 98.8935
[6 empty] | Sub Total --> | [6 empty] | 7.9667 | 0 | 0 | 0
33 | SR2L37A | KOLAR - CHENNAI | 219 | SR-II | -- | 2013-11-30 | 6:00 | 2013-12-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 18 | N/A | N/A | N/A | Shut down availed for construction of 400 kV Chittoor - Thiruvalam D/C line vide SRLDC code no CR-11/ 901. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 18
34 | SR2L38 | KOLAR - HOODY - I | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
35 | SR2L39 | KOLAR - HOODY - II | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
36 | SR2L40 | KOLAR - HOSUR - I | 69 | SR-II | -- | 2013-11-07 | 9:07 | 2013-11-07 | 17:00 | -- | -- | -- | 7.8833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for line defects rectification works vide SRLDC code no. CR-11/183. |  | 98.9051
[6 empty] | Sub Total --> | [6 empty] | 7.8833 | 0 | 0 | 0
37 | SR2L41 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L43 | MADURAI - TUTICORIN 1 | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L44 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L45 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L46 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L47 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-08 | 16:24 | -- | -- | -- | 0 | 0 | 0 | 184.4 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-10/842. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 184.4
43 | SR2L48 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2013-11-09 | 22:45 | 2013-11-20 | 8:33 | -- | -- | -- | 0 | 0 | 0 | 249.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/317. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 249.8
44 | SR2L49 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L50 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L51 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L52 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L53 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SRL53 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR2L54 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L55 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2013-11-09 | 8:55 | 2013-11-11 | 19:24 | -- | -- | -- | 0 | 0 | 0 | 58.4833 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of 400KV Kayathar - SV Chatram line vide SRLDC code no. CR-11/280. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 58.4833
52 | SR2L56 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L57 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | 2013-11-09 | 9:05 | 2013-11-11 | 19:06 | -- | -- | -- | 0 | 0 | 0 | 58.0167 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of 400KV Kayathar - SV Chatram line vide SRLDC code no. CR-11/281. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 58.0167
54 | SR2L58 | NEYVELI TS-I EXTENSION - TRICHY | 171.95 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L59 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2013-11-22 | 12:04 | 2013-11-22 | 13:35 | -- | -- | -- | 0 | 0 | 0 | 1.5167 | N/A | N/A | N/A | Shut down availed by M/s NLC for breaker testing and wiring checking works vide SRLDC code no. CR-11/ 694. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.5167
56 | SR2L60 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2013-11-29 | 5:51 | 2013-11-29 | 8:55 | -- | -- | -- | 0 | 0 | 0 | 3.0667 | N/A | N/A | N/A | Emergency shut down availed by M/s NLC for attending general lock out problem in circuit breaker at Neyveli TS-2 end vide SRLDC code no. CR-11/865. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.0667
57 | SR2L61 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | 2013-11-03 | 9:43 | 2013-11-04 | 19:07 | -- | -- | -- | 0 | 0 | 0 | 33.4 | N/A | N/A | N/A | Shut down availed by M/s TNEB for erection works of 400 kV Kayathur-Sunguvarchatram D/C line vide SRLDC code no. CR-11/ 43. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33.4
58 | SR2L62 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | 2013-11-25 | 7:14 | 2013-11-25 | 17:27 | -- | -- | -- | 0 | 0 | 0 | 10.2167 | N/A | N/A | N/A | Shut down availed for installation of OPGW under Microwave replacement project vide SRLDC code no. CR-11/750. |  | 100
[5 empty] | -- | 2013-11-26 | 7:09 | 2013-11-26 | 17:42 | -- | -- | -- | 0 | 0 | 0 | 10.55 | N/A | N/A | N/A | Shut down availed for installation of OPGW under Microwave replacement project vide SRLDC code no. CR-11/782.
[5 empty] | -- | 2013-11-28 | 7:07 | 2013-11-28 | 17:14 | -- | -- | -- | 0 | 0 | 0 | 10.1167 | N/A | N/A | N/A | Shut down availed for installation of OPGW under Microwave replacement project vide SRLDC code no. CR-11/836.
[5 empty] | -- | 2013-11-29 | 7:12 | 2013-11-29 | 18:38 | -- | -- | -- | 0 | 0 | 0 | 11.4333 | N/A | N/A | N/A | Shut down availed for installation of OPGW under Microwave replacement project vide SRLDC code no. CR-11/868.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 42.3167
59 | SR2L63 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | 2013-11-16 | 8:02 | 2013-11-16 | 16:57 | -- | -- | -- | 8.9167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending hot spot at loc no 252, 307, 310 & 307 vide SRLDC code no. CR-11/517. |  | 98.7616
[6 empty] | Sub Total --> | [6 empty] | 8.9167 | 0 | 0 | 0
60 | SR2L64 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L65 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L66 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L67 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L68 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L70 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L71 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L72 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
68 | SR2L73 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L74 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
70 | SR2L75 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2013-11-09 | 10:50 | 2013-11-20 | 8:43 | -- | -- | -- | 0 | 0 | 0 | 261.8833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/300. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 261.8833
71 | SR2L76 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | 2013-11-02 | 23:47 | 2013-11-09 | 10:48 | -- | -- | -- | 0 | 0 | 0 | 155.0167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/33. |  | 100
[5 empty] | -- | 2013-11-20 | 9:06 | 2013-11-20 | 15:40 | -- | -- | -- | 0 | 0 | 0 | 6.5667 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for replacement of faulty SF6 gas density monitor at Kudamkulam end vide SRLDC code no. CR-11/ 628.
[5 empty] | -- | 2013-11-20 | 15:40 | 2013-12-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 248.3333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message dtd. 20.11.2013.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 409.9167
72 | SR2L77 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L78 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L79 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR2L80 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L83 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | 2013-11-06 | 7:58 | 2013-11-06 | 16:44 | -- | -- | -- | 8.7667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for insulator replacement work at loc. 109 vide SRLDC code no. CR-11/129. |  | 98.7824
[6 empty] | Sub Total --> | [6 empty] | 8.7667 | 0 | 0 | 0
77 | SR2L84 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | 2013-11-07 | 8:02 | 2013-11-07 | 16:07 | -- | -- | -- | 8.0833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for insulator replacement work at loc. 109 vide SRLDC code no. CR-11/181. |  | 98.8773
[6 empty] | Sub Total --> | [6 empty] | 8.0833 | 0 | 0 | 0
78 | SR2L85 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L86 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L87 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L88 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | 2013-11-07 | 17:30 | 2013-11-07 | 17:48 | -- | -- | -- | 0 | 0 | 0.3 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Palakkad end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.3 | 0
82 | SR2L89 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L90 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | 2013-11-11 | 1:51 | 2013-11-11 | 11:29 | -- | 1 | -- | 9.6333 | 0 | 0 | 0 | N/A | N/A | N/A | Line tripped on Y-N fault due to decapping of insulator at Loc. No.34 (SR-1 portion of the line). |  | 98.662
[6 empty] | 2013-11-11 | 11:29 | 2013-11-11 | 13:54 |  |  |  | 0 | 0 | 0 | 2.4167 |  |  |  | Charging delayed due to system constraints.
[6 empty] | Sub Total --> | [6 empty] | 9.6333 | 0 | 0 | 0
84 | SR2L91 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | 2013-11-05 | 7:25 | 2013-11-05 | 9:17 | -- | -- | -- | 0 | 1.8667 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of direct trip signal from Vallur (NTECL SS) end. |  | 100
[5 empty] | -- | 2013-11-11 | 11:00 | 2013-11-11 | 13:51 | -- | -- | -- | 0 | 0 | 0 | 2.85 | N/A | N/A | N/A | Charging delayed due to system constraints.
[5 empty] | Insulator failure | 2013-11-11 | 8:32 | 2013-11-11 | 11:00 | -- | 1 | -- | 0 | 0 | 0 | 2.4667 | N/A | N/A | N/A | Shut down availed to facilitate attending Y-Phase decapping in Kalavindapattu-Vallur line-1, as it is multi circuit tower vide SRLDC code no. CR-11/342.
[5 empty] | -- | 2013-11-29 | 9:33 | 2013-12-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 38.45 | N/A | N/A | N/A | Shut down availed by M/s NTECL for attending gas leakage at isolator at Vallur GIS end vide SRLDC code no CR-11/ 873.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.8667 | 0 | 0
85 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
89 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-02 | 17:04 | -- | -- | -- | 0 | 0 | 0 | 41.0667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-10/545. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 41.0667
90 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | 2013-11-02 | 17:09 | 2013-11-06 | 10:07 | -- | -- | -- | 0 | 0 | 0 | 88.9667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-11/30. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 88.9667
91 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | 2013-11-26 | 9:03 | 2013-11-26 | 15:18 | -- | -- | -- | 6.25 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-11/789. |  | 99.1319
[6 empty] | Sub Total --> | [6 empty] | 6.25 | 0 | 0 | 0
92 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | 2013-11-27 | 8:32 | 2013-11-27 | 14:43 | -- | -- | -- | 6.1833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-11/807. |  | 99.1412
[6 empty] | Sub Total --> | [6 empty] | 6.1833 | 0 | 0 | 0
93 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | 2013-11-04 | 11:18 | 2013-11-04 | 13:02 | -- | -- | -- | 1.7333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed to attend hot spot observed in 220KV R-ph bushing terminal connector vide SRLDC code no CR-11/76. |  | 99.7593
[6 empty] | Sub Total --> | [6 empty] | 1.7333 | 0 | 0 | 0
102 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
104 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [11 empty] | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | 2013-11-12 | 8:59 | 2013-11-12 | 14:04 | -- | -- | -- | 5.0833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of 400KV R-phase bushing vide SRLDC code no. CR-11/389. |  | 99.294
[6 empty] | Sub Total --> | [6 empty] | 5.0833 | 0 | 0 | 0
110 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | 2013-11-11 | 9:26 | 2013-11-11 | 14:36 | -- | -- | -- | 5.1667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-11/344. |  | 99.2824
[6 empty] | Sub Total --> | [6 empty] | 5.1667 | 0 | 0 | 0
118 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | 2013-11-14 | 9:15 | 2013-11-14 | 14:05 | -- | -- | -- | 4.8333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-11/450. |  | 99.3287
[6 empty] | Sub Total --> | [6 empty] | 4.8333 | 0 | 0 | 0
119 | SR2T36 | TRICHY ICT - I | 315 | SR-II | -- | 2013-11-13 | 12:04 | 2013-11-13 | 15:04 | -- | -- | -- | 0 | 0 | 0 | 3 | N/A | N/A | N/A | Shut down availed by M/s TNEB for attending hot spots at 230 kV Alundur SS vide SRLDC code no. CR-11/418. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3
120 | SR2T37 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T38 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T39 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T40 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T41 | UDUMALPET ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T42 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T43 | UDUMALPET ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2013-11-06 | 8:08 | 2013-11-06 | 21:52 | -- | -- | -- | 0 | 0 | 0 | 13.7333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-07 | 7:35 | 2013-11-07 | 22:22 | -- | -- | -- | 0 | 0 | 0 | 14.7833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:39 | 2013-11-08 | 21:35 | -- | -- | -- | 0 | 0 | 0 | 14.9333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-09 | 7:10 | 2013-11-13 | 21:39 | -- | -- | -- | 0 | 0 | 0 | 110.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-14 | 9:33 | 2013-11-14 | 21:49 | -- | -- | -- | 0 | 0 | 0 | 12.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-15 | 8:43 | 2013-11-15 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 13.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-16 | 6:22 | 2013-11-16 | 21:39 | -- | -- | -- | 0 | 0 | 0 | 15.2833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-17 | 8:45 | 2013-11-19 | 22:07 | -- | -- | -- | 0 | 0 | 0 | 61.3667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-20 | 9:02 | 2013-11-20 | 22:53 | -- | -- | -- | 0 | 0 | 0 | 13.85 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-21 | 17:55 | 2013-11-21 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 4.6333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-22 | 8:55 | 2013-11-22 | 22:38 | -- | -- | -- | 0 | 0 | 0 | 13.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-23 | 5:58 | 2013-11-23 | 21:29 | -- | -- | -- | 0 | 0 | 0 | 15.5167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-25 | 10:10 | 2013-11-25 | 21:37 | -- | -- | -- | 0 | 0 | 0 | 11.45 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-26 | 8:56 | 2013-11-26 | 22:25 | -- | -- | -- | 0 | 0 | 0 | 13.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-27 | 8:42 | 2013-11-27 | 21:32 | -- | -- | -- | 0 | 0 | 0 | 12.8333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-28 | 8:40 | 2013-11-28 | 21:39 | -- | -- | -- | 0 | 0 | 0 | 12.9833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-29 | 8:19 | 2013-11-29 | 21:27 | -- | -- | -- | 0 | 0 | 0 | 13.1333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-30 | 8:26 | 2013-12-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 15.5667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 383.5333
128 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2013-11-06 | 7:57 | 2013-11-06 | 21:45 | -- | -- | -- | 0 | 0 | 0 | 13.8 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-07 | 7:38 | 2013-11-07 | 22:02 | -- | -- | -- | 0 | 0 | 0 | 14.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:41 | 2013-11-08 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 15.8667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-09 | 7:02 | 2013-11-09 | 22:18 | -- | -- | -- | 0 | 0 | 0 | 15.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-11 | 10:11 | 2013-11-13 | 21:31 | -- | -- | -- | 0 | 0 | 0 | 59.3333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-14 | 9:33 | 2013-11-14 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 12.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-16 | 6:30 | 2013-11-16 | 21:32 | -- | -- | -- | 0 | 0 | 0 | 15.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-22 | 8:51 | 2013-11-22 | 22:34 | -- | -- | -- | 0 | 0 | 0 | 13.7167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-23 | 5:58 | 2013-11-23 | 21:22 | -- | -- | -- | 0 | 0 | 0 | 15.4 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-25 | 10:08 | 2013-11-25 | 21:27 | -- | -- | -- | 0 | 0 | 0 | 11.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-26 | 8:40 | 2013-11-26 | 22:21 | -- | -- | -- | 0 | 0 | 0 | 13.6833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-27 | 8:38 | 2013-11-27 | 21:33 | -- | -- | -- | 0 | 0 | 0 | 12.9167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-28 | 8:34 | 2013-11-28 | 21:34 | -- | -- | -- | 0 | 0 | 0 | 13 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-29 | 10:11 | 2013-11-29 | 23:00 | -- | -- | -- | 0 | 0 | 0 | 12.8167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 238.7333
130 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2013-11-06 | 9:48 | 2013-11-06 | 21:19 | -- | -- | -- | 0 | 0 | 0 | 11.5167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-11 | 10:08 | 2013-11-11 | 21:33 |  |  |  | 0 | 0 | 0 | 11.4167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 22.9333
132 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | 2013-11-07 | 9:30 | 2013-11-07 | 22:02 | -- | -- | -- | 0 | 0 | 0 | 12.5333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.5333
131 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-03 | 21:25 | -- | -- | -- | 0 | 0 | 0 | 69.4167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-06 | 7:55 | 2013-11-07 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 38.15 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:25 | 2013-11-16 | 21:31 | -- | -- | -- | 0 | 0 | 0 | 207.1 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-17 | 8:36 | 2013-11-19 | 22:04 | -- | -- | -- | 0 | 0 | 0 | 61.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-25 | 5:56 | 2013-11-27 | 21:24 | -- | -- | -- | 0 | 0 | 0 | 63.4667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-28 | 8:34 | 2013-11-29 | 21:17 | -- | -- | -- | 0 | 0 | 0 | 36.7167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 476.3167
132 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | 2013-11-11 | 10:09 | 2013-11-11 | 21:37 | -- | -- | -- | 0 | 0 | 0 | 11.4667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.4667
133 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-01 | 22:34 | -- | -- | -- | 0 | 0 | 0 | 22.5667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-03 | 18:30 | 2013-11-03 | 21:41 | -- | -- | -- | 0 | 0 | 0 | 3.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-05 | 14:05 | 2013-11-07 | 17:49 | -- | -- | -- | 0 | 0 | 0 | 51.7333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:29 | 2013-11-11 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 87.1833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-13 | 15:52 | 2013-11-16 | 12:58 | -- | -- | -- | 0 | 0 | 0 | 69.1 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-21 | 12:19 | 2013-11-21 | 22:32 | -- | -- | -- | 0 | 0 | 0 | 10.2167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-22 | 16:46 | 2013-11-23 | 21:35 | -- | -- | -- | 0 | 0 | 0 | 28.8167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-28 | 16:43 | 2013-11-28 | 21:45 | -- | -- | -- | 0 | 0 | 0 | 5.0333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-29 | 10:13 | 2013-12-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 37.7833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 315.6167
134 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2013-11-06 | 7:55 | 2013-11-06 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 13.8167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-07 | 7:29 | 2013-11-07 | 22:03 | -- | -- | -- | 0 | 0 | 0 | 14.5667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:37 | 2013-11-08 | 21:24 | -- | -- | -- | 0 | 0 | 0 | 14.7833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-09 | 7:02 | 2013-11-09 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 15.2 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-11 | 10:13 | 2013-11-13 | 21:29 | -- | -- | -- | 0 | 0 | 0 | 59.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-14 | 9:35 | 2013-11-14 | 21:42 | -- | -- | -- | 0 | 0 | 0 | 12.1167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-16 | 6:28 | 2013-11-16 | 21:29 | -- | -- | -- | 0 | 0 | 0 | 15.0167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-22 | 8:53 | 2013-11-22 | 22:34 | -- | -- | -- | 0 | 0 | 0 | 13.6833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-23 | 7:47 | 2013-11-23 | 21:20 | -- | -- | -- | 0 | 0 | 0 | 13.55 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-27 | 8:33 | 2013-11-27 | 21:23 | -- | -- | -- | 0 | 0 | 0 | 12.8333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-29 | 10:07 | 2013-11-29 | 21:15 | -- | -- | -- | 0 | 0 | 0 | 11.1333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 195.9667
135 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2013-11-06 | 9:52 | 2013-11-06 | 21:07 | -- | -- | -- | 0 | 0 | 0 | 11.25 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-07 | 9:31 | 2013-11-07 | 22:06 | -- | -- | -- | 0 | 0 | 0 | 12.5833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-11 | 10:05 | 2013-11-11 | 21:27 | -- | -- | -- | 0 | 0 | 0 | 11.3667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.2
136 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-01 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 22.55 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-03 | 18:28 | 2013-11-07 | 17:38 | -- | -- | -- | 0 | 0 | 0 | 95.1667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:30 | 2013-11-11 | 21:34 | -- | -- | -- | 0 | 0 | 0 | 87.0667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-13 | 15:59 | 2013-11-15 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 54.25 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-21 | 12:28 | 2013-11-21 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 10.0833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-28 | 16:40 | 2013-11-28 | 21:44 | -- | -- | -- | 0 | 0 | 0 | 5.0667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 274.1833
138 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-03 | 21:30 | -- | -- | -- | 0 | 0 | 0 | 69.5 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-06 | 9:58 | 2013-11-07 | 22:07 | -- | -- | -- | 0 | 0 | 0 | 36.15 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-08 | 6:15 | 2013-11-08 | 21:29 | -- | -- | -- | 0 | 0 | 0 | 15.2333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-09 | 7:04 | 2013-11-15 | 22:10 | -- | -- | -- | 0 | 0 | 0 | 159.1 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-16 | 6:14 | 2013-11-16 | 21:35 | -- | -- | -- | 0 | 0 | 0 | 15.35 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 295.3333
139 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-01 | 0:20 | -- | -- | -- | 0 | 0 | 0 | 0.33333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-11 | 10:09 | 2013-11-11 | 13:24 | -- | -- | -- | 0 | 0 | 0 | 3.25 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-11 | 15:43 | 2013-11-11 | 21:33 | -- | -- | -- | 0 | 0 | 0 | 5.8333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-14 | 9:51 | 2013-11-14 | 21:48 | -- | -- | -- | 0 | 0 | 0 | 11.95 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 21.3667
140 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
141 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2R17 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-01 | 22:10 | -- | -- | -- | 0 | 0 | 0 | 22.1667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-11 | 10:05 | 2013-11-16 | 21:34 | -- | -- | -- | 0 | 0 | 0 | 131.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-22 | 8:54 | 2013-11-22 | 22:33 | -- | -- | -- | 0 | 0 | 0 | 13.65 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 167.3
143 | SR2R18 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
144 | SR2R19 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
145 | SR2R20 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2013-11-06 | 9:52 | 2013-11-07 | 17:39 | -- | -- | -- | 0 | 0 | 0 | 31.7833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-11 | 10:07 | 2013-11-13 | 12:25 | -- | -- | -- | 0 | 0 | 0 | 50.3 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-25 | 10:08 | 2013-11-26 | 8:11 | -- | -- | -- | 0 | 0 | 0 | 22.05 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 104.1333
146 | SR2R21 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2013-11-06 | 9:52 | 2013-11-07 | 17:40 | -- | -- | -- | 0 | 0 | 0 | 31.8 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-11 | 10:07 | 2013-11-13 | 12:26 | -- | -- | -- | 0 | 0 | 0 | 50.3167 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2013-11-25 | 10:08 | 2013-11-26 | 8:11 | -- | -- | -- | 0 | 0 | 0 | 22.05 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 104.1667
147 | SR2R22 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2R23 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2R24 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | 2013-11-01 | 0:00 | 2013-11-01 | 22:17 | -- | -- | -- | 0 | 0 | 0 | 22.2833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2013-11-11 | 13:54 | 2013-11-15 | 22:15 | -- | -- | -- | 0 | 0 | 0 | 104.35 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 126.6333
150 | SR2R25 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | 2013-11-18 | 20:33 | 2013-11-18 | 20:33 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 258.95 Km from Talcher end (Tower no.705). |  | 100
[5 empty] | -- | 2013-11-27 | 20:15 | 2013-11-27 | 20:15 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 259.34 kM from Talcher end (Tower no. 706).
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2R26 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
[22 empty] | 15084.958 | 15084.958 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse

## Sheet1
removed
26 | SR2L30 | HOSUR-SALEM II | 125.325 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100
109 |  | HOSUR ICT III