## SOP
[20 empty] | Prepared by | Sarat Chandra D., Dy. Mgr.
Standard of Performance data for the month of FEBRUARY - 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl.No | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2018-02-24 | 8:38 | 2018-02-24 | 17:35 | -- | -- | -- | 0 | 0 | 0 | 8.95 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/978. |  | 100
[5 empty] | -- | 2018-02-25 | 8:20 | 2018-02-25 | 18:13 | -- | -- | -- | 0 | 0 | 0 | 9.88 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1015.
[5 empty] | -- | 2018-02-26 | 8:25 | 2018-02-26 | 18:32 | -- | -- | -- | 0 | 0 | 0 | 10.12 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1043.
[5 empty] | -- | 2018-02-27 | 7:51 | 2018-02-27 | 17:50 | -- | -- | -- | 0 | 0 | 0 | 9.98 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1084.
[5 empty] | -- | 2018-02-28 | 8:10 | 2018-02-28 | 18:20 | -- | -- | -- | 0 | 0 | 0 | 10.17 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1132.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 49.1
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2018-02-03 | 8:26 | 2018-02-03 | 17:45 | -- | -- | -- | 0 | 0 | 0 | 9.32 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/87. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.32
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-03 | 19:11 | -- | -- | -- | 0 | 0 | 0 | 67.18 | N/A | N/A | N/A | Shut down availed by M/s NTPC for attending the problem in CB hydraulic mechanism in R-phase at Kayamkulam end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 67.18
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2018-02-01 | 8:43 | 2018-02-01 | 19:17 | -- | -- | -- | 0 | 0 | 0 | 10.57 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/02. |  | 100
[5 empty] | -- | 2018-02-02 | 8:36 | 2018-02-02 | 17:43 | -- | -- | -- | 0 | 0 | 0 | 9.12 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/41.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 19.69
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | -- | 2018-02-19 | 0:34 | 2018-02-19 | 0:34 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N fault. FLR:20.04km from Kayamkulam end. Fault is in KSEB portion. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2018-02-24 | 8:34 | 2018-02-24 | 17:38 | -- | -- | -- | 0 | 0 | 0 | 9.07 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/977. |  | 100
[5 empty] | -- | 2018-02-25 | 8:19 | 2018-02-25 | 18:12 | -- | -- | -- | 0 | 0 | 0 | 9.88 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1014.
[5 empty] | -- | 2018-02-26 | 8:22 | 2018-02-26 | 18:28 | -- | -- | -- | 0 | 0 | 0 | 10.1 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1042.
[5 empty] | -- | 2018-02-27 | 7:50 | 2018-02-27 | 17:55 | -- | -- | -- | 0 | 0 | 0 | 10.08 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1083.
[5 empty] | -- | 2018-02-28 | 8:11 | 2018-02-28 | 18:21 | -- | -- | -- | 0 | 0 | 0 | 10.17 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1131.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 49.3
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | 2018-02-01 | 8:44 | 2018-02-01 | 19:20 | -- | -- | -- | 0 | 0 | 0 | 10.6 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/03. |  | 100
[5 empty] | -- | 2018-02-02 | 8:38 | 2018-02-02 | 17:34 | -- | -- | -- | 0 | 0 | 0 | 8.93 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/42.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 19.53
8 | SR2L114 | ALAMATHY - THIRUVALAM TN - I | 65.116 | SR-II | -- | 2018-02-01 | 13:37 | 2018-02-02 | 18:01 | -- | -- | -- | 0 | 28.4 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-G fault. FLR: 60km from Almathy end (TNEB portion). |  | 100
[5 empty] | -- | 2018-02-10 | 10:23 | 2018-02-12 | 19:54 | -- | -- | -- | 0 | 0 | 0 | 57.52 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of 765kV Ariyalur-Thiruvalum D/C line vide SRLDC code no. CR-02/354.
[6 empty] | Sub Total --> | [6 empty] | 0 | 28.4 | 0 | 57.52
9 | SR2L115 | ALAMATHY - THIRUVALAM TN - II | 65.116 | SR-II | -- | 2018-02-10 | 10:25 | 2018-02-12 | 19:54 | -- | -- | -- | 0 | 0 | 0 | 57.48 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of 765kV Ariyalur-Thiruvalum D/C line vide SRLDC code no. CR-02/355. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 57.48
10 | SR2L112 | ALAMATHY - VALLUR - I | 65.116 | SR-II | -- | 2018-02-13 | 10:17 | 2018-02-13 | 19:23 | -- | -- | -- | 0 | 0 | 0 | 9.1 | N/A | N/A | N/A | Shut down availed by M/s TNEB for fixing vibration dampers at Almathy end vide SRLDC code no. CR-02/479. |  | 100
[5 empty] | -- | 2018-02-16 | 17:31 | 2018-02-16 | 19:30 | -- | -- | -- | 0 | 1.98 | 0 | 0 | N/A | N/A | N/A | Tripped on B-G fault due to LA failure at Almathy TNEB SS.
[5 empty] | -- | 2018-02-17 | 11:40 | 2018-02-17 | 15:34 | -- | -- | -- | 0 | 0 | 0 | 3.9 | N/A | N/A | N/A | Shut down availed by M/s TNEB for LA replacement work at Almathy end vide SRLDC code CR-02/666.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.98 | 0 | 13
11 | SR2L113 | ALAMATHY - VALLUR - II | 65.116 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | 2018-02-03 | 10:57 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 613.05 | N/A | N/A | N/A | Shut down availed for tower erection & stringing in multicircuit portion of 400kV Dharmapuri-Somanahalli D/C line vide SRLDC code no. CR-02/94. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 613.05
15 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
16 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
18 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
20 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
21 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
24 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L24 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L25 | CUDDAPAH - NP KUNTA I | 61.233 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L26 | GOOTY - BANGALORE | 301.667 | SR-II | -- | 2018-02-18 | 9:06 | 2018-02-18 | 14:40 | -- | -- | -- | 0 | 0 | 0 | 5.57 | N/A | N/A | N/A | Shut down availed for isolator replacement works under ADD CAP at Somanahalli end vide SRLDC code no. CR-02/720. |  | 100
[5 empty] | -- | 2018-02-25 | 10:27 | 2018-02-25 | 16:13 | -- | -- | -- | 0 | 0 | 0 | 5.77 | N/A | N/A | N/A | Shut down availed for isolator replacement at Somanahalli end under addcap works vide SRLDC code CR-02/1018.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.34
29 | SR2L27 | HASSAN - MYSORE I | 95.875 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
30 | SR2L28 | HASSAN - MYSORE II | 95.875 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
31 | SR2L29 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-15 | 17:03 | -- | -- | -- | 0 | 353.05 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-N fault due to insulator decapping at loc. No. 905 (KPTCL portion). |  | 100
[5 empty] | -- | 2018-02-17 | 15:21 | 2018-02-18 | 13:11 | -- | -- | -- | 0 | 21.83 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N fault. FLR:149km from Hassan (KPTCL portion).
[6 empty] | Sub Total --> | [6 empty] | 0 | 374.88 | 0 | 0
32 | SR2L30 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2018-02-20 | 9:56 | 2018-02-20 | 18:10 | -- | -- | -- | 0 | 0 | 0 | 8.23 | N/A | N/A | N/A | shut down availed by M/s KPTCL for insulator replacement at Loc No:380 vide SRLDC code CR-02/789. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.23
33 | SR2L31 | HOSUR-SALEM II | 125.325 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
34 | SR2L32 | HOSUR-SALEM | 126.339 | SR-II | -- | 2018-02-24 | 10:07 | 2018-02-24 | 14:19 | -- | -- | -- | 4.2 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-02/981. |  | 99.375
[6 empty] | Sub Total --> | [6 empty] | 4.2 | 0 | 0 | 0
35 | SR2L33 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2018-02-16 | 20:58 | 2018-02-17 | 8:47 | -- | -- | -- | 0 | 0 | 0 | 11.82 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/655. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.82
36 | SR2L34 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L35 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2018-02-19 | 17:30 | 2018-02-19 | 19:48 | -- | -- | -- | 0 | 0 | 0 | 2.3 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending decapping of Line-2 at Loc No:137 vide SRLDC code no. CR-02/773. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.3
38 | SR2L36 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2018-02-19 | 5:40 | 2018-02-19 | 20:20 | -- | -- | -- | 0 | 14.67 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-N (Ph-earth) transient fault. FLR: 114 kM from Kaiga end. Fault occurred in KPTCL portion of the line. |  | 100
[5 empty] | -- | 2018-02-22 | 17:21 | 2018-02-22 | 18:42 | -- | -- | -- | 0 | 1.35 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of direct trip signal at Kaiga end.
[5 empty] | -- | 2018-02-27 | 12:47 | 2018-02-27 | 13:50 | -- | -- | -- | 0 | 0 | 0 | 1.05 | N/A | N/A | N/A | Shut down availed by M/s KPTCL attending arc over line isolator vide SRLDC code no. CR-02/1102.
[6 empty] | Sub Total --> | [6 empty] | 0 | 16.02 | 0 | 1.05
39 | SR2L37 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L38 | KOLAR - BANGALORE | 97.391 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L39 | KOLAR - HOODY - I | 51.067 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L40 | KOLAR - HOODY - II | 51.067 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
43 | SR2L41 | KOLAR - HOSUR - I | 69 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L42 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L43 | KOLAR - THIRUVALAM - I | 153.195 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L99 | KUDGI - KOLHAPUR - I | 189.799 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L100 | KUDGI - KOLHAPUR - II | 189.799 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L44 | MADURAI - TUTICORIN POOLING STN I | 115.602 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR2L45 | MADURAI - TUTICORIN POOLING STN II | 152.167 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR2L46 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L47 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
52 | SR2L97 | MYSORE - KOZHIKODE I | 215.524 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L98 | MYSORE - KOZHIKODE II | 215.524 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR2L48 | 'NAGAPATTINAM PS - TRICHY - I | 158.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L96 | 'NAGAPATTINAM PS - TRICHY - II | 158.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
56 | SR2L49 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2018-02-26 | 7:19 | 2018-02-26 | 18:16 | -- | -- | -- | 0 | 0 | 0 | 10.95 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/1039. |  | 100
[5 empty] | -- | 2018-02-27 | 7:19 | 2018-02-27 | 19:48 | -- | -- | -- | 0 | 0 | 0 | 12.48 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/1079.
[5 empty] | -- | 2018-02-28 | 8:08 | 2018-02-28 | 19:39 | -- | -- | -- | 0 | 0 | 0 | 11.52 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/1130.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 34.95
57 | SR2L50 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2018-02-23 | 7:17 | 2018-02-23 | 21:29 | -- | -- | -- | 0 | 0 | 0 | 14.2 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/930. |  | 100
[5 empty] | -- | 2018-02-24 | 7:35 | 2018-02-24 | 18:59 | -- | -- | -- | 0 | 0 | 0 | 11.4 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/973.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 25.6
58 | SR2L101 | NARENDRA - KUDGI I | 176.133 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L102 | NARENDRA - KUDGI II | 176.133 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L51 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L52 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L53 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L54 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L55 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SRL56 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SRL57 | NEYVELI TS II - NAGAPATTINAM PS - I | 49.217 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L58 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | 2018-02-02 | 10:26 | 2018-02-02 | 17:14 | -- | -- | -- | 0 | 0 | 0 | 6.8 | N/A | N/A | N/A | Shut down availed by M/s NLC for AMP works at Neyveli TS-2 end vide SRLDC code no. CR-02/50. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.8
68 | SR2L59 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L60 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
70 | SR2L61 | NEYVELI TS-I EXPANSION - NAGAPATTINAM PS - I | 171.95 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L62 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
72 | SR2L63 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L64 | NEYVELI-SALEM - II | 178.72 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L103 | NP KUNTA - KOLAR I | 130.702 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR2L65 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L66 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L116 | PAVAGADA - TUMKUR III | 104.7 | SR-II | -- | 2018-02-11 | 10:47 | 2018-02-11 | 20:25 | -- | -- | -- | 0 | 0 | 0 | 9.63 | N/A | N/A | N/A | Shut down availed for ICT-2 commissioning works vide SRLDC code no. CR-02/404. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.63
78 | SR2L117 | PAVAGADA - TUMKUR IV | 104.7 | SR-II | -- | 2018-02-11 | 10:48 | 2018-02-11 | 20:26 | -- | -- | -- | 0 | 0 | 0 | 9.63 | N/A | N/A | N/A | Shut down availed for ICT-2 commissioning works vide SRLDC code no. CR-02/405. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.63
79 | SR2L67 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L68 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L69 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR2L105 | SALEM - SALEM POOLING STN I | 59.04 | SR-II | -- | 2018-02-25 | 10:04 | 2018-02-25 | 15:00 | -- | -- | -- | 4.93 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-02/1017. |  | 99.2664
[6 empty] | Sub Total --> | [6 empty] | 4.93 | 0 | 0 | 0
83 | SR2L106 | SALEM - SALEM POOLING STN II | 59.04 | SR-II | -- | 2018-02-27 | 10:11 | 2018-02-27 | 13:09 | -- | -- | -- | 2.97 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-02/1090. |  | 99.558
[6 empty] | Sub Total --> | [6 empty] | 2.97 | 0 | 0 | 0
84 | SR2L70 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
85 | SR2L71 | SALEM - UDUMALPET II | 137.91 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2L72 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2L73 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | 2018-02-15 | 11:07 | 2018-02-16 | 21:43 | -- | -- | -- | 0 | 0 | 0 | 34.6 | N/A | N/A | N/A | Shut down availed for converting line reactor as switchable at Sriperumbudur end vide SRLDC code no. CR-02/572. |  | 100
[5 empty] | -- | 2018-02-23 | 10:07 | 2018-02-23 | 19:17 | -- | -- | -- | 0 | 0 | 0 | 9.17 | N/A | N/A | N/A | Shut down availed for conversion of Line reactor to switchable at Sriperumbudur end vide SRLDC code no. CR-02/942.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 43.77
88 | SR2L74 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | 2018-02-01 | 8:35 | 2018-02-03 | 20:26 | -- | -- | -- | 0 | 0 | 0 | 59.85 | N/A | N/A | N/A | Shut down availed by M/s KSEB for enhancement of capacity of bus isolator at Edamon end vide SRLDC code no. CR-02/06. |  | 100
[5 empty] | -- | 2018-02-19 | 14:58 | 2018-02-19 | 18:58 | -- | -- | -- | 0 | 4 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N fault due to failure of R-Phase LA at KSEB Edmon SS.
[5 empty] | -- | 2018-02-24 | 8:27 | 2018-02-24 | 17:41 | -- | -- | -- | 0 | 0 | 0 | 9.23 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/974.
[5 empty] | -- | 2018-02-25 | 8:17 | 2018-02-26 | 18:55 | -- | -- | -- | 0 | 0 | 0 | 34.63 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1012.
[5 empty] | -- | 2018-02-27 | 7:41 | 2018-02-27 | 18:29 | -- | -- | -- | 0 | 0 | 0 | 10.8 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1081.
[5 empty] | -- | 2018-02-28 | 8:02 | 2018-02-28 | 18:57 | -- | -- | -- | 0 | 0 | 0 | 10.92 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1128.
[6 empty] | Sub Total --> | [6 empty] | 0 | 4 | 0 | 125.43
89 | SR2L75 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2018-02-24 | 8:27 | 2018-02-24 | 17:42 | -- | -- | -- | 0 | 0 | 0 | 9.25 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/975. |  | 100
[5 empty] | -- | 2018-02-25 | 8:17 | 2018-02-25 | 18:23 | -- | -- | -- | 0 | 0 | 0 | 10.1 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1013.
[5 empty] | -- | 2018-02-26 | 8:20 | 2018-02-26 | 18:52 | -- | -- | -- | 0 | 0 | 0 | 10.53 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1044.
[5 empty] | -- | 2018-02-27 | 7:40 | 2018-02-27 | 17:58 | -- | -- | -- | 0 | 0 | 0 | 10.3 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1082.
[5 empty] | -- | 2018-02-28 | 8:03 | 2018-02-28 | 18:40 | -- | -- | -- | 0 | 0 | 0 | 10.62 | N/A | N/A | N/A | Shut down availed by M/s KSEB for construction works at Edamon SS vide SRLDC code no. CR-02/1129.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 50.8
90 | SR2L110 | THIRUNELVELI - EDAMON - III | 81.94 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2L111 | THIRUNELVELI - EDAMON - IV | 81.94 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2L76 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2018-02-16 | 10:16 | 2018-02-16 | 18:37 | -- | -- | -- | 0 | 0 | 0 | 8.35 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for attending hotspot in Kudankulam S/Y vide SRLDC code no. CR-02/629. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.35
93 | SR2L77 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | 2018-02-13 | 12:10 | 2018-02-13 | 13:23 | -- | -- | -- | 0 | 0 | 0 | 1.22 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for charging of bus reactor at Kudankulam end vide SRLDC code no. CR-02/485. |  | 100
[5 empty] | -- | 2018-02-20 | 7:54 | 2018-02-20 | 20:54 | -- | -- | -- | 0 | 0 | 0 | 13 | N/A | N/A | N/A | Shut down availed for construction work of 400kV Kudankulam-Tuticorin D/C line vide SRLDC code no. CR-02/786.
[5 empty] | -- | 2018-02-21 | 8:01 | 2018-02-21 | 17:50 | -- | -- | -- | 0 | 0 | 0 | 9.82 | N/A | N/A | N/A | Shut down availed for construction work of 400kV Kudankulam-Tuticorin D/C line vide SRLDC code no. CR-02/835.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 24.04
94 | SR2L78 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2018-02-23 | 8:33 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 135.45 | N/A | N/A | N/A | Shut down availed for rearrangement of the line to connect at Tuticorin PS vide SRLDC code no. CR-02/931. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 135.45
95 | SR2L79 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | 2018-02-23 | 8:27 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 135.55 | N/A | N/A | N/A | Shut down availed for rearrangement of the line to connect at Tuticorin PS vide SRLDC code no. CR-02/932. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 135.55
96 | SR2L80 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2L81 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2L82 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2L83 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2L84 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II | -- | 2018-02-10 | 10:18 | 2018-02-12 | 20:30 | -- | -- | -- | 0 | 0 | 0 | 58.2 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of 765kV Ariyalur-Thiruvalum D/C line vide SRLDC code no. CR-02/356. |  | 100
[5 empty] | -- | 2018-02-26 | 8:04 | 2018-02-28 | 18:25 | -- | -- | -- | 0 | 0 | 0 | 58.35 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction works of 765kV Ariyalur-Thiruvalam D/C line vide SRLDC code no. CR-02/1040.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 116.55
101 | SR2L85 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | 2018-02-10 | 10:27 | 2018-02-12 | 20:32 | -- | -- | -- | 0 | 0 | 0 | 58.08 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction of 765kV Ariyalur-Thiruvalum D/C line vide SRLDC code no. CR-02/357. |  | 100
[5 empty] | -- | 2018-02-26 | 8:06 | 2018-02-28 | 18:26 | -- | -- | -- | 0 | 0 | 0 | 58.33 | N/A | N/A | N/A | Shut down availed by M/s TNEB for construction works of 765kV Ariyalur-Thiruvalam D/C line vide SRLDC code no. CR-02/1041.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 116.41
102 | SR2L86 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2L87 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | 2018-02-05 | 18:01 | 2018-02-05 | 18:01 |  |  |  | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 17.34 kM from Trichur end. |  | 100
[6 empty] | 2018-02-05 | 18:07 | 2018-02-05 | 18:30 |  |  |  | 0 | 0 | 0.38 | 0 | N/A | N/A | N/A | Tripped on B-N transient fault due to forest fire under the line. FLR- 18.05 kM from Trichur end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.38 | 0
104 | SR2L88 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2L89 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2L90 | TUTICORIN JV TPS - TUTICORIN POOLING STN I | 127.232 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2L107 | TUTICORIN JV TPS - TUTICORIN POOLING STN II | 127.232 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2L108 | TUTICORIN POOLING STN - SALEM POOLING STN I | 368.84 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2L109 | TUTICORIN POOLING STN - SALEM POOLING STN II | 368.84 | SR-II | [17 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2L91 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | 2018-02-24 | 9:34 | 2018-02-24 | 18:53 | -- | -- | -- | 0 | 0 | 0 | 9.32 | N/A | N/A | N/A | shut down availed for isolator replacement at Udumalpet under addcap works vide SRLDC code no. CR-02/980. |  | 100
[5 empty] | -- | 2018-02-27 | 10:57 | 2018-02-27 | 18:08 | -- | -- | -- | 0 | 0 | 0 | 7.18 | N/A | N/A | N/A | Shut down availed for isolator replacement at Udumalpet under ADD CAP vide SRLDC code no. CR-02/1095.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16.5
111 | SR2L92 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2L93 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | 2018-02-10 | 9:17 | 2018-02-10 | 17:21 | -- | -- | -- | 0 | 0 | 0 | 8.07 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-02/351. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.07
113 | SR2L94 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2L95 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | 2018-02-18 | 8:26 | 2018-02-18 | 17:52 | -- | -- | -- | 0 | 0 | 0 | 9.43 | N/A | N/A | N/A | Shut down availed for bay extension works of ICT-3 vide SRLDC code no. CR-02/716. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.43
116 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | 2018-02-18 | 8:28 | 2018-02-18 | 17:54 | -- | -- | -- | 0 | 0 | 0 | 9.43 | N/A | N/A | N/A | Shut down availed for bay extension works of ICT-3 vide SRLDC code no. CR-02/717. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.43
117 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2018-02-03 | 10:54 | 2018-02-03 | 18:39 | -- | -- | -- | 0 | 0 | 0 | 7.75 | N/A | N/A | N/A | Shut down availed for replacement of isolator under add-cap work vide SRLDC code no. CR-02/95. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.75
119 | SR2T51 | BANGALORE ICT - III | 501 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | 2018-02-13 | 9:05 | 2018-02-13 | 15:52 |  |  |  | 6.78 | 0 | 0 | 0 |  |  |  | Shut down availed for AMP works & arresting oil leakage vide SRLDC code no. CR-02/472. |  | 98.9911
[6 empty] | Sub Total --> | [6 empty] | 6.78 | 0 | 0 | 0
123 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | 2018-02-14 | 9:06 | 2018-02-14 | 13:50 |  |  |  | 4.73 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for AMP works vide SRLDC code no. CR-02/503. |  | 99.2961
[6 empty] | Sub Total --> | [6 empty] | 4.73 | 0 | 0 | 0
124 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | 2018-02-15 | 10:04 | 2018-02-15 | 14:10 |  |  |  | 4.1 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for AMP works vide SRLDC code no. CR-02/566. |  | 99.3899
[6 empty] | Sub Total --> | [6 empty] | 4.1 | 0 | 0 | 0
125 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
129 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T50 | KALIVANDAPATTU ICT - III | 500 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | 2018-02-10 | 10:58 | 2018-02-10 | 18:53 |  |  |  | 0 | 0 | 0 | 7.92 |  |  |  | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-02/359. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.92
135 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | 2018-02-10 | 10:59 | 2018-02-10 | 18:54 |  |  |  | 0 | 0 | 0 | 7.92 | -- | -- | -- | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-02/360. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.92
136 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2T46 | KOZHIKODE - ICT I | 315 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
139 | SR2T47 | KOZHIKODE - ICT II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
140 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
141 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2T53 | MADURAI ICT - III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
143 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
144 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | 2018-02-25 | 10:55 | 2018-02-25 | 12:39 |  |  |  | 1.73 | 0 | 0 | 0 |  |  |  | Shut down availed for replacement of R-phase LA vide SRLDC code no. CR-02/1020. |  | 99.7426
[6 empty] | Sub Total --> | [6 empty] | 1.73 | 0 | 0 | 0
145 | SR2T52 | MYSORE ICT III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
147 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
150 | SR2T56 | PAVAGADA ICT - I | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2T57 | PAVAGADA ICT - II | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
152 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
153 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
154 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
155 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
156 | SR2T54 | PUGALUR ICT - III | 500 | SR-II | -- | 2018-02-22 | 9:42 | 2018-02-22 | 16:49 | -- | -- | -- | 7.12 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for warranty testing & AMP works vide SRLDC code no. CR-02/887. |  | 98.9405
[6 empty] | Sub Total --> | [6 empty] | 7.12 | 0 | 0 | 0
157 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
158 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
159 | SR2T36 | THIRUVALAM ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
160 | SR2T37 | THIRUVALAM ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
161 | SR2T38 | TRICHY ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
162 | SR2T39 | TRICHY ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
163 | SR2T55 | TRICHY ICT - III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
164 | SR2T40 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
165 | SR2T41 | TRIVANDRUM - ICT II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
166 | SR2T42 | TRIVANDRUM - ICT III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
167 | SR2T48 | TUMKUR - ICT I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
168 | SR2T49 | TUMKUR - ICT II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
169 | SR2T43 | UDUMALPET ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
170 | SR2T44 | UDUMALPET ICT - II | 315 | SR-II | -- | 2018-02-19 | 10:15 | 2018-02-23 | 23:22 | -- | -- | -- | 0 | 0 | 0 | 109.12 | N/A | N/A | N/A | shut down availed for isolator replacement at Udumalpet under addcap works vide SRLDC code CR-02/755. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 109.12
171 | SR2T45 | UDUMALPET ICT - III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
172 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-09 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 214.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1073. |  | 100
[5 empty] | -- | 2018-02-10 | 7:04 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 448.93 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/349.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 663.26
173 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-09 | 20:35 | -- | -- | -- | 0 | 0 | 0 | 212.58 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1142. |  | 100
[5 empty] | -- | 2018-02-12 | 11:15 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 396.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/428.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 609.33
174 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-09 | 20:54 | -- | -- | -- | 0 | 0 | 0 | 212.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/859. |  | 100
[5 empty] | -- | 2018-02-12 | 11:54 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 396.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/435.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 609
175 | SR2R31 | HASSAN BUS REACTOR - II | 125 | SR-II | -- | 2018-02-12 | 11:45 | 2018-02-12 | 18:31 | -- | -- | -- | 0 | 0 | 0 | 6.77 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/432. |  | 100
[5 empty] | -- | 2018-02-23 | 12:47 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 131.22 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/953.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 137.99
176 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | 2018-02-23 | 12:45 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 131.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/952. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 131.25
177 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/687. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
178 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
179 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/279. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
180 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-09 | 21:49 | -- | -- | -- | 0 | 0 | 0 | 213.82 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1072. |  | 100
[5 empty] | -- | 2018-02-10 | 6:59 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 449.02 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/348.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 662.84
181 | SR2R28 | KUDGI BUS REACTOR - I | 125 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
182 | SR2R32 | KUDGI BUS REACTOR - II | 125 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
183 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2018-02-01 | 0:00 | 2018-02-04 | 9:56 | -- | -- | -- | 0 | 0 | 0 | 81.93 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1079. |  | 100
[5 empty] | -- | 2018-02-07 | 12:45 | 2018-02-09 | 20:30 | -- | -- | -- | 0 | 0 | 0 | 55.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/240.
[5 empty] | -- | 2018-02-12 | 11:24 | 2018-02-18 | 18:39 | -- | -- | -- | 0 | 0 | 0 | 151.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/429.
[5 empty] | -- | 2018-02-19 | 10:54 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 229.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/760.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 518.03
184 | SR2R30 | NAGAPATTINAM PS BUS REACTOR - I | 50 | SR-II | -- | 2018-02-16 | 8:45 | 2018-02-16 | 22:18 | -- | -- | -- | 0 | 0 | 0 | 13.55 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/620. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.55
185 | SR2R10 | NARENDRA BUS REACTOR | 125 | SR-II | -- | 2018-02-26 | 11:19 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 60.68 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/1054. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 60.68
186 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/633. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
187 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2018-02-28 | 16:33 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 7.45 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/1145. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.45
188 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
189 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2018-02-28 | 16:35 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 7.42 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/1146. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.42
190 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
191 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
192 | SR2R33 | TRIVENDRUM BUS REACTOR - I | 125 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/704. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
193 | SR2R29 | TUMKUR BUS REACTOR - I | 63 | SR-II | -- | 2018-02-26 | 11:23 | 2018-02-26 | 18:32 | -- | -- | -- | 0 | 0 | 0 | 7.15 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/1057. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.15
194 | SR2R17 | TUTICORIN POOLING STN BUS REACTOR - I | 63 | SR-II | -- | 2018-02-21 | 11:56 | 2018-03-01 | 0:00 |  |  |  | 0 | 0 | 0 | 180.07 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-02/858. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 180.07
195 | SR2R36 | Chittor Line Reactor at Sriperumbudur | 50 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
196 | SR2R37 | Hosur-2 Line Reactor at Salem | 50 | SR-II | -- | 2018-02-26 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 72 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/701. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 72
197 | SR2R38 | Karaikudi Line Reactor at Madurai | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
198 | SR2R18 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/701. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
199 | SR2R26 | Mysore 1 Line Reactor at Kozhikode | 50 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
200 | SR2R27 | Mysore 2 Line Reactor at Kozhikode | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
201 | SR2R39 | Nagapattinam-1 Line Reactor at Trichy | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
202 | SR2R40 | Nagapattinam-2 Line Reactor at Trichy | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
203 | SR2R41 | Nellore-1 Line Reactor at Thiruvalam | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
204 | SR2R42 | Nellore-2 Line Reactor at Thiruvalam | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
205 | SR2R19 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | [16 empty] | 100 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
206 | SR2R20 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
207 | SR2R34 | Palakkad 1 Line Reactor at Trichur | 50 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/57. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
208 | SR2R35 | Palakkad 2 Line Reactor at Trichur | 50 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/58. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
209 | SR2R43 | Salem-2 Line Reactor at Udumalpet | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
210 | SR2R44 | SV Chatram Line Reactor at Sriperumbudur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
211 | SR2R21 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/501. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
212 | SR2R22 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-02-01 | 0:00 | 2018-03-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 672 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/703. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672
213 | SR2R45 | Trichy Line Reactor at Madurai | 50 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
214 | SR2R23 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
215 | SR2R24 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
216 | SR2R25 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
217 | SR2P1 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
218 | SR2P2 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse