## SOP
[20 empty] | Prepared by | Sarat Chandra D., Dy. Mgr.
Standard of Performance data for the month of JANUARY - 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl.No | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2018-01-07 | 8:31 | 2018-01-07 | 11:06 | -- | -- | -- | 0 | 0 | 0 | 2.58 | N/A | N/A | N/A | Shut down availed by M/s KSEB for CT clamp replacement works at Edappon end vide SRLDC code no. CR-01/181. |  | 100
[5 empty] | -- | 2018-01-12 | 8:55 | 2018-01-16 | 19:53 | -- | -- | -- | 0 | 0 | 0 | 106.97 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of bays at Edamon end vide SRLDC code no. CR-01/440.
[5 empty] | -- | 2018-01-20 | 8:05 | 2018-01-20 | 14:22 | -- | -- | -- | 0 | 0 | 0 | 6.28 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of bays at Edamon end vide SRLDC code no. CR-01/749.
[5 empty] | -- | 2018-01-29 | 8:01 | 2018-01-29 | 18:26 | -- | -- | -- | 0 | 0 | 0 | 10.42 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1136.
[5 empty] | -- | 2018-01-30 | 8:41 | 2018-01-30 | 18:10 | -- | -- | -- | 0 | 0 | 0 | 9.48 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1191.
[5 empty] | -- | 2018-01-31 | 8:43 | 2018-01-31 | 16:48 | -- | -- | -- | 0 | 0 | 0 | 8.08 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1241.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 143.81
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2018-01-10 | 8:09 | 2018-01-10 | 14:32 | -- | -- | -- | 0 | 0 | 0 | 6.38 | N/A | N/A | N/A | Shut down availed by M/s KSEB for attending hotspot in CT clamp at Edappon end vide SRLDC code no. CR-01/308. |  | 100
[5 empty] | -- | 2018-01-28 | 8:44 | 2018-01-28 | 18:36 | -- | -- | -- | 0 | 0 | 0 | 9.87 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1115.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16.25
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2018-01-09 | 8:30 | 2018-01-09 | 17:44 | -- | -- | -- | 0 | 0 | 0 | 9.23 | N/A | N/A | N/A | Shut down availed by M/s KSEB for half yearly maintenance works at Kundra end vide SRLDC code no. CR-01/260. |  | 100
[5 empty] | -- | 2018-01-28 | 8:48 | 2018-01-28 | 19:00 | -- | -- | -- | 0 | 0 | 0 | 10.2 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1116.
[5 empty] | -- | 2018-01-28 | 19:00 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 77 | N/A | N/A | N/A | Shut down availed by M/s NTPC for attending the problem in CB hydraulic mechanism at Kayamkulam.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 96.43
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2018-01-22 | 10:11 | 2018-01-22 | 18:37 | -- | -- | -- | 0 | 0 | 0 | 8.43 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/835. |  | 100
[5 empty] | -- | 2018-01-25 | 9:03 | 2018-01-25 | 19:16 | -- | -- | -- | 0 | 0 | 0 | 10.22 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1008.
[5 empty] | -- | 2018-01-27 | 8:03 | 2018-01-27 | 19:17 | -- | -- | -- | 0 | 0 | 0 | 11.23 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1074.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 29.88
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | -- | 2018-01-22 | 10:08 | 2018-01-22 | 18:11 | -- | -- | -- | 0 | 0 | 0 | 8.05 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/836. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.05
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2018-01-04 | 8:48 | 2018-01-04 | 16:32 | -- | -- | -- | 0 | 0 | 0 | 7.73 | N/A | N/A | N/A | Shut down availed by M/s KSEB for half yearly maintenance works at Kundra end vide SRLDC code no. CR-01/98. |  | 100
[5 empty] | -- | 2018-01-17 | 7:41 | 2018-01-20 | 20:33 | -- | -- | -- | 0 | 0 | 0 | 84.87 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of bays at Edamon end vide SRLDC code no. CR-01/577.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 92.6
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | 2018-01-25 | 9:04 | 2018-01-25 | 19:29 | -- | -- | -- | 0 | 0 | 0 | 10.42 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1009. |  | 100
[5 empty] | -- | 2018-01-27 | 9:19 | 2018-01-27 | 18:59 | -- | -- | -- | 0 | 0 | 0 | 9.67 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-01/1075.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 20.09
8 | SR2L114 | ALAMATHY - THIRUVALAM TN - I | 65.116 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
9 | SR2L115 | ALAMATHY - THIRUVALAM TN - II | 65.116 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L112 | ALAMATHY - VALLUR - I | 65.116 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
11 | SR2L113 | ALAMATHY - VALLUR - II | 65.116 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
15 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
16 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
18 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
20 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
21 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | 2018-01-15 | 1:02 | 2018-01-15 | 1:29 | -- | -- | -- | 0 | 0.45 | 0 | 0 | N/A | N/A | N/A | Tripped at Chittoor APTRANSCO end only on B-G fault. Auto-reclosed successfully at Sriperumbudur end. FLR : 23.69 kM from Sriperumbudur end. |  | 100
[5 empty] | -- | 2018-01-24 | 10:25 | 2018-01-31 | 19:21 | -- | -- | -- | 0 | 0 | 0 | 176.93 | N/A | N/A | N/A | Shut down availed for converting line reactor as switchable at Sriperumbudur end vide SRLDC code no. CR-01/950.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.45 | 0 | 176.93
24 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L24 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L25 | CUDDAPAH - NP KUNTA I | 61.233 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L26 | GOOTY - BANGALORE | 301.667 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L27 | HASSAN - MYSORE I | 95.875 | SR-II | -- | 2018-01-18 | 14:09 | 2018-01-18 | 14:25 | -- | -- | -- | 0 | 0 | 0 | 0.27 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-01/639. |  | 100
[6 empty] | 2018-01-23 | 15:36 | 2018-01-23 | 18:04 |  |  |  | 0 | 0 | 0 | 2.47 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation in the system vide SRLDC code no. CR-01/915.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.74
30 | SR2L28 | HASSAN - MYSORE II | 95.875 | SR-II | -- | 2018-01-23 | 15:37 | 2018-01-25 | 6:07 | -- | -- | -- | 0 | 0 | 0 | 38.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation in the system vide SRLDC code no. CR-01/916. |  | 100
[6 empty] | 2018-01-25 | 12:32 | 2018-01-27 | 10:34 | -- | -- | -- | 0 | 0 | 0 | 46.03 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation in the system vide SRLDC code no. CR-01/1028.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 84.53
31 | SR2L29 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | 2018-01-01 | 0:00 | 2018-02-01 | 0:00 |  |  |  | 0 | 743.99 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-N fault due to insulator decapping at loc. 905 (KPTCL portion). |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 743.99 | 0 | 0
32 | SR2L30 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2018-01-17 | 12:02 | 2018-01-17 | 17:07 | -- | -- | -- | 0 | 0 | 0 | 5.08 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for maintenance works at Talaguppa end vide SRLDC code no. CR-01/595. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.08
33 | SR2L31 | HOSUR-SALEM II | 125.325 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
34 | SR2L32 | HOSUR-SALEM | 126.339 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
35 | SR2L33 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
36 | SR2L34 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L35 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2018-01-29 | 10:32 | 2018-01-29 | 15:47 | -- | -- | -- | 0 | 0 | 0 | 5.25 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for arresting CT oil leakage at Kaiga end vide SRLDC code no CR-01/1148. |  | 100
[5 empty] | -- | 2018-01-30 | 20:47 | 2018-01-31 | 11:24 | -- | -- | -- | 0 | 0 | 0 | 14.62 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1231.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 19.87
38 | SR2L36 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L37 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | 2018-01-17 | 7:11 | 2018-01-17 | 18:19 | -- | -- | -- | 0 | 0 | 0 | 11.13 | N/A | N/A | N/A | Shut down availed for converting line reactor as switchable at Madurai end vide SRLDC code no. CR-01/576. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.13
40 | SR2L38 | KOLAR - BANGALORE | 97.391 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L39 | KOLAR - HOODY - I | 51.067 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L40 | KOLAR - HOODY - II | 51.067 | SR-II | -- | 2018-01-14 | 17:39 | 2018-01-15 | 2:31 | -- | -- | -- | 8.87 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-G fault due to failure of LA at Hoody end. |  | 98.8078
[6 empty] | Sub Total --> | [6 empty] | 8.87 | 0 | 0 | 0
43 | SR2L41 | KOLAR - HOSUR - I | 69 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L42 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L43 | KOLAR - THIRUVALAM - I | 153.195 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L99 | KUDGI - KOLHAPUR - I | 189.799 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L100 | KUDGI - KOLHAPUR - II | 189.799 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L44 | MADURAI - TUTICORIN POOLING STN I | 115.602 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR2L45 | MADURAI - TUTICORIN POOLING STN II | 152.167 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR2L46 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L47 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2018-01-11 | 10:30 | 2018-01-11 | 18:13 | -- | -- | -- | 0 | 0 | 0 | 7.72 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for attending hot spot at Kudamkulam end vide SRLDC code no. CR-01/381. |  | 100
[5 empty] | -- | 2018-01-22 | 8:24 | 2018-01-24 | 19:07 | -- | -- | -- | 0 | 0 | 0 | 58.72 | N/A | N/A | N/A | Shut down availed for restoring of lines at Tirunelveli vide SRLDC code no CR-01/833.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 66.44
52 | SR2L97 | MYSORE - KOZHIKODE I | 215.524 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L98 | MYSORE - KOZHIKODE II | 215.524 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR2L48 | 'NAGAPATTINAM PS - TRICHY - I | 158.7 | SR-II | -- | 2018-01-23 | 10:10 | 2018-01-23 | 16:24 | -- | -- | -- | 0 | 0 | 0 | 6.23 | N/A | N/A | N/A | Shut down availed for converting line reactor as switchable at Trichy end vide SRLDC code no. CR-01/900. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.23
55 | SR2L96 | 'NAGAPATTINAM PS - TRICHY - II | 158.7 | SR-II | -- | 2018-01-22 | 15:15 | 2018-01-22 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 2.98 | N/A | N/A | N/A | Shut down availed for converting line reactor as switchable at Trichy end vide SRLDC code no. CR-01/870. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.98
56 | SR2L49 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
57 | SR2L50 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
58 | SR2L101 | NARENDRA - KUDGI I | 176.133 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L102 | NARENDRA - KUDGI II | 176.133 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L51 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L52 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L53 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L54 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | 2018-01-21 | 18:01 | 2018-01-21 | 18:25 | -- | -- | -- | 0 | 0 | 0.4 | 0 |  |  |  | Line tripped on operation of over voltage protection at Mysore end. Direct trip signal received at Nelamangala end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.4 | 0
64 | SR2L55 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SRL56 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SRL57 | NEYVELI TS II - NAGAPATTINAM PS - I | 49.217 | SR-II | -- | 2018-01-02 | 10:43 | 2018-01-02 | 15:11 | -- | -- | -- | 0 | 0 | 0 | 4.47 |  |  |  | Shut down availed by M/s NLC for test charging of newly replaced bus coupler CB at NLY TS II end vide SRLDC code no. CR-01/23. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.47
67 | SR2L58 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
68 | SR2L59 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2018-01-14 | 3:25 | 2018-01-14 | 9:42 | -- | -- | -- | 0 | 6.28 | 0 | 0 | -- | -- | -- | Tripped due to receipt of DT from Neyveli TS2 end. |  | 100
[5 empty] | -- | 2018-01-18 | 9:03 | 2018-01-18 | 15:38 | -- | -- | -- | 0 | 0 | 0 | 6.58 | -- | -- | -- | Shut down availed by M/s NLC for protection checking at Neyvelli end vide SRLDC code no. CR-01/615.
[6 empty] | Sub Total --> | [6 empty] | 0 | 6.28 | 0 | 6.58
69 | SR2L60 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
70 | SR2L61 | NEYVELI TS-I EXPANSION - NAGAPATTINAM PS - I | 171.95 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L62 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
72 | SR2L63 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2018-01-05 | 8:56 | 2018-01-12 | 16:40 | -- | -- | -- | 0 | 0 | 0 | 175.73 | N/A | N/A | N/A | Shut down availed by M/s NLC for retrofitting works at Neyveli end vide SRLDC code no. CR-01/132. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 175.73
73 | SR2L64 | NEYVELI-SALEM - II | 178.72 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L103 | NP KUNTA - KOLAR I | 130.702 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR2L65 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L66 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L116 | PAVAGADA - TUMKUR III | 104.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L67 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L68 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L69 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L105 | SALEM - SALEM POOLING STN I | 59.04 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR2L106 | SALEM - SALEM POOLING STN II | 59.04 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L70 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR2L71 | SALEM - UDUMALPET II | 137.91 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
85 | SR2L72 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- | 2018-01-13 | 21:54 | 2018-01-13 | 21:54 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 72.2 kM from Thiruvalam end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2L73 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2L74 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | 2018-01-20 | 8:10 | 2018-01-21 | 7:00 | -- | -- | -- | 0 | 0 | 0 | 22.83 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of bays at Edamon end vide SRLDC code no. CR-01/797. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 22.83
88 | SR2L75 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2018-01-15 | 8:27 | 2018-01-15 | 19:06 | -- | -- | -- | 0 | 0 | 0 | 10.65 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of Bays at Edamon end vide SRLDC code no. CR-01/542. |  | 100
[6 empty] | 2018-01-20 | 8:10 | 2018-01-20 | 14:46 | -- | -- | -- | 0 | 0 | 0 | 6.6 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of bays at Edamon end vide SRLDC code no. CR-01/750.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 17.25
89 | SR2L110 | THIRUNELVELI - EDAMON - III | 81.94 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2L111 | THIRUNELVELI - EDAMON - IV | 81.94 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2L76 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2018-01-11 | 10:30 | 2018-01-11 | 18:13 | -- | -- | -- | 0 | 0 | 0 | 7.72 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for attending hot spot at Kudamkulam end vide SRLDC code no. CR-01/381. |  | 100
[5 empty] | -- | 2018-01-22 | 8:24 | 2018-01-24 | 19:56 | -- | -- | -- | 0 | 0 | 0 | 59.53 | N/A | N/A | N/A | Shut down availed for restoring of lines at Tirunelveli vide SRLDC code no CR-01/833.
[5 empty] | -- | 2018-01-27 | 16:14 | 2018-01-27 | 19:50 | -- | -- | -- | 0 | 0 | 0 | 3.6 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for attending hotspot in Kudankulam switch yard vide SRLDC code no. CR-01/1099.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 70.85
92 | SR2L77 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | Conductor Snapping | 2018-01-03 | 10:55 | 2018-01-03 | 22:15 | -- | -- | -- | 11.33 | 0 | 0 | 0 | 48 | N | N/A | Tripped on R-Y fault due to conductor snapping at loc no: 176. |  | 98.4772
[6 empty] | Sub Total --> | [6 empty] | 11.33 | 0 | 0 | 0
93 | SR2L78 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2018-01-03 | 9:45 | 2018-01-03 | 11:39 | -- | -- | -- | 0 | 0 | 0 | 1.9 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for attending hotspot at Kudankulam end vide SRLDC code no. CR-01/54. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.9
94 | SR2L79 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2L80 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2L81 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2L82 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2L83 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2L84 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2L85 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2L86 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2L87 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2L88 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
104 | SR2L89 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | 2018-01-18 | 7:09 | 2018-01-18 | 17:00 | -- | -- | -- | 0 | 0 | 0 | 9.85 | N/A | N/A | N/A | Shut down availed for converting line reactor as switchable at Madurai end vide SRLDC code no. CR-01/611. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.85
105 | SR2L90 | TUTICORIN JV TPS - TUTICORIN POOLING STN I | 127.232 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2L107 | TUTICORIN JV TPS - TUTICORIN POOLING STN II | 127.232 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2L108 | TUTICORIN POOLING STN - SALEM POOLING STN I | 368.84 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2L109 | TUTICORIN POOLING STN - SALEM POOLING STN II | 368.84 | SR-II | [17 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2L91 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2L92 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2L93 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2L94 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2L95 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T51 | BANGALORE ICT - III | 501 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
129 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T50 | KALIVANDAPATTU ICT - III | 500 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
135 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
136 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2T46 | KOZHIKODE - ICT I | 315 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2T47 | KOZHIKODE - ICT II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
139 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
140 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
141 | SR2T53 | MADURAI ICT - III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
143 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
144 | SR2T52 | MYSORE ICT III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
145 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
147 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | 2018-01-18 | 9:43 | 2018-01-18 | 14:09 | -- | -- | -- | 4.43 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP Works vide SRLDC code no. CR-01/621. |  | 99.4046
[6 empty] | Sub Total --> | [6 empty] | 4.43 | 0 | 0 | 0
148 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | 2018-01-19 | 9:18 | 2018-01-19 | 13:48 | -- | -- | -- | 4.5 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP Works vide SRLDC code no. CR-01/680. |  | 99.3952
[6 empty] | Sub Total --> | [6 empty] | 4.5 | 0 | 0 | 0
149 | SR2T56 | PAVAGADA ICT - I | 500 | SR-II | -- | 2018-01-19 | 9:18 | 2018-01-19 | 13:48 | -- | -- | -- | 4.5 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP Works vide SRLDC code no. CR-01/680. |  | 99.3952
[6 empty] | Sub Total --> | [6 empty] | 4.5 | 0 | 0 | 0
150 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | 2018-01-27 | 11:38 | 2018-01-27 | 12:40 | -- | -- | -- | 1.03 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for checking OLTC oil leak & to topup oil in OLTC tank vide SRLDC code no. CR-01/1083. |  | 99.8616
[6 empty] | Sub Total --> | [6 empty] | 1.03 | 0 | 0 | 0
152 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
153 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
154 | SR2T54 | PUGALUR ICT - III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
155 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
156 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
157 | SR2T36 | THIRUVALAM ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
158 | SR2T37 | THIRUVALAM ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
159 | SR2T38 | TRICHY ICT - I | 315 | SR-II | -- | 2018-01-19 | 10:50 | 2018-01-19 | 16:01 | -- | -- | -- | 0 | 0 | 0 | 5.18 | N/A | N/A | N/A | Shut down availed by M/s TNEB for maintenance work at TNEB 230kV SS vide SRLDC code no. CR-01/696. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.18
160 | SR2T39 | TRICHY ICT - II | 315 | SR-II | -- | 2018-01-23 | 11:35 | 2018-01-23 | 14:51 | -- | -- | -- | 0 | 0 | 0 | 3.27 | N/A | N/A | N/A | Shut down availed by M/s TNEB for maintenance of downstream 220kV Bus coupler at Alundur SS vide SRLDC code no. CR-01/904. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.27
161 | SR2T55 | TRICHY ICT - III | 500 | SR-II | -- | 2018-01-09 | 16:37 | 2018-01-09 | 18:46 | -- | -- | -- | 0 | 0 | 0 | 2.15 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-01/282. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.15
162 | SR2T40 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
163 | SR2T41 | TRIVANDRUM - ICT II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
164 | SR2T42 | TRIVANDRUM - ICT III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
165 | SR2T48 | TUMKUR - ICT I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
166 | SR2T49 | TUMKUR - ICT II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
167 | SR2T43 | UDUMALPET ICT - I | 315 | SR-II | -- | 2018-01-10 | 2:27 | 2018-01-10 | 4:13 | -- | -- | -- | 0 | 1.77 | 0 | 0 | N/A | N/A | N/A | Tripped (230kV side only) on operation of 230kV busbar protection at 230kV Mywadi SS due to fault in TNEB downstream system. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.77 | 0 | 0
168 | SR2T44 | UDUMALPET ICT - II | 315 | SR-II | -- | 2018-01-10 | 2:27 | 2018-01-10 | 4:15 | -- | -- | -- | 0 | 1.8 | 0 | 0 | N/A | N/A | N/A | Tripped (230kV side only) on operation of 230kV busbar protection at 230kV Mywadi SS due to fault in TNEB downstream system. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.8 | 0 | 0
169 | SR2T45 | UDUMALPET ICT - III | 315 | SR-II | -- | 2018-01-10 | 2:27 | 2018-01-10 | 4:16 | -- | -- | -- | 0 | 1.82 | 0 | 0 | N/A | N/A | N/A | Tripped (230kV side only) on operation of 230kV busbar protection at 230kV Mywadi SS due to fault in TNEB downstream system. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.82 | 0 | 0
170 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-07 | 22:28 | -- | -- | -- | 0 | 0 | 0 | 166.47 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/1062. |  | 100
[5 empty] | -- | 2018-01-08 | 7:35 | 2018-01-14 | 21:52 | -- | -- | -- | 0 | 0 | 0 | 158.28 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/215.
[5 empty] | -- | 2018-01-16 | 8:01 | 2018-01-18 | 23:12 | -- | -- | -- | 0 | 0 | 0 | 63.18 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/559.
[5 empty] | -- | 2018-01-19 | 9:31 | 2018-01-21 | 18:26 | -- | -- | -- | 0 | 0 | 0 | 56.92 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/682.
[5 empty] | -- | 2018-01-22 | 9:53 | 2018-01-26 | 21:36 | -- | -- | -- | 0 | 0 | 0 | 107.72 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/844.
[5 empty] | -- | 2018-01-27 | 7:44 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 112.27 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1073.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 664.84
171 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2018-01-06 | 8:18 | 2018-01-07 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 37.93 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/171. |  | 100
[5 empty] | -- | 2018-01-08 | 11:56 | 2018-01-14 | 21:51 | -- | -- | -- | 0 | 0 | 0 | 153.92 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/223.
[5 empty] | -- | 2018-01-19 | 10:07 | 2018-01-21 | 21:05 | -- | -- | -- | 0 | 0 | 0 | 58.97 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/688.
[5 empty] | -- | 2018-01-22 | 9:52 | 2018-01-27 | 16:24 | -- | -- | -- | 0 | 0 | 0 | 126.53 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/845.
[5 empty] | -- | 2018-01-29 | 9:09 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 62.85 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1142.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 440.2
172 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2018-01-18 | 12:00 | 2018-01-19 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 33.67 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/632. |  | 100
[5 empty] | -- | 2018-01-19 | 9:57 | 2018-01-19 | 21:17 | -- | -- | -- | 0 | 0 | 0 | 11.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/685.
[5 empty] | -- | 2018-01-20 | 10:58 | 2018-01-21 | 18:09 | -- | -- | -- | 0 | 0 | 0 | 31.18 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/774.
[5 empty] | -- | 2018-01-22 | 11:19 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 228.68 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/859.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 304.86
173 | SR2R31 | HASSAN BUS REACTOR - II | 125 | SR-II | -- | 2018-01-03 | 12:24 | 2018-01-03 | 17:53 | -- | -- | -- | 0 | 0 | 0 | 5.48 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/68. |  | 100
[5 empty] | -- | 2018-01-20 | 10:55 | 2018-01-21 | 18:10 | -- | -- | -- | 0 | 0 | 0 | 31.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/772.
[5 empty] | -- | 2018-01-22 | 11:09 | 2018-01-26 | 18:27 | -- | -- | -- | 0 | 0 | 0 | 103.3 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/858.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 140.03
174 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/86. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
175 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-14 | 22:45 | -- | -- | -- | 0 | 0 | 0 | 334.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/444. |  | 100
[6 empty] | 2018-01-19 | 10:02 | 2018-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 301.97 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/687.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 636.72
176 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | 2018-01-12 | 9:53 | 2018-01-13 | 19:49 | -- | -- | -- | 0 | 0 | 0 | 33.93 | N/A | N/A | N/A | Shut down availed for bay extension works vide SRLDC code no. CR-01/445. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 33.93
177 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-07 | 22:20 | -- | -- | -- | 0 | 0 | 0 | 166.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-10/909. |  | 100
[5 empty] | -- | 2018-01-09 | 12:39 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 539.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/279.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 705.68
178 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-01 | 21:41 | -- | -- | -- | 0 | 0 | 0 | 21.68 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/1171. |  | 100
[5 empty] | -- | 2018-01-02 | 7:50 | 2018-01-07 | 22:14 | -- | -- | -- | 0 | 0 | 0 | 134.4 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/18.
[5 empty] | -- | 2018-01-08 | 7:31 | 2018-01-12 | 2:08 | -- | -- | -- | 0 | 0 | 0 | 90.62 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/214.
[5 empty] | -- | 2018-01-12 | 6:59 | 2018-01-14 | 21:39 | -- | -- | -- | 0 | 0 | 0 | 62.67 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/435.
[5 empty] | -- | 2018-01-16 | 8:00 | 2018-01-18 | 23:05 | -- | -- | -- | 0 | 0 | 0 | 63.08 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/558.
[5 empty] | -- | 2018-01-19 | 6:50 | 2018-01-26 | 21:28 | -- | -- | -- | 0 | 0 | 0 | 182.63 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/673.
[5 empty] | -- | 2018-01-27 | 7:35 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 112.42 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1072.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 667.5
179 | SR2R28 | KUDGI BUS REACTOR - I | 125 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
180 | SR2R32 | KUDGI BUS REACTOR - II | 125 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
181 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2018-01-18 | 11:39 | 2018-01-18 | 23:11 | -- | -- | -- | 0 | 0 | 0 | 11.53 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/631. |  | 100
[5 empty] | -- | 2018-01-19 | 9:30 | 2018-01-19 | 21:22 | -- | -- | -- | 0 | 0 | 0 | 11.87 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/683.
[5 empty] | -- | 2018-01-20 | 10:51 | 2018-01-21 | 18:07 | -- | -- | -- | 0 | 0 | 0 | 31.27 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/771.
[5 empty] | -- | 2018-01-22 | 11:08 | 2018-01-26 | 18:28 | -- | -- | -- | 0 | 0 | 0 | 103.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/857.
[5 empty] | -- | 2018-01-27 | 10:27 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 109.55 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/1079.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 267.55
182 | SR2R30 | NAGAPATTINAM PS BUS REACTOR - I | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
183 | SR2R10 | NARENDRA BUS REACTOR | 125 | SR-II | -- | 2018-01-09 | 9:28 | 2018-01-09 | 19:41 | -- | -- | -- | 0 | 0 | 0 | 10.22 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/266. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.22
184 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-14 | 22:32 | -- | -- | -- | 0 | 0 | 0 | 334.53 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/920. |  | 100
[5 empty] | -- | 2018-01-18 | 11:50 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 324.17 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/633.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 658.7
185 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2018-01-08 | 7:32 | 2018-01-08 | 21:25 | -- | -- | -- | 0 | 0 | 0 | 13.88 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/213. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 13.88
186 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
187 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
188 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
189 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
190 | SR2R33 | TRIVENDRUM BUS REACTOR - I | 125 | SR-II | -- | 2018-01-12 | 7:44 | 2018-01-14 | 22:05 | -- | -- | -- | 0 | 0 | 0 | 62.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/438. |  | 100
[5 empty] | -- | 2018-01-19 | 11:40 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 300.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/704.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 362.68
191 | SR2R29 | TUMKUR BUS REACTOR - I | 63 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
192 | SR2R17 | TUTICORIN POOLING STN BUS REACTOR - I | 63 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
193 | SR2R18 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2018-01-19 | 11:32 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 300.47 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/701. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 300.47
194 | SR2R26 | Mysore 1 Line Reactor at Kozhikode | 50 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
195 | SR2R27 | Mysore 2 Line Reactor at Kozhikode | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
196 | SR2R19 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | [16 empty] | 100 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
197 | SR2R20 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
198 | SR2R21 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-07 | 22:26 | -- | -- | -- | 0 | 0 | 0 | 166.43 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/501. |  | 100
[6 empty] | 2018-01-19 | 11:35 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 300.42 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/702.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 466.85
199 | SR2R22 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-07 | 22:27 | -- | -- | -- | 0 | 0 | 0 | 166.45 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/502. |  | 100
[5 empty] | -- | 2018-01-19 | 11:35 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 300.42 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/703.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 466.87
200 | SR2R23 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-11 | 23:35 | -- | -- | -- | 0 | 0 | 0 | 263.58 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/1173. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 263.58
201 | SR2R24 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2018-01-01 | 0:00 | 2018-01-11 | 23:36 | -- | -- | -- | 0 | 0 | 0 | 263.6 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/1174. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 263.6
202 | SR2R25 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
203 | SR2R34 | Palakkad 1 Line Reactor at Trichur | 50 | SR-II | -- | 2018-01-03 | 10:57 | 2018-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 685.05 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/57. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 685.05
204 | SR2R35 | Palakkad 2 Line Reactor at Trichur | 50 | SR-II | -- | 2018-01-03 | 10:56 | 2018-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 685.07 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/58. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 685.07
205 | SR2P1 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | 2018-01-06 | 6:00 | 2018-01-07 | 21:03 | -- | -- | -- | 0 | 0 | 0 | 39.05 | N/A | N/A | N/A | Shut down availed for CLR insulator replacement in pollution strectch end vide SRLDC code no. CR-01/167. |  | 99.0565
[5 empty] | -- | 2018-01-08 | 6:56 | 2018-01-08 | 18:00 | -- | -- | -- | 0 | 0 | 0 | 11.07 | N/A | N/A | N/A | Shut down availed for replacement of grading electrodes of valve cooling system for performance improvement of HVDC system vide SRLDC code no. CR-01/210.
[5 empty] | -- | 2018-01-08 | 19:06 | 2018-01-09 | 0:54 | -- | -- | -- | 5.8 | 0 | 0 | 0 | N/A | N/A | N/A | Blocked due to receipt of ESOF signal from Talcher
[5 empty] | -- | 2018-01-09 | 7:51 | 2018-01-09 | 9:04 | -- | -- | -- | 1.22 | 0 | 0 | 0 | N/A | N/A | N/A | Blocked due to receipt of ESOF signal from Talcher end.
[5 empty] | -- | 2018-01-14 | 6:31 | 2018-01-14 | 6:31 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 34.8 kM from Talcher end (Tower no. 98).
[6 empty] | Sub Total --> | [6 empty] | 7.02 | 0 | 0 | 50.12
206 | SR2P2 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | 2018-01-06 | 6:03 | 2018-01-07 | 18:56 | -- | -- | -- | 0 | 0 | 0 | 36.88 | N/A | N/A | N/A | Shut down availed for CLR insulator replacement in pollution strectch end vide SRLDC code no. CR-01/168. |  | 100
[5 empty] | -- | 2018-01-09 | 7:36 | 2018-01-09 | 21:14 | -- | -- | -- | 0 | 0 | 0 | 13.63 | N/A | N/A | N/A | Shut down availed for replacement of grading electrodes of valve cooling system for performance improvement of HVDC system vide SRLDC code no. CR-01/255.
[5 empty] | -- | 2018-01-14 | 6:24 | 2018-01-14 | 6:24 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 608.2 kM from Talcher end (Tower no. 1107).
[5 empty] | -- | 2018-01-31 | 6:15 | 2018-01-31 | 6:15 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 137.8 kM from Talcher end (Tower no. 338).
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 50.51
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse