## Lines
Element wise availability for the month of April-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
AC Transmission Lines
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | EDAPPON - EDAMON | 2013-04-26 | 16:59 | 2013-04-26 | 17:17 | 0 | 0.3 | 0 | 0 | Tripped at Edappon end only due to dc failure at Edappon (KSEB SS) end. | 100
|  | Sub Total --> |  |  |  | 0 | 0.3 | 0 | 0
2 | KAYAMKULAM - EDAPPON | 2013-04-15 | 16:08 | 2013-04-15 | 16:15 | 0 | 0.11667 | 0 | 0 | Tripped at Edappon end only while changing DC source at Edappon (KSEB SS) end. | 100
|  | 2013-04-26 | 16:59 | 2013-04-26 | 17:14 | 0 | 0.25 | 0 | 0 | Tripped at Edappon end only due to dc failure at Edappon (KSEB SS) end.
|  | 2013-04-30 | 9:13 | 2013-04-30 | 17:21 | 0 | 0 | 0 | 8.1333 | Shut down availed by M/s KSEB for relay testing works at Edappon (KSEB SS) end vide SRLDC code no. CR-04/567.
|  | Sub Total --> |  |  |  | 0 | 0.36667 | 0 | 8.1333
3 | KAYAMKULAM - KUNDRA | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | KAYAMKULAM - POLLAM - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | KAYAMKULAM - POLLAM - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
6 | KUNDRA - EDAMON | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | ARASUR-UDUMALPET-I | 2013-04-24 | 16:39 | 2013-04-24 | 16:39 | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 24.2 KM from Udumalpet end. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | ARASUR-UDUMALPET-II | 2013-04-22 | 16:19 | 2013-04-22 | 17:15 | 0 | 0 | 0 | 0.93333 | Shut down availed for adjusting existing vibration damper between loc. No: 110 & 111 to facilitate OPGW stringing vide SRLDC code no. CR-04/426. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0.93333
9 | BANGALORE - SALEM | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | BHAVINI - ARANI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | BHAVINI - ARANI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | BHAVINI - KANCHEEPURAM I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | BHAVINI - KANCHEEPURAM II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | BHAVINI - SIRUSERI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | BHAVINI - SIRUSERI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | BIDADI - SOMANAHALLI I | 2013-04-08 | 18:54 | 2013-04-21 | 16:39 | 0 | 0 | 0 | 309.75 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/116. | 100
|  | 2013-04-22 | 9:37 | 2013-04-26 | 1:17 | 0 | 0 | 0 | 87.6667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/411.
|  | 2013-04-30 | 8:39 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 15.35 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/562.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 412.7667
17 | BIDADI - SOMANAHALLI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | CHITTOOR - CHENNAI | 2013-04-05 | 20:20 | 2013-04-05 | 22:05 | 1.75 | 0 | 0 | 0 | Shut down availed to isolate defective R phase CVT at Sriperumbudur end vide SRLDC code no. CR-04/58. | 99.7569
|  | Sub Total --> |  |  |  | 1.75 | 0 | 0 | 0
19 | CUDDAPAH - CHITTOOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | CUDDAPAH - KOLAR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
21 | GOOTY - BANGALORE | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | HASSAN - MYSORE I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | HASSAN - MYSORE II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
24 | HASSAN - NELAMANGALA I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
25 | HASSAN - TALAGUPPA I | 2013-04-07 | 3:40 | 2013-04-07 | 4:00 | 0 | 0.33333 | 0 | 0 | Tripped at Talaguppa end only on Y-N (Ph-earth) transient fault. FLR: 245.8 KM from Hassan end. Fault occured in KPTCL portion of the line. Auto reclosure successful at Hassan end. | 100
|  | 2013-04-08 | 13:50 | 2013-04-08 | 17:43 | 0 | 0 | 0 | 3.8833 | Shut down availed by M/s KPTCL for replacement of faulty suspension insulator string at Loc. No. 183 vide SRLDC code no. CR-04/107.
|  | 2013-04-22 | 10:27 | 2013-04-22 | 19:20 | 0 | 0 | 0 | 8.8833 | Shut down availed by M/s KPTCL for configuring and testing of REL 670 relay at Talaguppa end vide SRLDC code no. CR-04/414.
|  | 2013-04-25 | 23:20 | 2013-04-26 | 19:48 | 0 | 20.4667 | 0 | 0 | Tripped due to operation of Reactor back up impedence protection and over voltage protection at Talaguppa (KPTCL SS) end. Line CVT failed at Talaguppa end.
|  | Sub Total --> |  |  |  | 0 | 20.8 | 0 | 12.7667
26 | HOSUR-SALEM | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | KAIGA - NARENDRA I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | KAIGA - NARENDRA II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
29 | KAIGA - SIRSI - I | 2013-04-15 | 12:13 | 2013-04-15 | 16:14 | 0 | 0 | 0 | 4.0167 | Emergency shut down availed by M/s KPTCL for clearing the coconut tree branches between loc No. 174-175 vide SRLDC code no. CR-04/220. | 100
|  | 2013-04-22 | 10:18 | 2013-04-22 | 14:58 | 0 | 0 | 0 | 4.6667 | Shut down availed by M/s NPCIL for distance protection main-I relay testing at Kaiga end vide SRLDC code no. CR-04/413.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.6833
30 | KAIGA - SIRSI - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
31 | KARAIKUDI - MADURAI - I | 2013-04-17 | 10:03 | 2013-04-17 | 14:31 | 4.4667 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-04/277. | 99.3794
|  | 2013-04-24 | 20:09 | 2013-04-24 | 20:24 | 0 | 0 | 0.25 | 0 | Tripped on R-B fault with FLR: 13 kM from Madurai end due to heavy lightning and thunderstorm.
|  | Sub Total --> |  |  |  | 4.4667 | 0 | 0.25 | 0
32 | KOLAR - BANGALORE | 2013-04-09 | 9:58 | 2013-04-09 | 18:17 | 8.3167 | 0 | 0 | 0 | Shut down availed for replacement of Y-phase line CVT and Y-phase CT of 412 bay at Kolar end and AMP works vide SRLDC code no. CR-04/124. | 98.8449
|  | Sub Total --> |  |  |  | 8.3167 | 0 | 0 | 0
33 | KOLAR - CHENNAI | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | KOLAR - HOODY - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | KOLAR - HOODY - II | 2013-04-22 | 18:20 | 2013-04-22 | 19:02 | 0.7 | 0 | 0 | 0 | Hand tripped due to opening of line isolator at Kolar end due to heavy wind & rain. | 99.9028
|  | Sub Total --> |  |  |  | 0.7 | 0 | 0 | 0
36 | KOLAR - HOSUR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | KOLAR - HOSUR - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | MADURAI - TUTICORIN 1 | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | MADURAI - TUTICORIN 2 | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | MADURAI-THIRUNELVELI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | MADURAI-THIRUNELVELI - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
42 | NARENDRA - DAVANGERE I | 2013-04-18 | 8:58 | 2013-04-18 | 19:29 | 0 | 0 | 10.5167 | 0 | Shut down availed for cleaning of polluted suspension and pilot insulators vide SRLDC code no. CR-04/308. | 100
|  | 2013-04-26 | 1:09 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 118.85 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/496.
|  | Sub Total --> |  |  |  | 0 | 0 | 10.5167 | 118.85
43 | NARENDRA - DAVANGERE II | 2013-04-07 | 6:14 | 2013-04-07 | 6:14 | 0 | 0 | 0 | 0 | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR:42.73 KM from Narendra end. | 100
|  | 2013-04-11 | 12:49 | 2013-04-11 | 13:19 | 0 | 0 | 0.5 | 0 | Line tripped on B-N earth fault due to bush fire created by villagers under the line at loc. 195-196.
|  | 2013-04-19 | 8:21 | 2013-04-19 | 18:16 | 0 | 0 | 9.9167 | 0 | Shut down availed for cleaning of polluted suspension and pilot insulators vide SRLDC code no. CR-04/335.
|  | Sub Total --> |  |  |  | 0 | 0 | 10.4167 | 0
44 | NELAMANGALA - BIDADI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
45 | NELAMANGALA - BIDADI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
46 | NELAMANGALA - MYSORE I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
47 | NELAMANGALA - MYSORE II | 2013-04-15 | 21:24 | 2013-04-15 | 21:24 | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 10.9 KM from Mysore end. | 100
|  | 2013-04-29 | 14:55 | 2013-04-29 | 15:07 | 0 | 0.2 | 0 | 0 | Tripped at Nelamangala (KPTCL SS) end only.
|  | Sub Total --> |  |  |  | 0 | 0.2 | 0 | 0
48 | NEYVELI - BAHOOR | 2013-04-22 | 14:58 | 2013-04-22 | 16:06 | 0 | 1.1333 | 0 | 0 | Tripped on fault due to bush fire at Bahour (PED SS) switch yard. Delay in charging attributable to PED vide msg no:849 dated 22.04.13. | 100
|  | 2013-04-27 | 8:41 | 2013-04-27 | 16:09 | 0 | 0 | 0 | 7.4667 | Shut down availed by M/s NLC for routine maintenance works vide SRLDC code no. CR-04/513.
|  | Sub Total --> |  |  |  | 0 | 1.1333 | 0 | 7.4667
49 | NEYVELI - VILLIANUR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
50 | NEYVELI TS II - PUDUCHERRY-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
51 | NEYVELI TS II - PUGALUR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
52 | NEYVELI TS II - TRICHY - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
53 | NEYVELI TS II EXP - PUGALUR | 2013-04-07 | 16:15 | 2013-04-07 | 16:51 | 0 | 0.6 | 0 | 0 | Tripped on receipt of Direct trip signal from Neyveli TS II Expansion end. | 100
|  | Sub Total --> |  |  |  | 0 | 0.6 | 0 | 0
54 | NEYVELI TS-I EXTENSION - TRICHY | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
55 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 2013-04-22 | 8:47 | 2013-04-22 | 16:48 | 0 | 0 | 0 | 8.0167 | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS II end vide SRLDC code no. CR-04/403. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.0167
56 | NEYVELI-SALEM - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
57 | NEYVELI-SALEM - II | 2013-04-18 | 8:43 | 2013-04-18 | 16:58 | 0 | 0 | 0 | 8.25 | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-04/304. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.25
58 | PALAKKAD - TRICHUR I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
59 | PALAKKAD - TRICHUR II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
60 | PUDUCHERRY-SVCHATRAM-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
61 | PUGALUR - MADURAI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
62 | PUGALUR - MADURAI - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
63 | SALEM - UDUMALPET I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
64 | SALEM - UDUMALPET II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
65 | SVCHATRAM-SRIPERUMBUDUR-I | 2013-04-17 | 9:36 | 2013-04-17 | 15:19 | 0 | 0 | 0 | 5.7167 | Shut down availed by M/s TNEB for relay testing works at SV Chatram end vide SRLDC code no. CR-04/273. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 5.7167
66 | THIRUNELVELI - EDAMON - I | 2013-04-22 | 16:18 | 2013-04-22 | 18:34 | 0 | 0 | 0 | 2.2667 | Emergency shut down availed by M/s KSEB to attend arcing near R-Phase female contact of the bus sectionaliser isolator at Edamon (KSEB SS) end. | 100
|  | 2013-04-26 | 14:19 | 2013-04-26 | 14:25 | 0 | 0.1 | 0 | 0 | Tripped at Thirunelveli end only on receipt of direct trip signal from Edamon (KSEB SS) end.
|  | Sub Total --> |  |  |  | 0 | 0.1 | 0 | 2.2667
67 | THIRUNELVELI - EDAMON - II | 2013-04-22 | 16:19 | 2013-04-22 | 18:36 | 0 | 0 | 0 | 2.2833 | Emergency shut down availed by M/s KSEB to attend arcing near R-Phase female contact of the bus sectionaliser isolator at Edamon (KSEB SS) end. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 2.2833
68 | THIRUNELVELI - KUDAMKULAM-I | 2013-04-01 | 0:00 | 2013-04-07 | 9:24 | 0 | 0 | 0 | 153.4 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/518. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 153.4
69 | THIRUNELVELI - KUDAMKULAM-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
70 | THIRUNELVELI - KUDAMKULAM-III |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
71 | THIRUNELVELI - KUDAMKULAM-IV | 2013-04-30 | 0:22 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 23.6333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/556. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 23.6333
72 | THIRUNELVELI - TRIVANDRUM - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
73 | THIRUNELVELI - TRIVANDRUM - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
74 | THIRUNELVELI - UDUMALPET I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
75 | THIRUNELVELI - UDUMALPET II | 2013-04-17 | 16:36 | 2013-04-17 | 16:57 | 0 | 0 | 0.35 | 0 | Line tripped on operation of over voltage protection at Udumalpet end. | 100
|  | 2013-04-23 | 22:39 | 2013-04-23 | 22:45 | 0 | 0 | 0.1 | 0 | Line tripped on operation of over voltage protection at Tirunelveli end. Direct trip signal received at Udumalpet end.
|  | 2013-04-23 | 22:45 | 2013-04-24 | 11:35 | 0 | 0 | 0 | 12.8333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-04/472.
|  | 2013-04-24 | 12:19 | 2013-04-24 | 12:41 | 0 | 0 | 0.36667 | 0 | Line tripped on operation of over voltage protection at Thirunelveli end. Direct trip signal received at Udumalpet end.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.81667 | 12.8333
76 | TRICHUR - KOCHI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
77 | TRICHUR - KOCHI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
78 | TRICHY - KARAIKUDI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
79 | TRICHY - MADURAI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
80 | UDUMALPET - MADURAI | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
81 | UDUMALPET - PALAKKAD I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
82 | UDUMALPET - PALAKKAD II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
83 | VALLUR - KALIVANDAPATTU I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
84 | VALLUR - KALIVANDAPATTU II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## ICT
Element wise availability for the month of April-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Inter Connecting Transformers (ICTs)
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | ARASUR ICT - I | 2013-04-08 | 13:06 | 2013-04-08 | 18:19 | 5.2167 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-04/106. | 99.2755
|  | Sub Total --> |  |  |  | 5.2167 | 0 | 0 | 0
2 | ARASUR ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | BANGALORE ICT - I | 2013-04-13 | 11:59 | 2013-04-13 | 13:23 | 1.4 | 0 | 0 | 0 | Shut down availed for attending hot spot in 220kV side isolator Y-phase terminal connector vide SRLDC code no. CR-04/180. | 99.8054
|  | 2013-04-21 | 11:44 | 2013-04-21 | 12:19 | 0 | 0.58333 | 0 | 0 | 220 kV side tripped due to operation of Bus Bar protection at 220KV SS of M/s KPTCL due to flash over of R-phase insulator of Somanahlli - Tataguni 220 kV line.
|  | Sub Total --> |  |  |  | 1.4 | 0.58333 | 0 | 0
4 | BANGALORE ICT - II | 2013-04-21 | 11:44 | 2013-04-21 | 12:25 | 0 | 0.68333 | 0 | 0 | 221 kV side tripped due to operation of Bus Bar protection at 220KV SS of M/s KPTCL due to flash over of R-phase insulator of Somanahlli - Tataguni 220 kV line. | 100
|  | Sub Total --> |  |  |  | 0 | 0.68333 | 0 | 0
5 | BIDADI ICT-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
6 | BIDADI ICT-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | HASSAN ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | HASSAN ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
9 | HIRIYUR ICT | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | HIRIYUR ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | HOSUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | HOSUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | KALIVANDAPATTU ICT - I | 2013-04-19 | 8:41 | 2013-04-19 | 17:05 | 8.4 | 0 | 0 | 0 | Shut down availed for replacement of Y-Phase bushing due to Tan Delta violation vide SRLDC code no. CR-04/336. | 98.8333
|  | Sub Total --> |  |  |  | 8.4 | 0 | 0 | 0
14 | KALIVANDAPATTU ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | KARAIKUDI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | KARAIKUDI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
17 | KOCHI ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | KOCHI ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | KOLAR ICT | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | KOLAR ICT-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
21 | MADURAI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | MADURAI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | MYSORE ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
24 | MYSORE ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
25 | NARENDRA ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
26 | NARENDRA ICT II | 2013-04-29 | 10:01 | 2013-04-30 | 8:31 | 22.5 | 0 | 0 | 0 | Shut down availed for degassification of Transformer oil vide SRLDC code no. CR-04/545. | 96.875
|  | Sub Total --> |  |  |  | 22.5 | 0 | 0 | 0
27 | PALAKKAD ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | PALAKKAD ICT - II | 2013-04-13 | 9:59 | 2013-04-13 | 12:50 | 0 | 0 | 0 | 2.85 | Shut down availed for making connections for loading the tertiary winding of ICT-2 vide SRLDC code no. CR-04/177. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 2.85
29 | PUDUCHERRY ICT-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
30 | PUDUCHERRY ICT-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
31 | PUGALUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
32 | PUGALUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | THIRUNELVELI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | THIRUNELVELI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | TRICHY ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | TRICHY ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | TRIVANDRUM - ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | TRIVANDRUM - ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | TRIVANDRUM - ICT III | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | UDUMALPET ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | UDUMALPET ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
42 | UDUMALPET ICT - III | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## BR & Sw Reactors
Element wise availability for the month of April-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Bus Reactors & Switchable Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | BANGALORE BUS REACTOR | 2013-04-02 | 7:25 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 688.5833 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 688.5833
2 | BIDADI BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | HASSAN BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | HIRIYUR BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | HOSUR BUS REACTOR - I | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
6 | KARAIKUDI BUS REACTOR - I | 2013-04-15 | 16:13 | 2013-04-22 | 22:36 | 0 | 0 | 0 | 174.3833 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 174.3833
7 | KOCHI BUS REACTOR I | 2013-04-01 | 0:00 | 2013-04-29 | 9:19 | 0 | 0 | 0 | 681.3167 | H/T for voltage regulation | 100
|  | 2013-04-30 | 8:23 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 15.6167 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 696.9333
8 | KOLAR BUS REACTOR - I | 2013-04-02 | 7:21 | 2013-04-21 | 16:54 | 0 | 0 | 0 | 465.55 | H/T for voltage regulation | 100
|  | 2013-04-22 | 9:35 | 2013-04-26 | 0:44 | 0 | 0 | 0 | 87.15 | H/T for voltage regulation
|  | 2013-04-29 | 9:51 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 38.15 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 590.85
9 | MYSORE BUS REACTOR | 2013-04-09 | 9:59 | 2013-04-11 | 13:56 | 0 | 0 | 0 | 51.95 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 51.95
10 | NARENDRA BUS REACTOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | PALAKKAD BUS REACTOR - I | 2013-04-06 | 9:33 | 2013-04-29 | 9:18 | 0 | 0 | 0 | 551.75 | H/T for voltage regulation | 100
|  | 2013-04-30 | 8:17 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 15.7167 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 567.4667
12 | SALEM BUS REACTOR - I | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
13 | SRIPERUMBUDUR BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | THIRUNELVELI BUS REACTOR - I | 2013-04-15 | 15:15 | 2013-04-15 | 17:40 | 0 | 0 | 0 | 2.4167 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 2.4167
15 | THIRUNELVELI BUS REACTOR - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | Kolar Line Reactor at Bangalore | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
17 | Neyveli TS II Exp Line Reactor at Pugalur | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | Neyveli TS II Line Reactor at Pugalur | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | Thirunelveli 1 Line Reactor at Udumalpet | 2013-04-23 | 8:59 | 2013-04-24 | 12:43 | 0 | 0 | 0 | 27.7333 | H/T for voltage regulation | 100
|  | 2013-04-30 | 9:03 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 14.95 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 42.6833
20 | Thirunelveli 2 Line Reactor at Udumalpet | 2013-04-23 | 8:59 | 2013-04-24 | 12:41 | 0 | 0 | 0 | 27.7 | H/T for voltage regulation | 100
|  | 2013-04-30 | 9:04 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 14.9333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 42.6333
21 | Udumalpet 1 Line Reactor at Thirunelveli | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | Udumalpet 2 Line Reactor at Thirunelveli | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | Vallur 1 Line Reactor at Kalivandapattu | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## Non Sw Reactors
Element wise availability for the month of April-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Non Switchable Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | Chittoor Line reactor at Sriperumbudur (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | SV Chatram Line reactor at Sriperumbudur (Non switchable) | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
3 | Trichy Line reactor at Madurai (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | Karaikudi Line reactor at Madurai (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | Bangalore Line reactor at Salem (Non switchable) | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
6 | Neyveli 1 Line reactor at Salem (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | Gooty Line reactor at Bangalore (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | Palakkad 1 Line reactor at Trichur (Non switchable) | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
9 | Palakkad 2 Line reactor at Trichur (Non switchable) | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
10 | Neyveli TS-2 Line reactor at Trichy (Non switchable) | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
11 | Neyveli TS-1 Exp Line reactor at Trichy (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | Thirunelveli 1 Line reactor at Trivendrum (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | Salem 1 Line reactor at Udumalpet (Non switchable) | 2013-04-01 | 0:00 | 2013-05-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
14 | Salem 2 Line reactor at Udumalpet (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## HVDC
Element wise availability for the month of April-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
HVDC POLES
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | TALCHER - KOLAR HVDC POLE - I | 2013-04-01 | 0:00 | 2013-04-02 | 0:27 | 24.45 | 0 | 0 | 0 | Pole I blocked due to damage of Y-phase optical fibre at Talcher end. Emergency Switch-Off (ESOF) signal received at Kolar end. Inter Trip signal 1 transmitted. TCR = 1000 MW. Pole II came on Metallic Return mode. | 96.2477
|  | 2013-04-05 | 18:01 | 2013-04-05 | 18:01 | 0 | 0 | 0 | 0 | LFL and DC line fault recovery sequence operated at 278.52 kM from Kolar end (Tower no. 2930).
|  | 2013-04-23 | 14:26 | 2013-04-23 | 17:00 | 2.5667 | 0 | 0 | 0 | Pole blocked for replacement of broken middle stack insulator of BPI of pole I at Kolar end which was damaged due to heavy wind and rain vide SRLDC code no. CR-04/449.
|  | Sub Total --> |  |  |  | 27.0167 | 0 | 0 | 0
2 | TALCHER - KOLAR HVDC POLE - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0