## Lines
Element wise availability for the month of December-2012
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
AC Transmission Lines
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | Total Available Hours in the month (THM) | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | EDAPPON - EDAMON |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | KAYAMKULAM - EDAPPON | 2012-12-04 | 9:12 | 2012-12-04 | 17:35 | 0 | 0 | 0 | 8.3833 | Shut down availed by M/s NTPC for attending hotspots at Kayamkulam end vide SRLDC code no. CR-12/63. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.3833
3 | KAYAMKULAM - KUNDRA |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | KAYAMKULAM - POLLAM - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | KAYAMKULAM - POLLAM - II | 2012-12-03 | 9:25 | 2012-12-03 | 18:08 | 0 | 0 | 0 | 8.7167 | Shut down availed by M/s NTPC to attend hot spots at Kayamkulam end vide SRLDC code no. CR-12/47. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.7167
6 | KUNDRA - EDAMON |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | ARASUR-UDUMALPET-I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | ARASUR-UDUMALPET-II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
9 | BANGALORE - SALEM |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | BHAVINI - ARANI I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | BHAVINI - ARANI II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | BHAVINI - KANCHEEPURAM I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | BHAVINI - KANCHEEPURAM II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | BHAVINI - SIRUSERI I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | BHAVINI - SIRUSERI II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | BIDADI - SOMANAHALLI I | 2012-12-08 | 7:18 | 2012-12-08 | 12:38 | 0 | 0 | 0 | 5.3333 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/166. | 744 | 100
|  | 2012-12-08 | 16:51 | 2012-12-09 | 19:41 | 0 | 0 | 0 | 26.8333 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/184.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 32.1667
17 | BIDADI - SOMANAHALLI II | 2012-12-12 | 12:41 | 2012-12-12 | 17:29 | 0 | 0 | 0 | 4.8 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/241. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 4.8
18 | CHITTOOR - CHENNAI |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | CUDDAPAH - CHITTOOR | 2012-12-29 | 23:57 | 2012-12-30 | 0:55 | 0 | 0 | 0.96667 | 0 | Line tripped on operation of over voltage protection at Chittoor end. Direct trip signal received at Cuddapa end. | 743.0333 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0.96667 | 0
20 | CUDDAPAH - KOLAR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
21 | GOOTY - BANGALORE | 2012-12-21 | 8:23 | 2012-12-21 | 8:36 | 0.21667 | 0 | 0 | 0 | Tripped on Y-N (Ph-earth) transient fault. FLR: 14.92 KM from Bangalore end. Auto reclosure successful at Bangalore end. | 744 | 99.9709
|  | Sub Total --> |  |  |  | 0.21667 | 0 | 0 | 0
22 | HASSAN - MYSORE I | 2012-12-01 | 9:49 | 2012-12-01 | 17:58 | 0 | 0 | 0 | 8.15 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/05. | 744 | 97.6949
|  | 2012-12-03 | 9:55 | 2012-12-03 | 18:37 | 0 | 0 | 0 | 8.7 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/50
|  | 2012-12-04 | 10:13 | 2012-12-04 | 18:40 | 0 | 0 | 0 | 8.45 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/69
|  | 2012-12-04 | 18:40 | 2012-12-05 | 18:35 | 0 | 0 | 0 | 23.9167 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/91.
|  | 2012-12-07 | 1:11 | 2012-12-07 | 17:31 | 0 | 0 | 0 | 16.3333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/135.
|  | 2012-12-10 | 8:58 | 2012-12-10 | 18:28 | 0 | 0 | 0 | 9.5 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/205
|  | 2012-12-11 | 9:03 | 2012-12-11 | 18:38 | 0 | 0 | 0 | 9.5833 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/217
|  | 2012-12-12 | 9:05 | 2012-12-12 | 18:44 | 0 | 0 | 0 | 9.65 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/232
|  | 2012-12-13 | 9:50 | 2012-12-13 | 17:56 | 0 | 0 | 0 | 8.1 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/252
|  | 2012-12-14 | 9:28 | 2012-12-14 | 17:02 | 0 | 0 | 0 | 7.5667 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/272
|  | 2012-12-15 | 9:33 | 2012-12-15 | 17:52 | 0 | 0 | 0 | 8.3167 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/300
|  | 2012-12-16 | 8:29 | 2012-12-16 | 16:01 | 0 | 0 | 0 | 7.5333 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/319
|  | 2012-12-17 | 9:31 | 2012-12-17 | 18:00 | 0 | 0 | 0 | 8.4833 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/359
|  | 2012-12-18 | 10:10 | 2012-12-18 | 17:12 | 0 | 0 | 0 | 7.0333 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/384
|  | 2012-12-19 | 8:09 | 2012-12-19 | 16:52 | 0 | 0 | 0 | 8.7167 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/402
|  | 2012-12-20 | 8:07 | 2012-12-20 | 17:36 | 0 | 0 | 0 | 9.4833 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/423
|  | 2012-12-21 | 8:29 | 2012-12-22 | 1:38 | 17.15 | 0 | 0 | 0 | Line tripped on Y-B fault due to snapping of top phase conductor between Location No. 260 & 261.
|  | 2012-12-22 | 1:38 | 2012-12-22 | 7:04 | 0 | 0 | 0 | 5.4333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/746A.
|  | 2012-12-22 | 9:29 | 2012-12-22 | 18:04 | 0 | 0 | 0 | 8.5833 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/468
|  | 2012-12-23 | 9:50 | 2012-12-23 | 18:58 | 0 | 0 | 0 | 9.1333 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/484
|  | 2012-12-24 | 9:44 | 2012-12-24 | 17:30 | 0 | 0 | 0 | 7.7667 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/505
|  | Sub Total --> |  |  |  | 17.15 | 0 | 0 | 190.4333
23 | HASSAN - MYSORE II | 2012-12-21 | 0:03 | 2012-12-21 | 7:17 | 0 | 0 | 0 | 7.2333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/440. | 744 | 99.8096
|  | 2012-12-21 | 8:07 | 2012-12-21 | 9:32 | 1.4167 | 0 | 0 | 0 | Shut down availed for repair of damaged conductor between Location No. 235 & 236 vide SRLDC code no. CR-12/448.
|  | Sub Total --> |  |  |  | 1.4167 | 0 | 0 | 7.2333
24 | HASSAN - NELAMANGALA I | 2012-12-04 | 0:05 | 2012-12-04 | 6:35 | 0 | 0 | 0 | 6.5 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/62. | 742.8 | 100
|  | 2012-12-04 | 0:00 | 2012-12-04 | 0:05 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | 2012-12-05 | 0:01 | 2012-12-05 | 0:06 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | 2012-12-05 | 0:06 | 2012-12-05 | 6:39 | 0 | 0 | 0 | 6.55 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/98.
|  | 2012-12-17 | 0:00 | 2012-12-17 | 0:05 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | 2012-12-17 | 0:05 | 2012-12-17 | 7:24 | 0 | 0 | 0 | 7.3167 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/563.
|  | 2012-12-21 | 0:01 | 2012-12-21 | 0:23 | 0 | 0 | 0.36667 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | 2012-12-29 | 23:56 | 2012-12-30 | 0:31 | 0 | 0 | 0.58333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | Sub Total --> |  |  |  | 0 | 0 | 1.2 | 20.3667
25 | HASSAN - TALAGUPPA I | 2012-12-06 | 23:52 | 2012-12-07 | 7:33 | 0 | 0 | 0 | 7.6833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/133. | 738.8833 | 100
|  | 2012-12-16 | 10:29 | 2012-12-16 | 15:36 | 0 | 5.1167 | 0 | 0 | Line tripped at Talaguppa end only due to disturbance at Talaguppa KPTCL SS.
|  | Sub Total --> |  |  |  | 0 | 5.1167 | 0 | 7.6833
26 | HOSUR-SALEM |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | KAIGA - NARENDRA I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | KAIGA - NARENDRA II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
29 | KAIGA - SIRSI - I | 2012-12-05 | 23:53 | 2012-12-06 | 7:42 | 0 | 0 | 0 | 7.8167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/101. | 744 | 100
|  | 2012-12-07 | 22:02 | 2012-12-08 | 9:24 | 0 | 0 | 0 | 11.3667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/163.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 19.1833
30 | KAIGA - SIRSI - II | 2012-12-06 | 22:35 | 2012-12-07 | 9:21 | 0 | 0 | 0 | 10.7667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/127. | 743.0333 | 100
|  | 2012-12-11 | 11:51 | 2012-12-11 | 12:49 | 0 | 0.96667 | 0 | 0 | Tripped on R-N (Ph-earth) transient fault. FLR: 93.6 KM from Kaiga end. Fault occured in KPTCL portion of the line.
|  | Sub Total --> |  |  |  | 0 | 0.96667 | 0 | 10.7667
31 | KALIVANDAPATTU - SRIPERUMBUDUR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
32 | KARAIKUDI - MADURAI - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | KOLAR - BANGALORE |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | KOLAR - HOODY - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | KOLAR - HOODY - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | KOLAR - HOSUR - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | KOLAR - HOSUR - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | KOLAR - KALIVANDAPATTU |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | MADURAI - TUTICORIN JV TPS 1 |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | MADURAI - TUTICORIN JV TPS 2 |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | MADURAI-THIRUNELVELI - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
42 | MADURAI-THIRUNELVELI - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
43 | NARENDRA - DAVANGERE I | 2012-12-01 | 0:00 | 41249 | 12:05 | 0 | 0 | 0 | 132.0833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/661. | 744 | 100
|  | 2012-12-07 | 21:56 | 41251 | 9:41 | 0 | 0 | 0 | 11.75 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/162.
|  | 2012-12-19 | 20:52 | 41272 | 10:42 | 0 | 0 | 0 | 229.8333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/418.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 373.6667
44 | NARENDRA - DAVANGERE II | 2012-12-06 | 22:35 | 2012-12-07 | 9:15 | 0 | 0 | 0 | 10.6667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/128. | 744 | 100
|  | 2012-12-14 | 22:48 | 2012-12-19 | 15:21 | 0 | 0 | 0 | 112.55 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/297.
|  | 2012-12-30 | 17:26 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 30.5667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/586.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 153.7833
45 | NELAMANGALA - BIDADI I | 2012-12-08 | 7:19 | 2012-12-08 | 12:20 | 0 | 0 | 0 | 5.0167 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/165. | 744 | 100
|  | 2012-12-08 | 17:02 | 2012-12-09 | 20:14 | 0 | 0 | 0 | 27.2 | Shut down availed for installation of OPGW vide SRLDC code no. CR-12/185.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 32.2167
46 | NELAMANGALA - BIDADI II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
47 | NELAMANGALA - MYSORE I | 2012-12-05 | 23:57 | 2012-12-06 | 7:33 | 0 | 0 | 0 | 7.6 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/102. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 7.6
48 | NELAMANGALA - MYSORE II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
49 | NEYVELI - BAHOOR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
50 | NEYVELI - VILLIANUR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
51 | NEYVELI TS II - PUDUCHERRY-I | 2012-12-27 | 7:20 | 2012-12-27 | 16:06 | 0 | 0 | 0 | 8.7667 | Shut down availed by M/s NLC to attend the snapped strands of ACSR conductor in 400kV bus-2 at Neyveli TS-2 end vide SRLDC code no. CR-12/531. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.7667
52 | NEYVELI TS II - PUGALUR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
53 | NEYVELI TS II - TRICHY - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
54 | NEYVELI TS II EXP - PUGALUR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
55 | NEYVELI TS-I EXTENSION - TRICHY |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
56 | NEYVELI TS-II - NEYVELI TS-I EXPANSION |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
57 | NEYVELI-SALEM - I | 2012-12-29 | 9:04 | 2012-12-29 | 15:52 | 0 | 0 | 0 | 6.8 | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-12/555. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 6.8
58 | NEYVELI-SALEM - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
59 | PALAKKAD - TRICHUR I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
60 | PALAKKAD - TRICHUR II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
61 | PUDUCHERRY-SUNGUVARCHATRAM-I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
62 | PUGALUR - MADURAI - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
63 | PUGALUR - MADURAI - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
64 | SALEM - UDUMALPET I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
65 | SALEM - UDUMALPET II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
66 | SUNGUVARCHATRAM-SRIPERUMBUDUR-I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
67 | THIRUNELVELI - EDAMON - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
68 | THIRUNELVELI - EDAMON - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
69 | THIRUNELVELI - KUDAMKULAM-I | 2012-12-07 | 21:53 | 2012-12-14 | 11:50 | 0 | 0 | 0 | 157.95 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/161. | 744 | 100
|  | 2012-12-21 | 13:11 | 2012-12-26 | 23:05 | 0 | 0 | 0 | 129.9 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/462.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 287.85
70 | THIRUNELVELI - KUDAMKULAM-II | 2012-12-01 | 0:00 | 2012-12-07 | 15:43 | 0 | 0 | 0 | 159.7167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/498. | 744 | 100
|  | 2012-12-14 | 13:45 | 2012-12-21 | 11:25 | 0 | 0 | 0 | 165.6667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/282.
|  | 2012-12-26 | 23:09 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 120.85 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/530.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 446.2333
71 | THIRUNELVELI - KUDAMKULAM-III | 2012-12-01 | 0:00 | 2012-12-06 | 17:03 | 0 | 0 | 0 | 137.05 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/493. | 744 | 100
|  | 2012-12-13 | 17:19 | 2012-12-22 | 11:08 | 0 | 0 | 0 | 209.8167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/265.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 346.8667
72 | THIRUNELVELI - KUDAMKULAM-IV | 2012-12-06 | 17:13 | 2012-12-13 | 17:12 | 0 | 0 | 0 | 167.9833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/119. | 744 | 100
|  | 2012-12-23 | 22:43 | 2012-12-31 | 10:02 | 0 | 0 | 0 | 179.3167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/496.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 347.3
73 | THIRUNELVELI - TRIVANDRUM - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
74 | THIRUNELVELI - TRIVANDRUM - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
75 | THIRUNELVELI - UDUMALPET I | 2012-12-01 | 0:00 | 2012-12-05 | 15:43 | 0 | 0 | 0 | 111.7167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/657. | 744 | 100
|  | 2012-12-15 | 22:09 | 2012-12-17 | 9:41 | 0 | 0 | 0 | 35.5333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/316.
|  | 2012-12-30 | 21:56 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 26.0667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/590.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 173.3167
76 | THIRUNELVELI - UDUMALPET II | 2012-12-06 | 23:21 | 2012-12-13 | 10:34 | 0 | 0 | 0 | 155.2167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/131. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 155.2167
77 | TRICHUR - KOCHI I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
78 | TRICHUR - KOCHI II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
79 | TRICHY - KARAIKUDI - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
80 | TRICHY - MADURAI - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
81 | UDUMALPET - MADURAI |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
82 | UDUMALPET - PALAKKAD I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
83 | UDUMALPET - PALAKKAD II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## ICT
Element wise availability for the month of December-2012
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Inter Connecting Transformers (ICTs)
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | Total Available Hours in the month (THM) | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | ARASUR ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | ARASUR ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | BANGALORE ICT - I | 2012-12-05 | 10:42 | 2012-12-05 | 10:52 | 0.16667 | 0 | 0 | 0 | Tripped while availing 400 kV bus-2 shut down at Somanahalli SS due to faulty bus voltage selection relay. | 744 | 99.9776
|  | 2012-12-27 | 10:25 | 2012-12-27 | 16:20 | 0 | 0 | 0 | 5.9167 | Shut down availed by M/s KPTCL to replace 220 kV GOS at 220kV Somanahalli SS vide SRLDC code no. CR-12/534.
|  | Sub Total --> |  |  |  | 0.16667 | 0 | 0 | 5.9167
4 | BANGALORE ICT - II | 2012-12-31 | 16:32 | 2012-12-31 | 17:22 | 0.83333 | 0 | 0 | 0 | Shut down availed for combination changing vide SRLDC code no. CR-12/603. | 744 | 99.888
|  | Sub Total --> |  |  |  | 0.83333 | 0 | 0 | 0
5 | BIDADI ICT-I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
6 | HASSAN ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | HASSAN ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | HIRIYUR ICT |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
9 | HIRIYUR ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | HOSUR ICT - I | 2012-12-23 | 11:05 | 2012-12-23 | 15:57 | 4.8667 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/486. | 744 | 99.3459
|  | Sub Total --> |  |  |  | 4.8667 | 0 | 0 | 0
11 | HOSUR ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | KALIVANDAPATTU ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | KALIVANDAPATTU ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | KARAIKUDI ICT - I | 2012-12-04 | 10:10 | 2012-12-04 | 14:30 | 4.3333 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/67. | 744 | 99.4176
|  | Sub Total --> |  |  |  | 4.3333 | 0 | 0 | 0
15 | KARAIKUDI ICT - II | 2012-12-05 | 9:57 | 2012-12-05 | 14:02 | 4.0833 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/83. | 744 | 99.4512
|  | Sub Total --> |  |  |  | 4.0833 | 0 | 0 | 0
16 | KOCHI ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
17 | KOCHI ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | KOLAR ICT |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | KOLAR ICT-II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | MADURAI ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
21 | MADURAI ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | MYSORE ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | MYSORE ICT II | 2012-12-23 | 10:12 | 2012-12-23 | 14:19 | 4.1167 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/485. | 744 | 99.4467
|  | Sub Total --> |  |  |  | 4.1167 | 0 | 0 | 0
24 | NARENDRA ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
25 | NARENDRA ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
26 | PALAKKAD ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | PALAKKAD ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | PUDUCHERRY ICT-I | 2012-12-18 | 10:08 | 2012-12-18 | 15:18 | 5.1667 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/383. | 744 | 99.3056
|  | Sub Total --> |  |  |  | 5.1667 | 0 | 0 | 0
29 | PUDUCHERRY ICT-II | 2012-12-19 | 10:00 | 2012-12-19 | 14:53 | 4.8833 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/404. | 744 | 99.3436
|  | Sub Total --> |  |  |  | 4.8833 | 0 | 0 | 0
30 | PUGALUR ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
31 | PUGALUR ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
32 | THIRUNELVELI ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | THIRUNELVELI ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | TRICHY ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | TRICHY ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | TRIVANDRUM - ICT I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | TRIVANDRUM - ICT II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | TRIVANDRUM - ICT III |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | UDUMALPET ICT - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | UDUMALPET ICT - II |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | UDUMALPET ICT - III |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## Reactors
Element wise availability for the month of December-2012
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Bus Reactors & Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | Total Available Hours in the month (THM) | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | BANGALORE BUS REACTOR | 2012-12-03 | 9:55 | 2012-12-03 | 22:52 | 0 | 0 | 0 | 12.95 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/48. | 744 | 100
|  | 2012-12-04 | 7:29 | 2012-12-04 | 21:42 | 0 | 0 | 0 | 14.2167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/64.
|  | 2012-12-07 | 7:23 | 2012-12-07 | 22:00 | 0 | 0 | 0 | 14.6167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/137.
|  | 2012-12-08 | 8:26 | 2012-12-08 | 23:04 | 0 | 0 | 0 | 14.6333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/168.
|  | 2012-12-09 | 8:16 | 2012-12-09 | 22:06 | 0 | 0 | 0 | 13.8333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/190.
|  | 2012-12-10 | 8:35 | 2012-12-10 | 23:23 | 0 | 0 | 0 | 14.8 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/204.
|  | 2012-12-11 | 8:03 | 2012-12-11 | 23:03 | 0 | 0 | 0 | 15 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/215.
|  | 2012-12-12 | 8:46 | 2012-12-13 | 22:12 | 0 | 0 | 0 | 37.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/229.
|  | 2012-12-14 | 10:00 | 2012-12-15 | 22:26 | 0 | 0 | 0 | 36.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/275.
|  | 2012-12-17 | 7:26 | 2012-12-19 | 23:45 | 0 | 0 | 0 | 64.3167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/349.
|  | 2012-12-20 | 9:09 | 2012-12-21 | 0:29 | 0 | 0 | 0 | 15.3333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/424.
|  | 2012-12-22 | 9:51 | 2012-12-23 | 0:17 | 0 | 0 | 0 | 14.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/470.
|  | 2012-12-24 | 9:11 | 2012-12-30 | 22:04 | 0 | 0 | 0 | 156.8833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/499.
|  | 2012-12-31 | 8:46 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 15.2333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/591.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 440.1167
2 | BIDADI BUS REACTOR - I | 2012-12-04 | 7:25 | 2012-12-04 | 21:38 | 0 | 0 | 0 | 14.2167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/65. | 744 | 100
|  | 2012-12-07 | 7:14 | 2012-12-07 | 21:47 | 0 | 0 | 0 | 14.55 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/138.
|  | 2012-12-12 | 9:06 | 2012-12-15 | 22:07 | 0 | 0 | 0 | 85.0167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/231.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 113.7833
2 | HASSAN BUS REACTOR - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | HIRIYUR BUS REACTOR - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | HOSUR BUS REACTOR - I | 2012-12-03 | 9:57 | 2012-12-04 | 21:38 | 0 | 0 | 0 | 35.6833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/49. | 744 | 100
|  | 2012-12-07 | 9:13 | 2012-12-07 | 21:45 | 0 | 0 | 0 | 12.5333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/143.
|  | 2012-12-08 | 8:25 | 2012-12-08 | 22:51 | 0 | 0 | 0 | 14.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/169.
|  | 2012-12-09 | 8:18 | 2012-12-09 | 21:36 | 0 | 0 | 0 | 13.3 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/191.
|  | 2012-12-10 | 8:25 | 2012-12-10 | 23:09 | 0 | 0 | 0 | 14.7333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/203.
|  | 2012-12-11 | 7:50 | 2012-12-13 | 21:56 | 0 | 0 | 0 | 62.1 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/214.
|  | 2012-12-14 | 9:50 | 2012-12-15 | 22:08 | 0 | 0 | 0 | 36.3 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/276.
|  | 2012-12-16 | 7:08 | 2012-12-16 | 21:55 | 0 | 0 | 0 | 14.7833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/318.
|  | 2012-12-17 | 7:22 | 2012-12-19 | 23:30 | 0 | 0 | 0 | 64.1333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/348.
|  | 2012-12-20 | 8:52 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 279.1333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/425.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 547.1333
6 | KARAIKUDI BUS REACTOR - I | 2012-12-16 | 9:50 | 2012-12-16 | 22:13 | 0 | 0 | 0 | 12.3833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/323. | 744 | 100
|  | 2012-12-17 | 9:27 | 2012-12-17 | 22:11 | 0 | 0 | 0 | 12.7333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/354.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 25.1167
7 | KOCHI BUS REACTOR I | 2012-12-08 | 9:08 | 2012-12-09 | 21:51 | 0 | 0 | 0 | 36.7167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/173. | 744 | 100
|  | 2012-12-17 | 9:15 | 2012-12-17 | 22:07 | 0 | 0 | 0 | 12.8667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/356.
|  | 2012-12-24 | 9:42 | 2012-12-28 | 9:08 | 0 | 0 | 0 | 95.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/504.
|  | 2012-12-29 | 9:25 | 2012-12-30 | 2:31 | 0 | 0 | 0 | 17.1 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/559.
|  | 2012-12-31 | 16:17 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 7.7167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/601.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 169.8333
8 | KOLAR BUS REACTOR - I | 2012-12-11 | 9:50 | 2012-12-11 | 23:00 | 0 | 0 | 0 | 13.1667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/220. | 744 | 100
|  | 2012-12-12 | 9:30 | 2012-12-13 | 1:54 | 0 | 0 | 0 | 16.4 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/234.
|  | 2012-12-15 | 9:47 | 2012-12-15 | 22:05 | 0 | 0 | 0 | 12.3 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/303.
|  | 2012-12-24 | 8:56 | 2012-12-30 | 4:05 | 0 | 0 | 0 | 139.15 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/500.
|  | 2012-12-31 | 8:50 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 15.1667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/595.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 196.1833
9 | MYSORE BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | NARENDRA BUS REACTOR |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | PALAKKAD BUS REACTOR - I | 2012-12-03 | 10:20 | 2012-12-04 | 21:56 | 0 | 0 | 0 | 35.6 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/51. | 744 | 100
|  | 2012-12-08 | 9:05 | 2012-12-09 | 21:50 | 0 | 0 | 0 | 36.75 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/172.
|  | 2012-12-16 | 9:46 | 2012-12-16 | 22:13 | 0 | 0 | 0 | 12.45 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/326.
|  | 2012-12-17 | 9:24 | 2012-12-17 | 21:52 | 0 | 0 | 0 | 12.4667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/353.
|  | 2012-12-20 | 10:11 | 2012-12-20 | 21:47 | 0 | 0 | 0 | 11.6 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/430.
|  | 2012-12-24 | 9:35 | 2012-12-28 | 9:13 | 0 | 0 | 0 | 95.6333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/503.
|  | 2012-12-29 | 9:18 | 2012-12-30 | 2:11 | 0 | 0 | 0 | 16.8833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/558.
|  | 2012-12-31 | 16:15 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 7.75 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/600.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 229.1333
12 | SALEM BUS REACTOR - I | 2012-12-11 | 9:47 | 2012-12-13 | 22:04 | 0 | 0 | 0 | 60.2833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/221. | 744 | 100
|  | 2012-12-16 | 9:43 | 2012-12-16 | 22:04 | 0 | 0 | 0 | 12.35 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/322.
|  | 2012-12-22 | 9:51 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 230.15 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/471.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 302.7833
13 | SRIPERUMBUDUR BUS REACTOR - I |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | THIRUNELVELI BUS REACTOR - I | 2012-12-19 | 10:01 | 2012-12-19 | 17:14 | 0 | 0 | 0 | 7.2167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/405. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 7.2167
15 | THIRUNELVELI BUS REACTOR - II | 2012-12-19 | 10:02 | 2012-12-19 | 17:13 | 0 | 0 | 0 | 7.1833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/406. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 7.1833
16 | Kolar Line Reactor at Bangalore | 2012-12-01 | 0:00 | 2012-12-23 | 22:39 | 0 | 0 | 0 | 550.65 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-11/472/2. | 744 | 100
|  | 2012-12-31 | 16:13 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 7.7833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/602.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 558.4334
17 | Kolar Line Reactor at Kalivandapattu |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | Neyveli TS II Exp Line Reactor at Pugalur |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | Neyveli TS II Line Reactor at Pugalur |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | Thirunelveli 1 Line Reactor at Udumalpet | 2012-12-08 | 9:10 | 2012-12-09 | 21:45 | 0 | 0 | 0 | 36.5833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/170. | 744 | 100
|  | 2012-12-13 | 9:45 | 2012-12-14 | 23:03 | 0 | 0 | 0 | 37.3 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/251.
|  | 2012-12-16 | 9:42 | 2012-12-16 | 22:08 | 0 | 0 | 0 | 12.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/324.
|  | 2012-12-20 | 9:52 | 2012-12-20 | 21:44 | 0 | 0 | 0 | 11.8667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/428.
|  | 2012-12-24 | 9:32 | 2012-12-28 | 9:07 | 0 | 0 | 0 | 95.5833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/501.
|  | 2012-12-29 | 9:09 | 2012-12-30 | 6:32 | 0 | 0 | 0 | 21.3833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/556.
|  | 2012-12-31 | 8:34 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 15.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/593.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 230.5833
21 | Thirunelveli 2 Line Reactor at Udumalpet | 2012-12-08 | 9:10 | 2012-12-09 | 21:47 | 0 | 0 | 0 | 36.6167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/171. | 744 | 100
|  | 2012-12-12 | 9:41 | 2012-12-14 | 23:04 | 0 | 0 | 0 | 61.3833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/234A.
|  | 2012-12-16 | 9:43 | 2012-12-16 | 22:12 | 0 | 0 | 0 | 12.4833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/325.
|  | 2012-12-17 | 9:00 | 2012-12-17 | 22:05 | 0 | 0 | 0 | 13.0833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/352.
|  | 2012-12-20 | 9:53 | 2012-12-20 | 21:45 | 0 | 0 | 0 | 11.8667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/429.
|  | 2012-12-24 | 9:33 | 2012-12-28 | 9:09 | 0 | 0 | 0 | 95.6 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/502.
|  | 2012-12-29 | 9:10 | 2012-12-30 | 6:32 | 0 | 0 | 0 | 21.3667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/557.
|  | 2012-12-31 | 8:34 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 15.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/594.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 267.8333
22 | Udumalpet 1 Line Reactor at Thirunelveli |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | Udumalpet 2 Line Reactor at Thirunelveli |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
24 | Chittoor Line reactor at Sriperumbudur (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
25 | SV Chatram Line reactor at Sriperumbudur (Non switchable) | 2012-12-01 | 0:00 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 744 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 744
26 | Trichy Line reactor at Madurai (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | Karaikudi Line reactor at Madurai (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | Bangalore Line reactor at Salem (Non switchable) | 2012-12-01 | 0:00 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 744 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 744
29 | Neyveli 1 Line reactor at Salem (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
30 | Gooty Line reactor at Bangalore (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
31 | Palakkad 1 Line reactor at Trichur (Non switchable) | 2012-12-01 | 0:00 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 744 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 744
32 | Palakkad 2 Line reactor at Trichur (Non switchable) | 2012-12-01 | 0:00 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 744 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 744
33 | Neyveli TS-2 Line reactor at Trichy (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | Neyveli TS-1 Exp Line reactor at Trichy (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | Thirunelveli 1 Line reactor at Trivendrum (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | Salem 1 Line reactor at Udumalpet (Non switchable) | 2012-12-01 | 0:00 | 2013-01-01 | 0:00 | 0 | 0 | 0 | 744 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 744
37 | Salem 2 Line reactor at Udumalpet (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 744 | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## HVDC
Element wise availability for the month of December-2012
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
HVDC POLES
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | Total Available Hours in the month (THM) | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | TALCHER - KOLAR HVDC POLE - I | 2012-12-02 | 6:20 | 2012-12-02 | 20:17 | 13.95 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/29. | 744 | 98.0332
|  | 2012-12-17 | 12:41 | 2012-12-17 | 13:22 | 0.68333 | 0 | 0 | 0 | Pole blocked on operation of last feeder trip protection, while testing main CB of converter transformer I.
|  | Sub Total --> |  |  |  | 14.6333 | 0 | 0 | 0
2 | TALCHER - KOLAR HVDC POLE - II | 2012-12-02 | 6:22 | 2012-12-02 | 19:55 | 13.55 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-12/30. | 744 | 98.1788
|  | Sub Total --> |  |  |  | 13.55 | 0 | 0 | 0