## Lines
Element wise availability for the month of June-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
AC Transmission Lines
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | EDAPPON - EDAMON | 2013-06-13 | 10:35 | 2013-06-13 | 22:44 | 0 | 0 | 0 | 12.15 | Shut down availed by M/s KSEB for replacing the hanging conductor of 220 kV upper bus at Edamon end vide SRLDC code no. CR-06/348. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 12.15
2 | KAYAMKULAM - EDAPPON | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | KAYAMKULAM - KUNDRA | 2013-06-21 | 10:10 | 2013-06-21 | 18:30 | 0 | 0 | 0 | 8.3333 | Shut down availed by M/s KSEB for relay testing works at Kundra end vide SRLDC code no. CR-06/665. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.3333
4 | KAYAMKULAM - POLLAM - I | 2013-06-18 | 10:11 | 2013-06-18 | 14:44 | 0 | 0 | 0 | 4.55 | Shut down availed by M/s KSEB for relay testing works vide SRLDC code no. CR-06/554. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 4.55
5 | KAYAMKULAM - POLLAM - II | 2013-06-19 | 10:29 | 2013-06-19 | 15:06 | 0 | 0 | 0 | 4.6167 | Shut down availed by M/s KSEB for relay testing works vide SRLDC code no. CR-06/602. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 4.6167
6 | KUNDRA - EDAMON | 2013-06-24 | 12:37 | 2013-06-24 | 15:45 | 0 | 0 | 0 | 3.1333 | Shut down availed by M/s KSEB for rectification of glow on lower bus at Edamon end vide SRLDC code no. CR-06/743. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 3.1333
7 | ARASUR-UDUMALPET-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | ARASUR-UDUMALPET-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
9 | BANGALORE - SALEM | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | BHAVINI - ARANI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | BHAVINI - ARANI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | BHAVINI - KANCHEEPURAM I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | BHAVINI - KANCHEEPURAM II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | BHAVINI - SIRUSERI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | BHAVINI - SIRUSERI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | BIDADI - SOMANAHALLI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
17 | BIDADI - SOMANAHALLI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | CHITTOOR - CHENNAI | 2013-06-14 | 13:35 | 2013-06-14 | 14:05 | 0.5 | 0 | 0 | 0 | Shut down availed for connecting line CVT HF cable to LMU unit of B phase CVT vide SRLDC code no. CR-06/404. | 99.8912
|  | 2013-06-21 | 9:17 | 2013-06-21 | 9:34 | 0.28333 | 0 | 0 | 0 | Tripped on R-N (Ph-earth) transient fault during tower erection works of new Nellore-Thiruvelam 400kV D/C line.
|  | Sub Total --> |  |  |  | 0.78333 | 0 | 0 | 0
19 | CUDDAPAH - CHITTOOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | CUDDAPAH - KOLAR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
21 | GOOTY - BANGALORE | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | HASSAN - MYSORE I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | HASSAN - MYSORE II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
24 | HASSAN - NELAMANGALA I | 2013-06-02 | 14:54 | 2013-06-03 | 8:02 | 0 | 0 | 0 | 17.1333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/38. | 100
|  | 2013-06-07 | 23:26 | 2013-06-08 | 6:38 | 0 | 0 | 0 | 7.2 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/193.
|  | 2013-06-07 | 0:36 | 2013-06-07 | 6:55 | 0 | 0 | 0 | 6.3167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/172.
|  | 2013-06-24 | 0:05 | 2013-06-24 | 6:25 | 0 | 0 | 0 | 6.3333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/817A.
|  | 2013-06-24 | 0:00 | 2013-06-24 | 0:05 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.083333 | 36.9833
25 | HASSAN - TALAGUPPA I | 2013-06-12 | 9:41 | 2013-06-12 | 19:06 | 0 | 0 | 0 | 9.4167 | Shut down availed by M/s KPTCL for replacement of B phase CVT at Talaguppa end vide SRLDC code no. CR-06/311. | 100
|  | 2013-06-13 | 14:00 | 2013-06-13 | 15:09 | 0 | 0 | 1.15 | 0 | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end.
|  | Sub Total --> |  |  |  | 0 | 0 | 1.15 | 9.4167
26 | HOSUR-SALEM | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | KAIGA - NARENDRA I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | KAIGA - NARENDRA II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
29 | KAIGA - SIRSI - I | 2013-06-01 | 6:20 | 2013-06-10 | 9:15 | 0 | 0 | 0 | 218.9167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/01. | 100
|  | 2013-06-18 | 9:11 | 2013-06-18 | 19:10 | 0 | 0 | 0 | 9.9833 | Shut down availed by M/s KPTCL for quarterly maintenance works at Guttur end vide SRLDC code no. CR-06/544.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 228.9
30 | KAIGA - SIRSI - II | 2013-06-24 | 23:17 | 2013-06-25 | 7:55 | 0 | 0 | 0 | 8.6333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/760. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.6333
31 | KARAIKUDI - MADURAI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
32 | KOLAR - BANGALORE | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | KOLAR - CHENNAI | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | KOLAR - HOODY - I | 2013-06-16 | 8:26 | 2013-06-16 | 18:28 | 0 | 0 | 0 | 10.0333 | Shut down availed by M/s KPTCL for works related to additional 500MVA ICT at Hoody end vide SRLDC code no. CR-06/467. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 10.0333
35 | KOLAR - HOODY - II | 2013-06-16 | 8:27 | 2013-06-16 | 18:25 | 0 | 0 | 0 | 9.9667 | Shut down availed by M/s KPTCL for works related to additional 500MVA ICT at Hoody end vide SRLDC code no. CR-06/468. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 9.9667
36 | KOLAR - HOSUR - I | 2013-06-28 | 8:38 | 2013-06-28 | 17:45 | 9.1167 | 0 | 0 | 0 | Shut down availed for isolator modification works at Kolar end vide SRLDC code no. CR-06/865. | 98.7338
|  | Sub Total --> |  |  |  | 9.1167 | 0 | 0 | 0
37 | KOLAR - HOSUR - II | 2013-06-29 | 8:00 | 2013-06-29 | 15:30 | 7.5 | 0 | 0 | 0 | Shut down availed for isolator modification works at Kolar end vide SRLDC code no. CR-06/878. | 98.9583
|  | Sub Total --> |  |  |  | 7.5 | 0 | 0 | 0
38 | MADURAI - TUTICORIN 1 | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | MADURAI - TUTICORIN 2 | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | MADURAI-THIRUNELVELI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | MADURAI-THIRUNELVELI - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
42 | NARENDRA - DAVANGERE I | 2013-06-01 | 0:00 | 2013-06-06 | 9:12 | 0 | 0 | 0 | 129.2 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/474. | 100
|  | 2013-06-22 | 5:53 | 2013-06-22 | 6:01 | 0 | 0 | 0.13333 | 0 | Tripped at Davanagere end only on Y-N (Ph-earth) transient fault due to a monkey climbed the tower at loc. 162 and died due to electrocution. Auto reclosure successful at Narendra end.
|  | 2013-06-22 | 6:01 | 2013-06-22 | 6:22 | 0 | 0.35 | 0 | 0 | Charging delayed by KPTCL Davanagere SS vide message no. CP-06/765.
|  | 2013-06-22 | 22:55 | 2013-06-24 | 7:55 | 0 | 0 | 0 | 33 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/718.
|  | 2013-06-25 | 21:43 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 122.2833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/796.
|  | Sub Total --> |  |  |  | 0 | 0.35 | 0.13333 | 284.4833
43 | NARENDRA - DAVANGERE II | 2013-06-08 | 7:35 | 2013-06-18 | 10:08 | 0 | 0 | 0 | 242.55 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/201. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 242.55
44 | NELAMANGALA - BIDADI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
45 | NELAMANGALA - BIDADI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
46 | NELAMANGALA - MYSORE I | 2013-06-04 | 0:41 | 2013-06-04 | 6:27 | 0 | 0 | 0 | 5.7667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/75. | 100
|  | 2013-06-13 | 15:40 | 2013-06-13 | 15:48 | 0 | 0 | 0 | 0.13333 | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-06/360.
|  | 2013-06-30 | 23:54 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 0.1 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/913.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 6
47 | NELAMANGALA - MYSORE II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
48 | NEYVELI - BAHOOR | 2013-06-29 | 20:40 | 2013-06-29 | 21:02 | 0 | 0.36667 | 0 | 0 | Charging delayed by Bahoor PED SS vide message no. CP-06/1022 dtd. 29.06.13. | 99.9629
|  | 2013-06-29 | 20:24 | 2013-06-29 | 20:40 | 0.26667 | 0 | 0 | 0 | Tripped on R-N (Ph-earth) transient fault. FLR: 9.2 KM from Neyveli end.
|  | Sub Total --> |  |  |  | 0.26667 | 0.36667 | 0 | 0
49 | NEYVELI - VILLIANUR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
50 | NEYVELI TS II - PUDUCHERRY-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
51 | NEYVELI TS II - PUGALUR |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
52 | NEYVELI TS II - TRICHY - I | 2013-06-01 | 10:07 | 2013-06-01 | 13:23 | 3.2667 | 0 | 0 | 0 | Shut down availed for replacement of broken insulators at Loc. No. 25 & 26 vide SRLDC code no. CR-06/11. | 99.5463
|  | Sub Total --> |  |  |  | 3.2667 | 0 | 0 | 0
53 | NEYVELI TS II EXP - PUGALUR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
54 | NEYVELI TS-I EXTENSION - TRICHY | 2013-06-29 | 9:53 | 2013-06-29 | 10:05 | 0 | 0 | 0 | 0.2 | Hand tripped for taking out Line reactor at Trichy end for voltage regulation as per SRLDC instructions vide code no. CR-06/882. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0.2
55 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
56 | NEYVELI-SALEM - I | 2013-06-19 | 8:39 | 2013-06-20 | 17:51 | 0 | 0 | 0 | 33.2 | Shut down availed by M/s NLC for routine maintenance works, CT painting and CTMK panel replacement works vide SRLDC code no. CR-06/589. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 33.2
57 | NEYVELI-SALEM - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
58 | PALAKKAD - TRICHUR I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
59 | PALAKKAD - TRICHUR II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
60 | PUDUCHERRY-SVCHATRAM-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
61 | PUGALUR - MADURAI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
62 | PUGALUR - MADURAI - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
63 | SALEM - UDUMALPET I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
64 | SALEM - UDUMALPET II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
65 | SVCHATRAM-SRIPERUMBUDUR-I | 2013-06-30 | 8:36 | 2013-06-30 | 15:54 | 0 | 0 | 0 | 7.3 | Shut down availed for OPGW striging works vide SRLDC code no. CR-06/900. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 7.3
66 | THIRUNELVELI - EDAMON - I | 2013-06-13 | 10:35 | 2013-06-13 | 22:48 | 0 | 0 | 0 | 12.2167 | Shut down availed by M/s KSEB for replacing the hanging conductor of 220 kV upper bus at Edamon end vide SRLDC code no. CR-06/350. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 12.2167
67 | THIRUNELVELI - EDAMON - II | 2013-06-13 | 10:35 | 2013-06-13 | 22:49 | 0 | 0 | 0 | 12.2333 | Shut down availed by M/s KSEB for replacing the hanging conductor of 220 kV upper bus at Edamon end vide SRLDC code no. CR-06/351. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 12.2333
68 | THIRUNELVELI - KUDAMKULAM-I | 2013-06-01 | 0:00 | 2013-06-01 | 10:28 | 0 | 0 | 0 | 10.4667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/400. | 100
|  | 2013-06-02 | 10:51 | 2013-06-02 | 11:47 | 0 | 0.93333 | 0 | 0 | Line tripped at Kudamkulam (NPCIL SS) end only due to circuit breaker problem at Kudamkulam end.
|  | 2013-06-24 | 23:01 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 144.9833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/761.
|  | Sub Total --> |  |  |  | 0 | 0.93333 | 0 | 155.45
69 | THIRUNELVELI - KUDAMKULAM-II | 2013-06-05 | 11:11 | 2013-06-08 | 2:07 | 0 | 0 | 0 | 62.9333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/113. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 62.9333
70 | THIRUNELVELI - KUDAMKULAM-III | 2013-06-01 | 13:23 | 2013-06-05 | 11:10 | 0 | 0 | 0 | 93.7833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/19. | 100
|  | 2013-06-08 | 1:47 | 2013-06-17 | 15:42 | 0 | 0 | 0 | 229.9167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/196.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 323.7
71 | THIRUNELVELI - KUDAMKULAM-IV | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
72 | THIRUNELVELI - TRIVANDRUM - I | 2013-06-22 | 9:34 | 2013-06-22 | 13:28 | 3.9 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-06/696. | 99.4583
|  | 2013-06-22 | 13:28 | 2013-06-22 | 15:00 | 0 | 0 | 0 | 1.5333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message dtd. 22.06.13.
|  | Sub Total --> |  |  |  | 3.9 | 0 | 0 | 1.5333
73 | THIRUNELVELI - TRIVANDRUM - II | 2013-06-02 | 0:01 | 2013-06-02 | 8:01 | 0 | 0 | 0 | 8 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/30. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8
74 | THIRUNELVELI - UDUMALPET I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
75 | THIRUNELVELI - UDUMALPET II | 2013-06-13 | 17:14 | 2013-06-14 | 8:03 | 0 | 0 | 0 | 14.8167 | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-06/365. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 14.8167
76 | TRICHUR - KOCHI I |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
77 | TRICHUR - KOCHI II | 2013-06-09 | 1:00 | 2013-06-09 | 1:29 | 0.48333 | 0 | 0 | 0 | Tripped on R-N fault due to heavy lightning and thunderstorm. | 99.4792
|  | 2013-06-15 | 12:51 | 2013-06-15 | 13:06 | 0.25 | 0 | 0 | 0 | Tripped on R-N (Ph-earth) transient fault. FLR: 18 Km from Kochi end.
|  | 2013-06-18 | 14:22 | 2013-06-18 | 17:23 | 3.0167 | 0 | 0 | 0 | Shut down availed for tightening of earth wire between loc no. 53-54 vide SRLDC code no. CR-06/567.
|  | Sub Total --> |  |  |  | 3.75 | 0 | 0 | 0
78 | TRICHY - KARAIKUDI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
79 | TRICHY - MADURAI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
80 | UDUMALPET - MADURAI | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
81 | UDUMALPET - PALAKKAD I | 2013-06-23 | 8:28 | 2013-06-23 | 14:39 | 0 | 0 | 0 | 6.1833 | Shut down availed for installation of OPGW under Microwave replacement project through off-line method vide SRLDC code no. CR-06/720. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 6.1833
82 | UDUMALPET - PALAKKAD II | 2013-06-14 | 9:37 | 2013-06-14 | 14:29 | 4.8667 | 0 | 0 | 0 | Shut down availed for jumper replacement works of CVT vide SRLDC code no. CR-06/397. | 99.3241
|  | Sub Total --> |  |  |  | 4.8667 | 0 | 0 | 0
83 | VALLUR - KALIVANDAPATTU I | 2013-06-27 | 10:09 | 2013-06-27 | 10:24 | 0 | 0.25 | 0 | 0 | Tripped due to suspected PLCC maloperation at Vallur (NTECL SS) end. | 100
|  | 2013-06-30 | 8:18 | 2013-06-30 | 15:01 | 0 | 0 | 0 | 6.7167 | Shut down availed for OPGW striging works vide SRLDC code no. CR-06/899.
|  | Sub Total --> |  |  |  | 0 | 0.25 | 0 | 6.7167
84 | VALLUR - KALIVANDAPATTU II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## ICT
Element wise availability for the month of June-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Inter Connecting Transformers (ICTs)
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | ARASUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | ARASUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | BANGALORE ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | BANGALORE ICT - II | 2013-06-03 | 12:00 | 2013-06-03 | 12:02 | 0.033333 | 0 | 0 | 0 | Tripped during relay checking. | 99.2269
|  | 2013-06-06 | 15:29 | 2013-06-06 | 17:05 | 1.6 | 0 | 0 | 0 | Tripped due to failure of micro switch of PRV in Unit 4 .
|  | 2013-06-30 | 10:41 | 2013-06-30 | 14:37 | 3.9333 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-06/902.
|  | Sub Total --> |  |  |  | 5.5667 | 0 | 0 | 0
5 | BIDADI ICT-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
6 | BIDADI ICT-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | HASSAN ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | HASSAN ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
9 | HIRIYUR ICT | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | HIRIYUR ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | HOSUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | HOSUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | KALIVANDAPATTU ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | KALIVANDAPATTU ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | KARAIKUDI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | KARAIKUDI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
17 | KOCHI ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | KOCHI ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | KOLAR ICT | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | KOLAR ICT-II | 2013-06-03 | 10:35 | 2013-06-03 | 16:10 | 5.5833 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-06/64. | 99.2245
|  | Sub Total --> |  |  |  | 5.5833 | 0 | 0 | 0
21 | MADURAI ICT - I | 2013-06-15 | 10:39 | 2013-06-15 | 13:27 | 2.8 | 0 | 0 | 0 | Shut down availed for replacement of 230 kV Y-Phase LA vide SRLDC code no. CR-06/443. | 99.6111
|  | Sub Total --> |  |  |  | 2.8 | 0 | 0 | 0
22 | MADURAI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | MYSORE ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
24 | MYSORE ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
25 | NARENDRA ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
26 | NARENDRA ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | PALAKKAD ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | PALAKKAD ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
29 | PUDUCHERRY ICT-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
30 | PUDUCHERRY ICT-II | 2013-06-08 | 11:01 | 2013-06-08 | 14:59 | 3.9667 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-06/208. | 99.4491
|  | Sub Total --> |  |  |  | 3.9667 | 0 | 0 | 0
31 | PUGALUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
32 | PUGALUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | THIRUNELVELI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | THIRUNELVELI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | TRICHY ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | TRICHY ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | TRIVANDRUM - ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | TRIVANDRUM - ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | TRIVANDRUM - ICT III | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | UDUMALPET ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | UDUMALPET ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
42 | UDUMALPET ICT - III | 2013-06-18 | 10:02 | 2013-06-18 | 12:04 | 2.0333 | 0 | 0 | 0 | Shut down availed for collecting 218 bay R-Phase CT oil sample vide SRLDC code no. CR-06/553. | 99.7176
|  | Sub Total --> |  |  |  | 2.0333 | 0 | 0 | 0

## BR & Sw Reactors
Element wise availability for the month of June-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Bus Reactors & Switchable Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | BANGALORE BUS REACTOR | 2013-06-01 | 9:58 | 2013-06-02 | 14:38 | 0 | 0 | 0 | 28.6667 | H/T for voltage regulation | 100
|  | 2013-06-05 | 10:03 | 2013-06-06 | 0:11 | 0 | 0 | 0 | 14.1333 | H/T for voltage regulation
|  | 2013-06-06 | 9:39 | 2013-06-07 | 0:19 | 0 | 0 | 0 | 14.6667 | H/T for voltage regulation
|  | 2013-06-07 | 9:38 | 2013-06-08 | 22:18 | 0 | 0 | 0 | 36.6667 | H/T for voltage regulation
|  | 2013-06-10 | 9:36 | 2013-06-12 | 23:09 | 0 | 0 | 0 | 61.55 | H/T for voltage regulation
|  | 2013-06-13 | 9:06 | 2013-06-13 | 23:10 | 0 | 0 | 0 | 14.0667 | H/T for voltage regulation
|  | 2013-06-14 | 8:14 | 2013-06-14 | 22:01 | 0 | 0 | 0 | 13.7833 | H/T for voltage regulation
|  | 2013-06-15 | 7:05 | 2013-06-16 | 17:17 | 0 | 0 | 0 | 34.2 | H/T for voltage regulation
|  | 2013-06-17 | 8:24 | 2013-06-17 | 22:20 | 0 | 0 | 0 | 13.9333 | H/T for voltage regulation
|  | 2013-06-18 | 8:22 | 2013-06-22 | 22:13 | 0 | 0 | 0 | 109.85 | H/T for voltage regulation
|  | 2013-06-24 | 9:39 | 2013-06-24 | 23:11 | 0 | 0 | 0 | 13.5333 | H/T for voltage regulation
|  | 2013-06-26 | 10:13 | 2013-06-28 | 22:16 | 0 | 0 | 0 | 60.05 | H/T for voltage regulation
|  | 2013-06-29 | 9:32 | 2013-06-29 | 21:37 | 0 | 0 | 0 | 12.0833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 427.1833
2 | BIDADI BUS REACTOR - I | 2013-06-11 | 9:50 | 2013-06-12 | 23:02 | 0 | 0 | 0 | 37.2 | H/T for voltage regulation | 100
|  | 2013-06-13 | 9:11 | 2013-06-13 | 22:58 | 0 | 0 | 0 | 13.7833 | H/T for voltage regulation
|  | 2013-06-14 | 8:15 | 2013-06-14 | 22:09 | 0 | 0 | 0 | 13.9 | H/T for voltage regulation
|  | 2013-06-15 | 7:07 | 2013-06-15 | 22:20 | 0 | 0 | 0 | 15.2167 | H/T for voltage regulation
|  | 2013-06-17 | 8:21 | 2013-06-17 | 22:15 | 0 | 0 | 0 | 13.9 | H/T for voltage regulation
|  | 2013-06-21 | 9:38 | 2013-06-21 | 23:38 | 0 | 0 | 0 | 14 | H/T for voltage regulation
|  | 2013-06-22 | 8:26 | 2013-06-22 | 22:28 | 0 | 0 | 0 | 14.0333 | H/T for voltage regulation
|  | 2013-06-26 | 10:02 | 2013-06-26 | 22:52 | 0 | 0 | 0 | 12.8333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 134.8667
3 | HASSAN BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | HIRIYUR BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | HOSUR BUS REACTOR - I | 2013-06-03 | 8:30 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 663.5 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 663.5
6 | KARAIKUDI BUS REACTOR - I | 2013-06-03 | 8:35 | 2013-06-03 | 23:15 | 0 | 0 | 0 | 14.6667 | H/T for voltage regulation | 100
|  | 2013-06-04 | 11:34 | 2013-06-04 | 21:59 | 0 | 0 | 0 | 10.4167 | H/T for voltage regulation
|  | 2013-06-06 | 11:52 | 2013-06-09 | 1:00 | 0 | 0 | 0 | 61.1333 | H/T for voltage regulation
|  | 2013-06-11 | 8:44 | 2013-06-11 | 21:33 | 0 | 0 | 0 | 12.8167 | H/T for voltage regulation
|  | 2013-06-13 | 19:08 | 2013-06-15 | 22:37 | 0 | 0 | 0 | 51.4833 | H/T for voltage regulation
|  | 2013-06-18 | 8:26 | 2013-06-18 | 22:28 | 0 | 0 | 0 | 14.0333 | H/T for voltage regulation
|  | 2013-06-19 | 10:45 | 2013-06-22 | 22:47 | 0 | 0 | 0 | 84.0333 | H/T for voltage regulation
|  | 2013-06-24 | 9:37 | 2013-06-25 | 22:15 | 0 | 0 | 0 | 36.6333 | H/T for voltage regulation
|  | 2013-06-26 | 11:44 | 2013-06-30 | 22:36 | 0 | 0 | 0 | 106.8667 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 392.0833
7 | KOCHI BUS REACTOR I | 2013-06-03 | 9:28 | 2013-06-03 | 20:58 | 0 | 0 | 0 | 11.5 | H/T for voltage regulation | 100
|  | 2013-06-04 | 11:32 | 2013-06-04 | 23:16 | 0 | 0 | 0 | 11.7333 | H/T for voltage regulation
|  | 2013-06-05 | 10:28 | 2013-06-06 | 0:16 | 0 | 0 | 0 | 13.8 | H/T for voltage regulation
|  | 2013-06-06 | 9:03 | 2013-06-09 | 1:23 | 0 | 0 | 0 | 64.3333 | H/T for voltage regulation
|  | 2013-06-10 | 9:48 | 2013-06-11 | 21:38 | 0 | 0 | 0 | 35.8333 | H/T for voltage regulation
|  | 2013-06-12 | 12:22 | 2013-06-12 | 23:09 | 0 | 0 | 0 | 10.7833 | H/T for voltage regulation
|  | 2013-06-13 | 9:14 | 2013-06-13 | 23:08 | 0 | 0 | 0 | 13.9 | H/T for voltage regulation
|  | 2013-06-14 | 8:21 | 2013-06-14 | 22:27 | 0 | 0 | 0 | 14.1 | H/T for voltage regulation
|  | 2013-06-15 | 8:24 | 2013-06-15 | 22:15 | 0 | 0 | 0 | 13.85 | H/T for voltage regulation
|  | 2013-06-17 | 8:25 | 2013-06-17 | 22:34 | 0 | 0 | 0 | 14.15 | H/T for voltage regulation
|  | 2013-06-18 | 9:37 | 2013-06-18 | 22:24 | 0 | 0 | 0 | 12.7833 | H/T for voltage regulation
|  | 2013-06-19 | 9:55 | 2013-06-20 | 22:04 | 0 | 0 | 0 | 36.15 | H/T for voltage regulation
|  | 2013-06-21 | 9:29 | 2013-06-22 | 23:02 | 0 | 0 | 0 | 37.55 | H/T for voltage regulation
|  | 2013-06-25 | 11:49 | 2013-06-25 | 22:10 | 0 | 0 | 0 | 10.35 | H/T for voltage regulation
|  | 2013-06-27 | 10:05 | 2013-06-28 | 22:17 | 0 | 0 | 0 | 36.2 | H/T for voltage regulation
|  | 2013-06-29 | 14:54 | 2013-06-30 | 22:11 | 0 | 0 | 0 | 31.2833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 368.3
8 | KOLAR BUS REACTOR - I | 2013-06-10 | 9:45 | 2013-06-12 | 22:58 | 0 | 0 | 0 | 61.2167 | H/T for voltage regulation | 100
|  | 2013-06-17 | 10:05 | 2013-06-17 | 22:14 | 0 | 0 | 0 | 12.15 | H/T for voltage regulation
|  | 2013-06-18 | 9:36 | 2013-06-18 | 22:17 | 0 | 0 | 0 | 12.6833 | H/T for voltage regulation
|  | 2013-06-19 | 9:50 | 2013-06-20 | 21:48 | 0 | 0 | 0 | 35.9667 | H/T for voltage regulation
|  | 2013-06-27 | 10:46 | 2013-06-28 | 22:05 | 0 | 0 | 0 | 35.3167 | H/T for voltage regulation
|  | 2013-06-29 | 9:11 | 2013-06-29 | 21:27 | 0 | 0 | 0 | 12.2667 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 169.6
9 | MYSORE BUS REACTOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | NARENDRA BUS REACTOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | PALAKKAD BUS REACTOR - I | 2013-06-03 | 9:31 | 2013-06-03 | 20:45 | 0 | 0 | 0 | 11.2333 | H/T for voltage regulation | 100
|  | 2013-06-04 | 11:41 | 2013-06-04 | 23:05 | 0 | 0 | 0 | 11.4 | H/T for voltage regulation
|  | 2013-06-05 | 10:08 | 2013-06-06 | 0:06 | 0 | 0 | 0 | 13.9667 | H/T for voltage regulation
|  | 2013-06-06 | 9:00 | 2013-06-09 | 1:11 | 0 | 0 | 0 | 64.1833 | H/T for voltage regulation
|  | 2013-06-10 | 9:44 | 2013-06-11 | 21:51 | 0 | 0 | 0 | 36.1167 | H/T for voltage regulation
|  | 2013-06-12 | 12:17 | 2013-06-12 | 23:03 | 0 | 0 | 0 | 10.7667 | H/T for voltage regulation
|  | 2013-06-13 | 9:11 | 2013-06-13 | 23:06 | 0 | 0 | 0 | 13.9167 | H/T for voltage regulation
|  | 2013-06-14 | 8:23 | 2013-06-14 | 22:13 | 0 | 0 | 0 | 13.8333 | H/T for voltage regulation
|  | 2013-06-15 | 8:22 | 2013-06-15 | 22:06 | 0 | 0 | 0 | 13.7333 | H/T for voltage regulation
|  | 2013-06-17 | 8:22 | 2013-06-17 | 22:24 | 0 | 0 | 0 | 14.0333 | H/T for voltage regulation
|  | 2013-06-18 | 9:34 | 2013-06-18 | 22:19 | 0 | 0 | 0 | 12.75 | H/T for voltage regulation
|  | 2013-06-19 | 9:52 | 2013-06-20 | 21:58 | 0 | 0 | 0 | 36.1 | H/T for voltage regulation
|  | 2013-06-21 | 9:23 | 2013-06-22 | 22:50 | 0 | 0 | 0 | 37.45 | H/T for voltage regulation
|  | 2013-06-25 | 11:57 | 2013-06-25 | 22:05 | 0 | 0 | 0 | 10.1333 | H/T for voltage regulation
|  | 2013-06-27 | 16:03 | 2013-06-28 | 22:15 | 0 | 0 | 0 | 30.2 | H/T for voltage regulation
|  | 2013-06-29 | 15:01 | 2013-06-30 | 22:12 | 0 | 0 | 0 | 31.1833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 361
12 | SALEM BUS REACTOR - I | 2013-06-07 | 9:40 | 2013-06-09 | 1:31 | 0 | 0 | 0 | 39.85 | H/T for voltage regulation | 100
|  | 2013-06-11 | 9:44 | 2013-06-16 | 2:41 | 0 | 0 | 0 | 112.95 | H/T for voltage regulation
|  | 2013-06-18 | 9:49 | 2013-06-18 | 22:16 | 0 | 0 | 0 | 12.45 | H/T for voltage regulation
|  | 2013-06-19 | 9:08 | 2013-06-24 | 23:34 | 0 | 0 | 0 | 134.4333 | H/T for voltage regulation
|  | 2013-06-27 | 15:12 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 80.8 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 380.4833
13 | SRIPERUMBUDUR BUS REACTOR - I | 2013-06-06 | 9:35 | 2013-06-09 | 15:08 | 0 | 0 | 0 | 77.55 | H/T for voltage regulation | 100
|  | 2013-06-10 | 10:38 | 2013-06-16 | 17:15 | 0 | 0 | 0 | 150.6167 | H/T for voltage regulation
|  | 2013-06-17 | 10:08 | 2013-06-29 | 21:47 | 0 | 0 | 0 | 299.65 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 527.8167
14 | THIRUNELVELI BUS REACTOR - I | 2013-06-04 | 11:31 | 2013-06-04 | 22:03 | 0 | 0 | 0 | 10.5333 | H/T for voltage regulation | 100
|  | 2013-06-05 | 15:06 | 2013-06-05 | 23:42 | 0 | 0 | 0 | 8.6 | H/T for voltage regulation
|  | 2013-06-06 | 8:57 | 2013-06-07 | 0:31 | 0 | 0 | 0 | 15.5667 | H/T for voltage regulation
|  | 2013-06-07 | 8:21 | 2013-06-07 | 11:04 | 0 | 0 | 0 | 2.7167 | H/T for voltage regulation
|  | 2013-06-11 | 8:38 | 2013-06-11 | 21:33 | 0 | 0 | 0 | 12.9167 | H/T for voltage regulation
|  | 2013-06-13 | 11:11 | 2013-06-13 | 23:06 | 0 | 0 | 0 | 11.9167 | H/T for voltage regulation
|  | 2013-06-14 | 9:57 | 2013-06-14 | 22:16 | 0 | 0 | 0 | 12.3167 | H/T for voltage regulation
|  | 2013-06-18 | 8:27 | 2013-06-18 | 22:17 | 0 | 0 | 0 | 13.8333 | H/T for voltage regulation
|  | 2013-06-19 | 10:44 | 2013-06-19 | 23:49 | 0 | 0 | 0 | 13.0833 | H/T for voltage regulation
|  | 2013-06-21 | 18:58 | 2013-06-21 | 23:02 | 0 | 0 | 0 | 4.0667 | H/T for voltage regulation
|  | 2013-06-22 | 8:51 | 2013-06-22 | 22:23 | 0 | 0 | 0 | 13.5333 | H/T for voltage regulation
|  | 2013-06-24 | 9:44 | 2013-06-24 | 23:22 | 0 | 0 | 0 | 13.6333 | H/T for voltage regulation
|  | 2013-06-27 | 15:08 | 2013-06-27 | 22:50 | 0 | 0 | 0 | 7.7 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 140.4167
15 | THIRUNELVELI BUS REACTOR - II | 2013-06-02 | 11:35 | 2013-06-02 | 20:38 | 9.05 | 0 | 0 | 0 | Shut down availed for attending oil leakage in conservator breather vide SRLDC code no. CR-06/33. | 98.7431
|  | 2013-06-03 | 10:22 | 2013-06-03 | 21:03 | 0 | 0 | 0 | 10.6833 | H/T for voltage regulation
|  | 2013-06-04 | 16:03 | 2013-06-04 | 22:07 | 0 | 0 | 0 | 6.0667 | H/T for voltage regulation
|  | 2013-06-05 | 14:17 | 2013-06-05 | 23:45 | 0 | 0 | 0 | 9.4667 | H/T for voltage regulation
|  | 2013-06-06 | 8:57 | 2013-06-07 | 0:35 | 0 | 0 | 0 | 15.6333 | H/T for voltage regulation
|  | 2013-06-07 | 8:23 | 2013-06-07 | 11:06 | 0 | 0 | 0 | 2.7167 | H/T for voltage regulation
|  | 2013-06-11 | 8:39 | 2013-06-11 | 21:36 | 0 | 0 | 0 | 12.95 | H/T for voltage regulation
|  | 2013-06-13 | 11:12 | 2013-06-13 | 23:12 | 0 | 0 | 0 | 12 | H/T for voltage regulation
|  | 2013-06-14 | 9:59 | 2013-06-14 | 22:19 | 0 | 0 | 0 | 12.3333 | H/T for voltage regulation
|  | 2013-06-21 | 18:59 | 2013-06-21 | 23:04 | 0 | 0 | 0 | 4.0833 | H/T for voltage regulation
|  | 2013-06-22 | 8:52 | 2013-06-22 | 22:25 | 0 | 0 | 0 | 13.55 | H/T for voltage regulation
|  | 2013-06-24 | 11:07 | 2013-06-24 | 23:24 | 0 | 0 | 0 | 12.2833 | H/T for voltage regulation
|  | 2013-06-27 | 15:09 | 2013-06-27 | 22:56 | 0 | 0 | 0 | 7.7833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 9.05 | 0 | 0 | 119.55
16 | Kolar Line Reactor at Bangalore | 2013-06-07 | 9:51 | 2013-06-09 | 0:51 | 0 | 0 | 0 | 39 | H/T for voltage regulation | 100
|  | 2013-06-11 | 9:49 | 2013-06-17 | 1:15 | 0 | 0 | 0 | 135.4333 | H/T for voltage regulation
|  | 2013-06-17 | 10:03 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 325.95 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 500.3833
17 | Neyveli TS II Exp Line Reactor at Pugalur |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | Neyveli TS II Line Reactor at Pugalur | 2013-06-14 | 10:12 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 397.8 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 397.8
19 | Thirunelveli 1 Line Reactor at Udumalpet | 2013-06-04 | 16:04 | 2013-06-04 | 22:54 | 0 | 0 | 0 | 6.8333 | H/T for voltage regulation | 100
|  | 2013-06-05 | 14:43 | 2013-06-07 | 0:22 | 0 | 0 | 0 | 33.65 | H/T for voltage regulation
|  | 2013-06-07 | 8:24 | 2013-06-07 | 22:53 | 0 | 0 | 0 | 14.4833 | H/T for voltage regulation
|  | 2013-06-11 | 9:36 | 2013-06-11 | 21:28 | 0 | 0 | 0 | 11.8667 | H/T for voltage regulation
|  | 2013-06-12 | 12:20 | 2013-06-15 | 22:08 | 0 | 0 | 0 | 81.8 | H/T for voltage regulation
|  | 2013-06-20 | 11:09 | 2013-06-22 | 22:35 | 0 | 0 | 0 | 59.4333 | H/T for voltage regulation
|  | 2013-06-24 | 10:55 | 2013-06-24 | 23:04 | 0 | 0 | 0 | 12.15 | H/T for voltage regulation
|  | 2013-06-26 | 11:47 | 2013-06-28 | 22:25 | 0 | 0 | 0 | 58.6333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 278.85
20 | Thirunelveli 2 Line Reactor at Udumalpet | 2013-06-04 | 16:05 | 2013-06-04 | 22:55 | 0 | 0 | 0 | 6.8333 | H/T for voltage regulation | 100
|  | 2013-06-05 | 14:44 | 2013-06-07 | 0:24 | 0 | 0 | 0 | 33.6667 | H/T for voltage regulation
|  | 2013-06-07 | 8:25 | 2013-06-07 | 22:53 | 0 | 0 | 0 | 14.4667 | H/T for voltage regulation
|  | 2013-06-11 | 9:36 | 2013-06-11 | 21:29 | 0 | 0 | 0 | 11.8833 | H/T for voltage regulation
|  | 2013-06-12 | 12:21 | 2013-06-15 | 22:08 | 0 | 0 | 0 | 81.7833 | H/T for voltage regulation
|  | 2013-06-20 | 11:09 | 2013-06-22 | 22:35 | 0 | 0 | 0 | 59.4333 | H/T for voltage regulation
|  | 2013-06-24 | 10:55 | 2013-06-24 | 23:05 | 0 | 0 | 0 | 12.1667 | H/T for voltage regulation
|  | 2013-06-26 | 11:48 | 2013-06-28 | 22:25 | 0 | 0 | 0 | 58.6167 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 278.85
21 | Udumalpet 1 Line Reactor at Thirunelveli | 2013-06-07 | 9:36 | 2013-06-07 | 22:31 | 0 | 0 | 0 | 12.9167 | H/T for voltage regulation | 100
|  | 2013-06-14 | 8:14 | 2013-06-15 | 21:14 | 0 | 0 | 0 | 37 | H/T for voltage regulation
|  | 2013-06-20 | 16:28 | 2013-06-20 | 21:48 | 0 | 0 | 0 | 5.3333 | H/T for voltage regulation
|  | 2013-06-21 | 10:05 | 2013-06-22 | 21:22 | 0 | 0 | 0 | 35.2833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 90.5333
22 | Udumalpet 2 Line Reactor at Thirunelveli | 2013-06-07 | 8:38 | 2013-06-07 | 22:32 | 0 | 0 | 0 | 13.9 | H/T for voltage regulation | 100
|  | 2013-06-14 | 8:15 | 2013-06-15 | 21:15 | 0 | 0 | 0 | 37 | H/T for voltage regulation
|  | 2013-06-20 | 16:29 | 2013-06-20 | 21:52 | 0 | 0 | 0 | 5.3833 | H/T for voltage regulation
|  | 2013-06-21 | 10:06 | 2013-06-22 | 22:23 | 0 | 0 | 0 | 36.2833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 92.5667
23 | Vallur 1 Line Reactor at Kalivandapattu | 2013-06-01 | 0:00 | 2013-06-02 | 14:43 | 0 | 0 | 0 | 38.7167 | H/T for voltage regulation | 100
|  | 2013-06-06 | 9:39 | 2013-06-09 | 15:11 | 0 | 0 | 0 | 77.5333 | H/T for voltage regulation
|  | 2013-06-10 | 9:32 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 494.4667 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 610.7167

## Non Sw Reactors
Element wise availability for the month of June-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Non Switchable Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | Chittoor Line reactor at Sriperumbudur (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
2 | SV Chatram Line reactor at Sriperumbudur (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
3 | Trichy Line reactor at Madurai (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
4 | Karaikudi Line reactor at Madurai (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | Bangalore Line reactor at Salem (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
6 | Neyveli 1 Line reactor at Salem (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
7 | Gooty Line reactor at Bangalore (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | Palakkad 1 Line reactor at Trichur (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
9 | Palakkad 2 Line reactor at Trichur (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
10 | Neyveli TS-2 Line reactor at Trichy (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
11 | Neyveli TS-1 Exp Line reactor at Trichy (Non switchable) | 2013-06-29 | 9:53 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 38.1167 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 38.1167
12 | Thirunelveli 1 Line reactor at Trivendrum (Non switchable) |  |  |  |  | 0 | 0 | 0 | 0 |  | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | Salem 1 Line reactor at Udumalpet (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
14 | Salem 2 Line reactor at Udumalpet (Non switchable) | 2013-06-01 | 0:00 | 2013-07-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720

## HVDC
Element wise availability for the month of June-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
HVDC POLES
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | TALCHER - KOLAR HVDC POLE - I | 2013-06-02 | 19:07 | 2013-06-02 | 19:07 | 0 | 0 | 0 | 0 | LFL and DC line fault recovery sequence operated at 273.98 kM from Kolar end (Tower no. 2942). | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | TALCHER - KOLAR HVDC POLE - II | 2013-06-13 | 8:35 | 2013-06-13 | 15:55 | 7.3333 | 0 | 0 | 0 | Pole- II manually deblocked to attend oil leakage in AC PLC noise capacitor unit at Talcher end vide SRLDC code no. CR-06/339. | 98.9815
|  | Sub Total --> |  |  |  | 7.3333 | 0 | 0 | 0