## Lines
Element wise availability for the month of September-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
AC Transmission Lines
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | EDAPPON - EDAMON | 2013-09-24 | 11:18 | 2013-09-24 | 16:39 | 0 | 0 | 0 | 5.35 | Shut down availed by M/s KSEB for rectification of hot spots in the 220 kV upper bus at Edamon SS vide SRLDC code no. CR-09/651. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 5.35
2 | KAYAMKULAM - EDAPPON | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | KAYAMKULAM - KUNDRA | 2013-09-01 | 0:00 | 2013-09-01 | 18:51 | 0 | 0 | 0 | 18.85 | Shut down aviled by M/s NTPC for CB overhauling works at Kayamkulam end vide CPCC code no. CP-08/1314. | 100
|  | 2013-09-25 | 9:32 | 2013-09-25 | 14:58 | 0 | 0 | 0 | 5.4333 | Shut down availed by M/s KSEB for attending hot spots at Kundra SS vide SRLDC code no. CR-09/699.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 24.2833
4 | KAYAMKULAM - POLLAM - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | KAYAMKULAM - POLLAM - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
6 | KUNDRA - EDAMON | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | ARASUR-UDUMALPET-I | 2013-09-23 | 8:36 | 2013-09-23 | 19:09 | 0 | 0 | 0 | 10.55 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted strech between loc. No: 74 to 189 vide SRLDC code no. CR-09/606. | 100
|  | 2013-09-24 | 7:53 | 2013-09-24 | 18:54 | 0 | 0 | 0 | 11.0167 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted strech between loc. No: 74 to 189 vide SRLDC code no. CR-09/645.
|  | 2013-09-25 | 7:57 | 2013-09-25 | 18:45 | 0 | 0 | 0 | 10.8 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted strech between loc. No: 74 to 189 vide SRLDC code no. CR-09/695.
|  | 2013-09-26 | 8:03 | 2013-09-26 | 18:06 | 0 | 0 | 0 | 10.05 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 74 to 189 vide SRLDC code no. CR-09/737.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 42.4167
8 | ARASUR-UDUMALPET-II | 2013-09-27 | 8:00 | 2013-09-27 | 18:02 | 0 | 0 | 0 | 10.0333 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted stretch between loc. No: 74 to 189 vide SRLDC code no. CR-09/775. | 100
|  | 2013-09-28 | 8:01 | 2013-09-28 | 19:49 | 0 | 0 | 0 | 11.8 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted strech between loc. No: 74 to 189 vide SRLDC code no. CR-09/814.
|  | 2013-09-29 | 8:00 | 2013-09-29 | 16:54 | 0 | 0 | 0 | 8.9 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted strech between loc. No: 74 to 189 vide SRLDC code no. CR-09/847.
|  | 2013-09-30 | 8:00 | 2013-09-30 | 15:06 | 0 | 0 | 0 | 7.1 | Shut down availed for replacement of disc insulator strings with CLR insulators in polluted strech between loc. No: 74 to 189 vide SRLDC code no. CR-09/880.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 37.8333
9 | BANGALORE - SALEM | 2013-09-21 | 10:14 | 2013-09-21 | 16:22 | 6.1333 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-09/557. | 99.1481
|  | Sub Total --> |  |  |  | 6.1333 | 0 | 0 | 0
10 | BHAVINI - ARANI I | 2013-09-04 | 21:38 | 2013-09-04 | 23:21 | 0 | 1.7167 | 0 | 0 | Line charging delayed by M/s BHAVINI vide message no. CP-09/164. | 98.4779
|  | 2013-09-04 | 10:42 | 2013-09-04 | 21:38 | 10.9333 | 0 | 0 | 0 | Shut down availed for guarantee test of equipments and AMP works vide SRLDC code no. CR-09/92.
|  | Sub Total --> |  |  |  | 10.9333 | 1.7167 | 0 | 0
11 | BHAVINI - ARANI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | BHAVINI - KANCHEEPURAM I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | BHAVINI - KANCHEEPURAM II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | BHAVINI - SIRUSERI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | BHAVINI - SIRUSERI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | BIDADI - SOMANAHALLI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
17 | BIDADI - SOMANAHALLI II | 2013-09-02 | 10:26 | 2013-09-03 | 16:50 | 30.4 | 0 | 0 | 0 | Shut availed for replacement of rigid conductor with tulip contact in all three phases of outer bus duct of 402 bay at Bidadi (GIS) SS vide SRLDC code no. CR-09/44. | 95.7778
|  | Sub Total --> |  |  |  | 30.4 | 0 | 0 | 0
18 | CHITTOOR - CHENNAI | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | CUDDAPAH - CHITTOOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | CUDDAPAH - KOLAR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
21 | GOOTY - BANGALORE | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | HASSAN - MYSORE I | 2013-09-03 | 23:48 | 2013-09-03 | 23:53 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end. | 100
|  | 2013-09-03 | 23:53 | 2013-09-04 | 6:28 | 0 | 0 | 0 | 6.5833 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/110.
|  | 2013-09-07 | 23:56 | 2013-09-08 | 0:01 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-08 | 0:01 | 2013-09-08 | 9:34 | 0 | 0 | 0 | 9.55 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/277.
|  | 2013-09-08 | 23:02 | 2013-09-09 | 6:42 | 0 | 0 | 0 | 7.6667 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/290.
|  | 2013-09-08 | 22:57 | 2013-09-08 | 23:02 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-09 | 23:53 | 2013-09-10 | 6:44 | 0 | 0 | 0 | 6.85 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/313.
|  | 2013-09-09 | 23:48 | 2013-09-09 | 23:53 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-11 | 0:01 | 2013-09-11 | 0:05 | 0 | 0 | 0.066667 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-11 | 0:05 | 2013-09-11 | 7:04 | 0 | 0 | 0 | 6.9833 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/360.
|  | 2013-09-12 | 0:01 | 2013-09-12 | 0:06 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-12 | 23:10 | 2013-09-12 | 23:17 | 0 | 0 | 0.11667 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-12 | 23:17 | 2013-09-13 | 8:02 | 0 | 0 | 0 | 8.75 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/450.
|  | 2013-09-12 | 0:06 | 2013-09-12 | 6:24 | 0 | 0 | 0 | 6.3 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/400.
|  | 2013-09-14 | 0:26 | 2013-09-14 | 8:37 | 0 | 0 | 0 | 8.1833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/386.
|  | 2013-09-15 | 0:00 | 2013-09-15 | 0:05 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-15 | 23:35 | 2013-09-16 | 7:33 | 0 | 0 | 0 | 7.9667 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/558.
|  | 2013-09-15 | 0:05 | 2013-09-15 | 9:21 | 0 | 0 | 0 | 9.2667 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/550.
|  | 2013-09-15 | 23:31 | 2013-09-15 | 23:35 | 0 | 0 | 0.066667 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-16 | 22:04 | 2013-09-17 | 6:41 | 0 | 0 | 0 | 8.6167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/440.
|  | 2013-09-17 | 23:31 | 2013-09-18 | 8:45 | 0 | 0 | 0 | 9.2333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/465.
|  | 2013-09-18 | 23:29 | 2013-09-18 | 23:32 | 0 | 0 | 0.05 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | 2013-09-18 | 23:32 | 2013-09-23 | 9:22 | 0 | 0 | 0 | 105.8333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/684.
|  | 2013-09-23 | 23:00 | 2013-09-24 | 19:05 | 0 | 0 | 0 | 20.0833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/640.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.8 | 221.8667
23 | HASSAN - MYSORE II | 2013-09-14 | 19:03 | 2013-09-14 | 19:34 | 0.51667 | 0 | 0 | 0 | Shut down availed for attending line isolator alignment problem at Hassan end vide SRLDC code no. CR-09/407. | 99.9282
|  | 2013-09-24 | 22:24 | 2013-09-25 | 5:26 | 0 | 0 | 0 | 7.0333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/683.
|  | 2013-09-29 | 17:59 | 2013-09-29 | 18:36 | 0 | 0 | 0.61667 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Mysore end.
|  | Sub Total --> |  |  |  | 0.51667 | 0 | 0.61667 | 7.0333
24 | HASSAN - NELAMANGALA I | 2013-09-03 | 23:58 | 2013-09-04 | 0:03 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end. | 100
|  | 2013-09-04 | 0:03 | 2013-09-04 | 6:32 | 0 | 0 | 0 | 6.4833 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/111.
|  | 2013-09-09 | 23:59 | 2013-09-10 | 0:05 | 0 | 0 | 0.1 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | 2013-09-10 | 0:05 | 2013-09-10 | 6:31 | 0 | 0 | 0 | 6.4333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/314.
|  | 2013-09-13 | 3:02 | 2013-09-13 | 3:05 | 0 | 0 | 0.05 | 0 | Line tripped on operation of over voltage protection at Hassan end. Direct trip signal received at Nelamangala end.
|  | 2013-09-13 | 3:05 | 2013-09-13 | 7:12 | 0 | 0 | 0 | 4.1167 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/454.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.23333 | 17.0333
25 | HASSAN - TALAGUPPA I | 2013-09-02 | 22:42 | 2013-09-02 | 23:23 | 0 | 0 | 0.68333 | 0 | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end. | 100
|  | 2013-09-02 | 23:23 | 2013-09-03 | 6:42 | 0 | 0 | 0 | 7.3167 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/60A.
|  | 2013-09-16 | 23:43 | 2013-09-16 | 23:48 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end.
|  | 2013-09-16 | 23:48 | 2013-09-17 | 6:27 | 0 | 0 | 0 | 6.65 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/593.
|  | 2013-09-18 | 23:56 | 2013-09-19 | 0:01 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end.
|  | 2013-09-19 | 0:01 | 2013-09-20 | 13:22 | 0 | 0 | 0 | 37.35 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/685.
|  | 2013-09-24 | 22:17 | 2013-09-24 | 22:22 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Talaguppa end. Direct trip signal received at Hassan end.
|  | 2013-09-24 | 22:22 | 2013-09-25 | 5:21 | 0 | 0 | 0 | 6.9833 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-08/973.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.93333 | 58.3
26 | HOSUR-SALEM | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
27 | KAIGA - NARENDRA I | 2013-09-15 | 0:05 | 2013-09-15 | 11:03 | 0 | 0 | 0 | 10.9667 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/550. | 100
|  | 2013-09-15 | 0:00 | 2013-09-15 | 0:05 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Narendra end. Direct trip signal received at Kaiga end.
|  | 2013-09-18 | 23:20 | 2013-09-18 | 23:24 | 0 | 0 | 0.066667 | 0 | Line tripped on operation of over voltage protection at Narendra end. Direct trip signal received at Kaiga end.
|  | 2013-09-18 | 23:24 | 2013-09-20 | 10:14 | 0 | 0 | 0 | 34.8333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/683.
|  | 2013-09-21 | 23:51 | 2013-09-21 | 23:58 | 0 | 0 | 0.11667 | 0 | Line tripped on operation of over voltage protection at Narendra end. Direct trip signal received at Kaiga end.
|  | 2013-09-21 | 23:58 | 2013-09-23 | 8:16 | 0 | 0 | 0 | 32.3 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/821.
|  | 2013-09-23 | 23:02 | 2013-09-24 | 7:28 | 0 | 0 | 0 | 8.4333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/639.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.26667 | 86.5333
28 | KAIGA - NARENDRA II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
29 | KAIGA - SIRSI - I | 2013-09-10 | 0:23 | 2013-09-13 | 19:32 | 0 | 0 | 0 | 91.15 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/249. | 100
|  | 2013-09-13 | 22:45 | 2013-09-23 | 10:01 | 0 | 0 | 0 | 227.2667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/379.
|  | 2013-09-23 | 23:59 | 2013-09-24 | 0:05 | 0 | 0 | 0.1 | 0 | Line Tripped on operation of over voltage protection at Guttur end.
|  | 2013-09-24 | 0:05 | 2013-09-26 | 9:00 | 0 | 0 | 0 | 56.9167 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/908.
|  | 2013-09-28 | 23:03 | 2013-09-29 | 8:40 | 0 | 0 | 0 | 9.6167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/843.
|  | 2013-09-30 | 0:07 | 2013-09-30 | 7:54 | 0 | 0 | 0 | 7.7833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/867.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.1 | 392.7333
30 | KAIGA - SIRSI - II | 2013-09-02 | 11:41 | 2013-09-02 | 13:10 | 0 | 1.4833 | 0 | 0 | Line tripped on receipt of Direct trip signal at Kaiga end due to operation of 220KV busbar protection at Guttur SS. | 100
|  | 2013-09-13 | 0:05 | 2013-09-13 | 0:10 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Guttur end. Direct trip signal received at Kaiga end.
|  | 2013-09-13 | 0:10 | 2013-09-13 | 9:06 | 0 | 0 | 0 | 8.9333 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/453.
|  | 2013-09-28 | 11:51 | 2013-09-28 | 18:58 | 0 | 0 | 0 | 7.1167 | Shut down availed by M/s KPTCL for relay testing at Guttur end vide SRLDC code no. CR-09/821.
|  | 2013-09-29 | 15:11 | 2013-09-29 | 18:33 | 0 | 3.3667 | 0 | 0 | Tripped due to receipt of direct trip signal at Kaiga end.
|  | Sub Total --> |  |  |  | 0 | 4.85 | 0.083333 | 16.05
31 | KARAIKUDI - MADURAI - I | 2013-09-03 | 10:10 | 2013-09-03 | 15:22 | 5.2 | 0 | 0 | 0 | Shut down availed for replacement of DGA violated Y-phase bushing of line reactor at Madurai end vide SRLDC code no. CR-09/70. | 99.2778
|  | Sub Total --> |  |  |  | 5.2 | 0 | 0 | 0
32 | KOLAR - BANGALORE | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | KOLAR - CHENNAI | 2013-09-03 | 23:58 | 2013-09-04 | 0:03 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Kolar end. Direct trip signal received at Sriperumbudur end. | 100
|  | 2013-09-04 | 0:03 | 2013-09-04 | 6:33 | 0 | 0 | 0 | 6.5 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/111.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.083333 | 6.5
34 | KOLAR - HOODY - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | KOLAR - HOODY - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | KOLAR - HOSUR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | KOLAR - HOSUR - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | MADURAI - TUTICORIN 1 | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | MADURAI - TUTICORIN 2 | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
40 | MADURAI-THIRUNELVELI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | MADURAI-THIRUNELVELI - II | 2013-09-01 | 0:00 | 2013-09-03 | 15:18 | 0 | 0 | 0 | 63.3 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/947. | 100
|  | 2013-09-06 | 22:51 | 2013-09-14 | 10:19 | 0 | 0 | 0 | 179.4667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/182.
|  | 2013-09-16 | 23:19 | 2013-09-21 | 11:40 | 0 | 0 | 0 | 108.35 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/442.
|  | 2013-09-27 | 10:23 | 2013-09-27 | 18:39 | 0 | 0 | 0 | 8.2667 | Shut down availed by M/s NPCIL for cleaning of wave trap, LA & CVT insulators at Kudamkulam end vide SRLDC code no. CR-09/779.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 359.3833
42 | NARENDRA - DAVANGERE I | 2013-09-15 | 0:05 | 2013-09-24 | 7:38 | 0 | 0 | 0 | 223.55 | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-09/550. | 100
|  | 2013-09-15 | 0:00 | 2013-09-15 | 0:05 | 0 | 0 | 0.083333 | 0 | Line tripped on operation of over voltage protection at Davangere end. Direct trip signal received at Narendra end.
|  | 2013-09-30 | 23:10 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 0.83333 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/914.
|  | Sub Total --> |  |  |  | 0 | 0 | 0.083333 | 224.3833
43 | NARENDRA - DAVANGERE II | 2013-09-01 | 22:18 | 2013-09-01 | 22:18 | 0 | 0 | 0 | 0 | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 89.37 KM from Narendra end. | 100
|  | 2013-09-01 | 22:45 | 2013-09-02 | 13:24 | 0 | 0 | 0 | 14.65 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/27.
|  | 2013-09-02 | 23:37 | 2013-09-15 | 8:12 | 0 | 0 | 0 | 296.5833 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/61.
|  | 2013-09-24 | 22:13 | 2013-09-30 | 8:08 | 0 | 0 | 0 | 129.9167 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/675.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 441.15
44 | NELAMANGALA - BIDADI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
45 | NELAMANGALA - BIDADI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
46 | NELAMANGALA - MYSORE I | 2013-09-08 | 23:40 | 2013-09-09 | 7:40 | 0 | 0 | 0 | 8 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/228. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8
47 | NELAMANGALA - MYSORE II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
48 | NEYVELI - BAHOOR | 2013-09-12 | 8:35 | 2013-09-12 | 21:04 | 0 | 0 | 0 | 12.4833 | Shut down availed by M/s PED for CB maintennce works at Bahoor end vide SRLDC code no. CR-09/325. | 100
|  | 2013-09-18 | 10:17 | 2013-09-18 | 13:31 | 0 | 0 | 3.2333 | 0 | Shut down availed for replacement of defective porcelain insulator with CLR insulator at loc.123 which was damaged due to lightning and rain vide SRLDC code no. CR-09/482.
|  | Sub Total --> |  |  |  | 0 | 0 | 3.2333 | 12.4833
49 | NEYVELI - VILLIANUR | 2013-09-24 | 14:06 | 2013-09-24 | 15:11 | 0 | 1.0833 | 0 | 0 | Tripped at Neyveli end only due to 220kV bus-1 fault at Neyveli end. | 100
|  | Sub Total --> |  |  |  | 0 | 1.0833 | 0 | 0
50 | NEYVELI TS II - PUDUCHERRY-I | 2013-09-10 | 8:30 | 2013-09-11 | 14:52 | 0 | 0 | 0 | 30.3667 | Shut down availed by M/s NLC for maintenance works at Neyveli end vide SRLDC code no. CR-09/263. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 30.3667
51 | NEYVELI TS II - PUGALUR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
52 | NEYVELI TS II - TRICHY - I | 2013-09-03 | 8:28 | 2013-09-04 | 15:37 | 0 | 0 | 0 | 31.15 | Shut down availed by M/s NLC for routine maitenance works at Neyveli TS-2 end vide SRLDC code no. CR-09/67. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 31.15
53 | NEYVELI TS II EXP - PUGALUR | 2013-09-17 | 7:16 | 2013-09-17 | 18:20 | 0 | 0 | 0 | 11.0667 | Shut down availed by M/s NLC for replacement of failed insulator string in bus coupler at Neyveli TS-2 Expansion end vide SRLDC code no. CR-09/452. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 11.0667
54 | NEYVELI TS-I EXTENSION - TRICHY | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
55 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
56 | NEYVELI-SALEM - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
57 | NEYVELI-SALEM - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
58 | PALAKKAD - TRICHUR I | 2013-09-07 | 11:06 | 2013-09-07 | 17:57 | 0 | 0 | 0 | 6.85 | Shut down availed for OPGW stringing works vide SRLDC code no. CR-09/189. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 6.85
59 | PALAKKAD - TRICHUR II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
60 | PUDUCHERRY-SVCHATRAM-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
61 | PUGALUR - MADURAI - I | 2013-09-17 | 15:01 | 2013-09-17 | 15:15 | 0.23333 | 0 | 0 | 0 | Tripped on Y-N (Ph-earth) transient fault. FLR: 82 KM from Madurai end. | 99.9676
|  | Sub Total --> |  |  |  | 0.23333 | 0 | 0 | 0
62 | PUGALUR - MADURAI - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
63 | SALEM - UDUMALPET I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
64 | SALEM - UDUMALPET II | 2013-09-01 | 9:47 | 2013-09-01 | 15:50 | 6.05 | 0 | 0 | 0 | Shut down availed for replacement of DGA violated R-phase bushing of line reactor at Udumalpet end vide SRLDC code no. CR-09/08. | 99.1597
|  | Sub Total --> |  |  |  | 6.05 | 0 | 0 | 0
65 | SVCHATRAM-SRIPERUMBUDUR-I | 2013-09-11 | 23:41 | 2013-09-12 | 1:37 | 1.9333 | 0 | 0 | 0 | Shut down availed for attending hotspot on B-phase wave trap terminal connector at Sriperumbudur end vide SRLDC code no. CR-09/312. | 99.7315
|  | Sub Total --> |  |  |  | 1.9333 | 0 | 0 | 0
66 | THIRUNELVELI - EDAMON - I | 2013-09-24 | 8:24 | 2013-09-24 | 17:16 | 0 | 0 | 0 | 8.8667 | Shut down availed by M/s KSEB for rectification of hot spots in the 220 kV upper bus at Edamon SS vide SRLDC code no. CR-09/646. | 100
|  | 2013-09-26 | 10:21 | 2013-09-26 | 11:23 | 0 | 0 | 0 | 1.0333 | Shut down availed by M/s KSEB for troubleshooting works in ABB relay at Edamon end vide SRLDC code no. CR-09/741.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 9.9
67 | THIRUNELVELI - EDAMON - II | 2013-09-02 | 17:40 | 2013-09-02 | 17:40 | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 81.9 KM from Thirunelveli end. | 100
|  | 2013-09-24 | 11:11 | 2013-09-24 | 18:23 | 0 | 0 | 0 | 7.2 | Shut down availed by M/s KSEB for rectification of hot spots in the 220 kV upper bus at Edamon SS vide SRLDC code no. CR-09/650.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 7.2
68 | THIRUNELVELI - KUDAMKULAM-I | 2013-09-01 | 0:00 | 2013-09-03 | 15:18 | 0 | 0 | 0 | 63.3 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/947. | 100
|  | 2013-09-06 | 22:51 | 2013-09-14 | 10:19 | 0 | 0 | 0 | 179.4667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/182.
|  | 2013-09-16 | 23:19 | 2013-09-21 | 11:40 | 0 | 0 | 0 | 108.35 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/442.
|  | 2013-09-27 | 10:23 | 2013-09-27 | 18:39 | 0 | 0 | 0 | 8.2667 | Shut down availed by M/s NPCIL for cleaning of wave trap, LA & CVT insulators at Kudamkulam end vide SRLDC code no. CR-09/779.
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 63.3
69 | THIRUNELVELI - KUDAMKULAM-II | 2013-09-26 | 10:24 | 2013-09-26 | 18:04 | 0 | 0 | 0 | 7.6667 | Shut down availed by M/s NPCIL for cleaning of wave trap, LA & CVT insulators at Kudamkulam end vide SRLDC code no. CR-09/742. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 7.6667
70 | THIRUNELVELI - KUDAMKULAM-III | 2013-09-04 | 23:16 | 2013-09-06 | 16:32 | 0 | 0 | 0 | 41.2667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/122. | 100
|  | 2013-09-24 | 23:53 | 2013-09-25 | 18:09 | 0 | 0 | 0 | 18.2667 | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-09/687.
|  | 2013-09-27 | 12:41 | 2013-09-27 | 13:01 | 0 | 0.33333 | 0 | 0 | Tripped at Thirunelveli End only on receipt of direct trip signal from Kudamkulam end while carrying out PLCC testing at Kudamkulam end.
|  | Sub Total --> |  |  |  | 0 | 0.33333 | 0 | 59.5333
71 | THIRUNELVELI - KUDAMKULAM-IV | 2013-09-21 | 12:28 | 2013-09-23 | 17:28 | 0 | 0 | 0 | 53 | Shut down availed by M/s NPCIL for maintenance works at Kudamkulam end vide SRLDC code no. CR-09/564. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 53
72 | THIRUNELVELI - TRIVANDRUM - I | 2013-09-05 | 10:35 | 2013-09-05 | 20:39 | 10.0667 | 0 | 0 | 0 | Shut down availed for line reactor B-phase bushing replacement work at Trivendrum end vide SRLDC code no. CR-09/131. | 98.6019
|  | Sub Total --> |  |  |  | 10.0667 | 0 | 0 | 0
73 | THIRUNELVELI - TRIVANDRUM - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
74 | THIRUNELVELI - UDUMALPET I | 2013-09-01 | 17:59 | 2013-09-01 | 18:16 | 0 | 0 | 0.28333 | 0 | Tripped on R-N fault due to flash over of R-phase insulator string at loc. No. 125 due to heavy lightning and thunderstorm. | 100
|  | 2013-09-07 | 9:05 | 2013-09-07 | 20:33 | 0 | 0 | 11.4667 | 0 | Shut down availed for replacement of R-phase suspention insulator string at loc no. 125 which was damaged due to flash over during heavy rain and lightining on 01.09.13 vide SRLDC code no. CR-09/186.
|  | Sub Total --> |  |  |  | 0 | 0 | 11.75 | 0
75 | THIRUNELVELI - UDUMALPET II | 2013-09-10 | 11:56 | 2013-09-10 | 18:35 | 6.65 | 0 | 0 | 0 | Shut down availed for line reactor LA replacement work vide SRLDC code no. CR-09/271. | 99.0764
|  | Sub Total --> |  |  |  | 6.65 | 0 | 0 | 0
76 | TRICHUR - KOCHI I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
77 | TRICHUR - KOCHI II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
78 | TRICHY - KARAIKUDI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
79 | TRICHY - MADURAI - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
80 | UDUMALPET - MADURAI | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
81 | UDUMALPET - PALAKKAD I | 2013-09-06 | 8:56 | 2013-09-06 | 17:54 | 0 | 0 | 0 | 8.9667 | Shut down availed for OPGW stringing works vide SRLDC code no. CR-09/156. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 8.9667
82 | UDUMALPET - PALAKKAD II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
83 | VALLUR - KALIVANDAPATTU I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
84 | VALLUR - KALIVANDAPATTU II | 2013-09-28 | 10:07 | 2013-09-28 | 10:07 | 0 | 0 | 0 | 0 | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 62.3 KM from Kalivindapattu end. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## ICT
Element wise availability for the month of September-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Inter Connecting Transformers (ICTs)
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | ARASUR ICT - I | 2013-09-11 | 10:26 | 2013-09-11 | 15:02 | 4.6 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-09/295. | 99.3611
|  | Sub Total --> |  |  |  | 4.6 | 0 | 0 | 0
2 | ARASUR ICT - II | 2013-09-12 | 10:23 | 2013-09-12 | 14:11 | 3.8 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-09/330. | 99.4722
|  | Sub Total --> |  |  |  | 3.8 | 0 | 0 | 0
3 | BANGALORE ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | BANGALORE ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | BIDADI ICT-I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
6 | BIDADI ICT-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
7 | HASSAN ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | HASSAN ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
9 | HIRIYUR ICT | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | HIRIYUR ICT II | 2013-09-10 | 9:26 | 2013-09-10 | 16:08 | 6.7 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-09/264. | 99.0694
|  | Sub Total --> |  |  |  | 6.7 | 0 | 0 | 0
11 | HOSUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
12 | HOSUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | KALIVANDAPATTU ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
14 | KALIVANDAPATTU ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
15 | KARAIKUDI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
16 | KARAIKUDI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
17 | KOCHI ICT I | 2013-09-04 | 12:46 | 2013-09-04 | 13:57 | 1.1833 | 0 | 0 | 0 | Shut down availed to attend hot spot at 220 kV B phase jumper vide SRLDC code no. CR-09/96. | 99.8356
|  | Sub Total --> |  |  |  | 1.1833 | 0 | 0 | 0
18 | KOCHI ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | KOLAR ICT | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
20 | KOLAR ICT-II | 2013-09-03 | 10:42 | 2013-09-03 | 10:49 | 0.11667 | 0 | 0 | 0 | Shut down availed for combintion changing vide SRLDC code no. CR-09/71. | 99.9838
|  | Sub Total --> |  |  |  | 0.11667 | 0 | 0 | 0
21 | MADURAI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
22 | MADURAI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | MYSORE ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
24 | MYSORE ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
25 | NARENDRA ICT I | 2013-09-17 | 10:11 | 2013-09-17 | 15:59 | 5.8 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-09/457. | 99.1944
|  | Sub Total --> |  |  |  | 5.8 | 0 | 0 | 0
26 | NARENDRA ICT II | 2013-09-18 | 10:18 | 2013-09-18 | 13:21 | 3.05 | 0 | 0 | 0 | Shut down availed for AMP works vide SRLDC code no. CR-09/481. | 99.5764
|  | Sub Total --> |  |  |  | 3.05 | 0 | 0 | 0
27 | PALAKKAD ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
28 | PALAKKAD ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
29 | PUDUCHERRY ICT-I | 2013-09-13 | 12:52 | 2013-09-13 | 13:16 | 0.4 | 0 | 0 | 0 | Tripped during 220 kV CB maintenance work. | 99.9444
|  | Sub Total --> |  |  |  | 0.4 | 0 | 0 | 0
30 | PUDUCHERRY ICT-II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
31 | PUGALUR ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
32 | PUGALUR ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
33 | THIRUNELVELI ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
34 | THIRUNELVELI ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
35 | TRICHY ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
36 | TRICHY ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
37 | TRIVANDRUM - ICT I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
38 | TRIVANDRUM - ICT II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
39 | TRIVANDRUM - ICT III | 2013-09-30 | 13:23 | 2013-09-30 | 13:26 | 0 | 0.05 | 0 | 0 | Shut down availed to remove bird nest from 220KV gantry vide SRLDC code no. CR-09/894. | 100
|  | Sub Total --> |  |  |  | 0 | 0.05 | 0 | 0
40 | UDUMALPET ICT - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
41 | UDUMALPET ICT - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
42 | UDUMALPET ICT - III | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0

## BR & Sw Reactors
Element wise availability for the month of September-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Bus Reactors & Switchable Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | BANGALORE BUS REACTOR | 2013-09-02 | 7:48 | 2013-09-02 | 22:58 | 0 | 0 | 0 | 15.1667 | H/T for voltage regulation | 100
|  | 2013-09-04 | 18:55 | 2013-09-04 | 23:27 | 0 | 0 | 0 | 4.5333 | H/T for voltage regulation
|  | 2013-09-05 | 7:01 | 2013-09-05 | 22:52 | 0 | 0 | 0 | 15.85 | H/T for voltage regulation
|  | 2013-09-06 | 8:24 | 2013-09-06 | 22:56 | 0 | 0 | 0 | 14.5333 | H/T for voltage regulation
|  | 2013-09-10 | 18:44 | 2013-09-10 | 21:47 | 0 | 0 | 0 | 3.05 | H/T for voltage regulation
|  | 2013-09-13 | 7:12 | 2013-09-13 | 22:43 | 0 | 0 | 0 | 15.5167 | H/T for voltage regulation
|  | 2013-09-14 | 8:19 | 2013-09-14 | 23:07 | 0 | 0 | 0 | 14.8 | H/T for voltage regulation
|  | 2013-09-16 | 7:39 | 2013-09-16 | 21:55 | 0 | 0 | 0 | 14.2667 | H/T for voltage regulation
|  | 2013-09-17 | 19:27 | 2013-09-17 | 22:20 | 0 | 0 | 0 | 2.8833 | H/T for voltage regulation
|  | 2013-09-18 | 8:14 | 2013-09-18 | 22:01 | 0 | 0 | 0 | 13.7833 | H/T for voltage regulation
|  | 2013-09-19 | 8:24 | 2013-09-19 | 21:45 | 0 | 0 | 0 | 13.35 | H/T for voltage regulation
|  | 2013-09-20 | 19:40 | 2013-09-20 | 22:56 | 0 | 0 | 0 | 3.2667 | H/T for voltage regulation
|  | 2013-09-21 | 7:19 | 2013-09-21 | 22:50 | 0 | 0 | 0 | 15.5167 | H/T for voltage regulation
|  | 2013-09-23 | 9:28 | 2013-09-23 | 22:26 | 0 | 0 | 0 | 12.9667 | H/T for voltage regulation
|  | 2013-09-24 | 16:16 | 2013-09-24 | 22:51 | 0 | 0 | 0 | 6.5833 | H/T for voltage regulation
|  | 2013-09-25 | 6:47 | 2013-09-25 | 22:08 | 0 | 0 | 0 | 15.35 | H/T for voltage regulation
|  | 2013-09-26 | 13:18 | 2013-09-29 | 21:14 | 0 | 0 | 0 | 79.9333 | H/T for voltage regulation
|  | 2013-09-30 | 7:12 | 2013-09-30 | 23:00 | 0 | 0 | 0 | 15.8 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 277.15
2 | BIDADI BUS REACTOR - I | 2013-09-25 | 8:50 | 2013-09-25 | 22:04 | 0 | 0 | 0 | 13.2333 | H/T for voltage regulation | 100
|  | 2013-09-26 | 13:16 | 2013-09-26 | 22:33 | 0 | 0 | 0 | 9.2833 | H/T for voltage regulation
|  | 2013-09-27 | 6:58 | 2013-09-27 | 22:13 | 0 | 0 | 0 | 15.25 | H/T for voltage regulation
|  | 2013-09-28 | 6:34 | 2013-09-29 | 21:12 | 0 | 0 | 0 | 38.6333 | H/T for voltage regulation
|  | 2013-09-30 | 7:10 | 2013-09-30 | 23:04 | 0 | 0 | 0 | 15.9 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 92.3
3 | HASSAN BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | HIRIYUR BUS REACTOR - I | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
5 | HOSUR BUS REACTOR - I | 2013-09-01 | 0:00 | 2013-09-01 | 21:49 | 0 | 0 | 0 | 21.8167 | H/T for voltage regulation | 100
|  | 2013-09-02 | 8:13 | 2013-09-02 | 22:54 | 0 | 0 | 0 | 14.6833 | H/T for voltage regulation
|  | 2013-09-05 | 7:02 | 2013-09-05 | 22:49 | 0 | 0 | 0 | 15.7833 | H/T for voltage regulation
|  | 2013-09-06 | 8:20 | 2013-09-06 | 22:43 | 0 | 0 | 0 | 14.3833 | H/T for voltage regulation
|  | 2013-09-10 | 18:40 | 2013-09-10 | 21:37 | 0 | 0 | 0 | 2.95 | H/T for voltage regulation
|  | 2013-09-11 | 19:36 | 2013-09-12 | 23:26 | 0 | 0 | 0 | 27.8333 | H/T for voltage regulation
|  | 2013-09-13 | 7:11 | 2013-09-13 | 22:39 | 0 | 0 | 0 | 15.4667 | H/T for voltage regulation
|  | 2013-09-14 | 8:06 | 2013-09-14 | 22:49 | 0 | 0 | 0 | 14.7167 | H/T for voltage regulation
|  | 2013-09-16 | 7:32 | 2013-09-16 | 21:45 | 0 | 0 | 0 | 14.2167 | H/T for voltage regulation
|  | 2013-09-18 | 8:06 | 2013-09-18 | 21:51 | 0 | 0 | 0 | 13.75 | H/T for voltage regulation
|  | 2013-09-19 | 8:17 | 2013-09-19 | 22:21 | 0 | 0 | 0 | 14.0667 | H/T for voltage regulation
|  | 2013-09-20 | 6:40 | 2013-09-20 | 22:47 | 0 | 0 | 0 | 16.1167 | H/T for voltage regulation
|  | 2013-09-21 | 7:03 | 2013-09-21 | 22:51 | 0 | 0 | 0 | 15.8 | H/T for voltage regulation
|  | 2013-09-22 | 8:05 | 2013-09-30 | 0:03 | 0 | 0 | 0 | 183.9667 | H/T for voltage regulation
|  | 2013-09-30 | 7:03 | 2013-09-30 | 22:53 | 0 | 0 | 0 | 15.8333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 401.3833
6 | KARAIKUDI BUS REACTOR - I | 2013-09-05 | 9:34 | 2013-09-05 | 18:35 | 0 | 0 | 0 | 9.0167 | H/T for voltage regulation | 100
|  | 2013-09-07 | 11:33 | 2013-09-07 | 22:03 | 0 | 0 | 0 | 10.5 | H/T for voltage regulation
|  | 2013-09-24 | 16:23 | 2013-09-24 | 22:34 | 0 | 0 | 0 | 6.1833 | H/T for voltage regulation
|  | 2013-09-25 | 10:12 | 2013-09-26 | 22:19 | 0 | 0 | 0 | 36.1167 | H/T for voltage regulation
|  | 2013-09-27 | 16:20 | 2013-09-27 | 22:19 | 0 | 0 | 0 | 5.9833 | H/T for voltage regulation
|  | 2013-09-28 | 18:30 | 2013-09-29 | 21:26 | 0 | 0 | 0 | 26.9333 | H/T for voltage regulation
|  | 2013-09-30 | 9:40 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 14.3333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 109.0667
7 | KOCHI BUS REACTOR I | 2013-09-05 | 7:04 | 2013-09-06 | 22:57 | 0 | 0 | 0 | 39.8833 | H/T for voltage regulation | 100
|  | 2013-09-07 | 11:33 | 2013-09-07 | 22:06 | 0 | 0 | 0 | 10.55 | H/T for voltage regulation
|  | 2013-09-12 | 18:51 | 2013-09-13 | 22:49 | 0 | 0 | 0 | 27.9667 | H/T for voltage regulation
|  | 2013-09-23 | 19:27 | 2013-09-23 | 22:41 | 0 | 0 | 0 | 3.2333 | H/T for voltage regulation
|  | 2013-09-24 | 16:21 | 2013-09-24 | 22:25 | 0 | 0 | 0 | 6.0667 | H/T for voltage regulation
|  | 2013-09-25 | 16:37 | 2013-09-26 | 22:39 | 0 | 0 | 0 | 30.0333 | H/T for voltage regulation
|  | 2013-09-27 | 16:15 | 2013-09-27 | 22:36 | 0 | 0 | 0 | 6.35 | H/T for voltage regulation
|  | 2013-09-28 | 18:30 | 2013-09-29 | 21:20 | 0 | 0 | 0 | 26.8333 | H/T for voltage regulation
|  | 2013-09-30 | 18:42 | 2013-09-30 | 23:21 | 0 | 0 | 0 | 4.65 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 155.5667
8 | KOLAR BUS REACTOR - I | 2013-09-02 | 8:11 | 2013-09-02 | 22:51 | 0 | 0 | 0 | 14.6667 | H/T for voltage regulation | 100
|  | 2013-09-04 | 18:49 | 2013-09-04 | 22:58 | 0 | 0 | 0 | 4.15 | H/T for voltage regulation
|  | 2013-09-05 | 7:00 | 2013-09-05 | 22:50 | 0 | 0 | 0 | 15.8333 | H/T for voltage regulation
|  | 2013-09-18 | 9:45 | 2013-09-18 | 21:48 | 0 | 0 | 0 | 12.05 | H/T for voltage regulation
|  | 2013-09-19 | 8:17 | 2013-09-19 | 21:32 | 0 | 0 | 0 | 13.25 | H/T for voltage regulation
|  | 2013-09-23 | 10:55 | 2013-09-23 | 22:21 | 0 | 0 | 0 | 11.4333 | H/T for voltage regulation
|  | 2013-09-25 | 9:01 | 2013-09-25 | 22:02 | 0 | 0 | 0 | 13.0167 | H/T for voltage regulation
|  | 2013-09-26 | 13:09 | 2013-09-26 | 22:04 | 0 | 0 | 0 | 8.9167 | H/T for voltage regulation
|  | 2013-09-27 | 6:55 | 2013-09-27 | 21:31 | 0 | 0 | 0 | 14.6 | H/T for voltage regulation
|  | 2013-09-28 | 6:34 | 2013-09-29 | 21:09 | 0 | 0 | 0 | 38.5833 | H/T for voltage regulation
|  | 2013-09-30 | 18:35 | 2013-09-30 | 22:52 | 0 | 0 | 0 | 4.2833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 150.7833
9 | MYSORE BUS REACTOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
10 | NARENDRA BUS REACTOR | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | PALAKKAD BUS REACTOR - I | 2013-09-07 | 11:35 | 2013-09-07 | 22:10 | 0 | 0 | 0 | 10.5833 | H/T for voltage regulation | 100
|  | 2013-09-12 | 18:48 | 2013-09-14 | 23:00 | 0 | 0 | 0 | 52.2 | H/T for voltage regulation
|  | 2013-09-23 | 19:25 | 2013-09-23 | 22:34 | 0 | 0 | 0 | 3.15 | H/T for voltage regulation
|  | 2013-09-24 | 16:17 | 2013-09-24 | 22:26 | 0 | 0 | 0 | 6.15 | H/T for voltage regulation
|  | 2013-09-25 | 16:36 | 2013-09-26 | 22:37 | 0 | 0 | 0 | 30.0167 | H/T for voltage regulation
|  | 2013-09-27 | 16:13 | 2013-09-27 | 22:17 | 0 | 0 | 0 | 6.0667 | H/T for voltage regulation
|  | 2013-09-28 | 18:28 | 2013-09-29 | 21:18 | 0 | 0 | 0 | 26.8333 | H/T for voltage regulation
|  | 2013-09-30 | 18:36 | 2013-09-30 | 23:14 | 0 | 0 | 0 | 4.6333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 139.6333
12 | SALEM BUS REACTOR - I | 2013-09-24 | 16:09 | 2013-09-29 | 21:25 | 0 | 0 | 0 | 125.2667 | H/T for voltage regulation | 100
|  | 2013-09-30 | 7:09 | 2013-09-30 | 23:13 | 0 | 0 | 0 | 16.0667 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 141.3333
13 | SRIPERUMBUDUR BUS REACTOR - I | 2013-09-02 | 8:18 | 2013-09-07 | 21:50 | 0 | 0 | 0 | 133.5333 | H/T for voltage regulation | 100
|  | 2013-09-21 | 18:26 | 2013-09-21 | 23:00 | 0 | 0 | 0 | 4.5667 | H/T for voltage regulation
|  | 2013-09-23 | 9:23 | 2013-09-29 | 21:33 | 0 | 0 | 0 | 156.1667 | H/T for voltage regulation
|  | 2013-09-30 | 18:36 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 5.4 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 299.6667
14 | THIRUNELVELI BUS REACTOR - I | 2013-09-05 | 18:47 | 2013-09-05 | 22:52 | 0 | 0 | 0 | 4.0833 | H/T for voltage regulation | 100
|  | 2013-09-24 | 16:16 | 2013-09-24 | 22:15 | 0 | 0 | 0 | 5.9833 | H/T for voltage regulation
|  | 2013-09-25 | 16:33 | 2013-09-25 | 22:10 | 0 | 0 | 0 | 5.6167 | H/T for voltage regulation
|  | 2013-09-27 | 16:18 | 2013-09-27 | 21:39 | 0 | 0 | 0 | 5.35 | H/T for voltage regulation
|  | 2013-09-28 | 18:47 | 2013-09-28 | 23:07 | 0 | 0 | 0 | 4.3333 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 25.3667
15 | THIRUNELVELI BUS REACTOR - II | 2013-09-05 | 18:49 | 2013-09-05 | 22:56 | 0 | 0 | 0 | 4.1167 | H/T for voltage regulation | 100
|  | 2013-09-24 | 16:17 | 2013-09-24 | 22:20 | 0 | 0 | 0 | 6.05 | H/T for voltage regulation
|  | 2013-09-25 | 16:34 | 2013-09-25 | 22:07 | 0 | 0 | 0 | 5.55 | H/T for voltage regulation
|  | 2013-09-27 | 16:18 | 2013-09-27 | 21:36 | 0 | 0 | 0 | 5.3 | H/T for voltage regulation
|  | 2013-09-28 | 18:47 | 2013-09-28 | 23:10 | 0 | 0 | 0 | 4.3833 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 25.4
16 | Kolar Line Reactor at Bangalore | 2013-09-01 | 0:00 | 2013-09-01 | 21:48 | 0 | 0 | 0 | 21.8 | H/T for voltage regulation | 100
|  | 2013-09-18 | 8:10 | 2013-09-18 | 21:49 | 0 | 0 | 0 | 13.65 | H/T for voltage regulation
|  | 2013-09-25 | 8:47 | 2013-09-30 | 0:02 | 0 | 0 | 0 | 111.25 | H/T for voltage regulation
|  | 2013-09-30 | 9:47 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 14.2167 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 160.9167
17 | Neyveli TS II Exp Line Reactor at Pugalur | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
18 | Neyveli TS II Line Reactor at Pugalur | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
19 | Thirunelveli 1 Line Reactor at Udumalpet | 2013-09-05 | 19:17 | 2013-09-05 | 22:57 | 0 | 0 | 0 | 3.6667 | H/T for voltage regulation | 100
|  | 2013-09-06 | 9:42 | 2013-09-08 | 21:56 | 0 | 0 | 0 | 60.2333 | H/T for voltage regulation
|  | 2013-09-24 | 16:10 | 2013-09-24 | 22:20 | 0 | 0 | 0 | 6.1667 | H/T for voltage regulation
|  | 2013-09-25 | 17:11 | 2013-09-30 | 0:03 | 0 | 0 | 0 | 102.8667 | H/T for voltage regulation
|  | 2013-09-30 | 9:42 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 14.3 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 187.2333
20 | Thirunelveli 2 Line Reactor at Udumalpet | 2013-09-05 | 19:19 | 2013-09-05 | 22:57 | 0 | 0 | 0 | 3.6333 | H/T for voltage regulation | 100
|  | 2013-09-06 | 9:44 | 2013-09-07 | 21:53 | 0 | 0 | 0 | 36.15 | H/T for voltage regulation
|  | 2013-09-24 | 16:11 | 2013-09-24 | 22:20 | 0 | 0 | 0 | 6.15 | H/T for voltage regulation
|  | 2013-09-25 | 17:12 | 2013-09-30 | 0:04 | 0 | 0 | 0 | 102.8667 | H/T for voltage regulation
|  | 2013-09-30 | 9:42 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 14.3 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 163.1
21 | Udumalpet 1 Line Reactor at Thirunelveli | 2013-09-05 | 18:56 | 2013-09-05 | 22:57 | 0 | 0 | 0 | 4.0167 | H/T for voltage regulation | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 4.0167
22 | Udumalpet 2 Line Reactor at Thirunelveli | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
23 | Vallur 1 Line Reactor at Kalivandapattu | 2013-09-01 | 0:00 | 2013-09-01 | 21:50 | 0 | 0 | 0 | 21.8333 | H/T for voltage regulation | 100
|  | 2013-09-02 | 7:47 | 2013-09-08 | 21:38 | 0 | 0 | 0 | 157.85 | H/T for voltage regulation
|  | 2013-09-18 | 8:20 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 303.6667 | H/T for voltage regulation
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 483.35

## Non Sw Reactors
Element wise availability for the month of September-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
Non Switchable Shunt Reactors
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | Chittoor Line reactor at Sriperumbudur (Non switchable) | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | SV Chatram Line reactor at Sriperumbudur (Non switchable) | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
3 | Trichy Line reactor at Madurai (Non switchable) | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
4 | Karaikudi Line reactor at Madurai (Non switchable) | 2013-09-01 | 0:00 | 2013-09-03 | 15:22 | 0 | 0 | 0 | 63.3667 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 63.3667
5 | Bangalore Line reactor at Salem (Non switchable) | 2013-09-01 | 0:00 | 2013-09-21 | 16:22 | 0 | 0 | 0 | 496.3667 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 496.3667
6 | Neyveli 1 Line reactor at Salem (Non switchable) | 2013-09-01 | 0:00 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
7 | Gooty Line reactor at Bangalore (Non switchable) | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
8 | Palakkad 1 Line reactor at Trichur (Non switchable) | 2013-09-01 | 0:00 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
9 | Palakkad 2 Line reactor at Trichur (Non switchable) | 2013-09-01 | 0:00 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
10 | Neyveli TS-2 Line reactor at Trichy (Non switchable) | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
11 | Neyveli TS-1 Exp Line reactor at Trichy (Non switchable) | 2013-09-01 | 0:00 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
12 | Thirunelveli 1 Line reactor at Trivendrum (Non switchable) | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
13 | Salem 1 Line reactor at Udumalpet (Non switchable) | 2013-09-01 | 0:00 | 2013-10-01 | 0:00 | 0 | 0 | 0 | 720 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 720
14 | Salem 2 Line reactor at Udumalpet (Non switchable) | 2013-09-01 | 0:00 | 2013-09-01 | 15:50 | 0 | 0 | 0 | 15.8333 | Hand tripped as per SRLDC instruction for voltage regulation in the system. | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 15.8333

## HVDC
Element wise availability for the month of September-2013
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
HVDC POLES
Sl No: | Name of the Transmission line | OUTAGE |  | RESTORATION |  | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | REASON OF OUTAGE | % Availability
|  | Date | Time | Date | Time | POWERGRID | OTHERS | System Constraints | Deemed Available
1 | TALCHER - KOLAR HVDC POLE - I | 2013-09-10 | 23:21 | 2013-09-10 | 23:21 | 0 | 0 | 0 | 0 | LFL and DC line fault recovery sequence operated at 214.96 kM from Talcher end (Tower no. 586). | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0
2 | TALCHER - KOLAR HVDC POLE - II | [9 empty] | 100
|  | Sub Total --> |  |  |  | 0 | 0 | 0 | 0