## SOP
[20 empty] | Prepared by | Sarat Chandra D., Sr. Engr.
Standard of Performance data for the month of JANUARY - 2017
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl.No | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2017-01-06 | 8:35 | 2017-01-06 | 18:34 | -- | -- | -- | 0 | 0 | 0 | 9.9833 | N/A | N/A | N/A | Shut down availed by M/s NTPC for replacement of Y-ph Lightning Arrester at Kayamkulam end vide SRLDC code no. CR-01/165. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.9833
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2017-01-07 | 8:47 | 2017-01-07 | 18:30 | -- | -- | -- | 0 | 0 | 0 | 9.7167 | N/A | N/A | N/A | Shut down availed by M/s NTPC for maintenance of equipments at Kayamkulam end vide SRLDC code no. CR-01/198. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.7167
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2017-01-18 | 11:19 | 2017-01-18 | 17:36 | -- | -- | -- | 0 | 0 | 0 | 6.2833 | N/A | N/A | N/A | Shut down availed by M/s KSEB for relay testing works at Kundra end vide SRLDC code no. CR-01/461. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.2833
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | 2017-01-19 | 9:56 | 2017-01-19 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 8.3 | N/A | N/A | N/A | Shut down availed by M/s KSEB for commissioning of bus bar protection panel at Pallom end vide SRLDC Code no. CR-01/507. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.3
8 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
9 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
11 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
15 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- | 2017-01-29 | 5:15 | 2017-01-29 | 6:31 | -- | -- | -- | 0 | 1.2667 | 0 | 0 | -- | -- | -- | Auto reclosure successful on Y-G fault at Sirusseri end but tripped at Bhavini end due to non-enabling of auto reclosure at Bhavini end, FLR: 17.1km from Sirusseri end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.2667 | 0 | 0
16 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
18 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
20 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
21 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L24 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L25 | CUDDAPAH - NP KUNTA I | 61.233 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
24 | SR2L26 | GOOTY - BANGALORE | 301.667 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L27 | HASSAN - MYSORE I | 95.875 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L28 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L29 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L30 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L31 | HOSUR-SALEM II | 125.325 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
30 | SR2L32 | HOSUR-SALEM | 126.339 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
31 | SR2L33 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2017-01-26 | 20:57 | 2017-01-27 | 18:34 | -- | -- | -- | 0 | 0 | 0 | 21.6167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/738. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 21.6167
32 | SR2L34 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | 2017-01-09 | 21:32 | 2017-01-17 | 11:27 | -- | -- | -- | 0 | 0 | 0 | 181.9167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/275. |  | 100
[6 empty] | 2017-01-27 | 21:21 | 2017-01-28 | 17:37 |  |  |  | 0 | 0 | 0 | 20.2667 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/784.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 202.1833
33 | SR2L35 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2017-01-07 | 11:43 | 2017-01-09 | 9:43 | -- | -- | -- | 0 | 0 | 0 | 46 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending oil leackage in Circuit Breaker at Guttur end vide SRLDC code no. CR-01/206. |  | 100
[5 empty] | -- | 2017-01-09 | 15:00 | 2017-01-09 | 20:23 | -- | -- | -- | 0 | 0 | 0 | 5.3833 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending oil leackage in Circuit Breaker at Guttur end vide SRLDC code no. CR-01/263.
[5 empty] | -- | 2017-01-17 | 11:47 | 2017-01-17 | 15:11 | -- | -- | -- | 0 | 0 | 0 | 3.4 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for jumper replacement works in KPTCL portion of the line vide SRLDC code no. CR-01/428.
[6 empty] | 2017-01-19 | 22:15 | 2017-01-20 | 11:10 |  |  |  | 0 | 0 | 0 | 12.9167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/534.
[6 empty] | Sub Total --> |  |  |  | -- | -- | -- | 0 | 0 | 0 | 67.7
34 | SR2L36 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2017-01-23 | 10:40 | 2017-01-23 | 17:14 | -- | -- | -- | 0 | 0 | 0 | 6.5667 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending quarterly maintenance works at Guttur end vide SRLDC code no. CR-01/624. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.5667
35 | SR2L37 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-04 | 8:26 | -- | -- | -- | 0 | 0 | 0 | 80.4333 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/642. |  | 100
[6 empty] | 2017-01-09 | 2:03 | 2017-01-09 | 7:40 |  |  |  | 0 | 0 | 0 | 5.6167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-01/146.
[6 empty] | 2017-01-09 | 1:55 | 2017-01-09 | 2:03 |  |  |  | 0 | 0 | 0.13333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Karaikudi end. Direct trip signal received at Trichy end.
[6 empty] | 2017-01-22 | 23:16 | 2017-01-31 | 17:12 |  |  |  | 0 | 0 | 0 | 209.9333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/618.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.13333 | 295.9833 | -- | -- | --
36 | SR2L38 | KOLAR - BANGALORE | 97.391 | SR-II | -- | 2017-01-07 | 9:28 | 2017-01-07 | 17:14 | -- | -- | -- | 0 | 0 | 0 | 7.7667 | -- | -- | -- | Shut down availed for commissioning of Fire Fighting system for Line Reactor at Somanahalli under addcap works vide SRLDC code no. CR-01/200. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.7667
37 | SR2L39 | KOLAR - HOODY - I | 51.067 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L40 | KOLAR - HOODY - II | 51.067 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L41 | KOLAR - HOSUR - I | 69 | SR-II | -- | 2017-01-04 | 12:03 | 2017-01-04 | 12:37 | -- | -- | -- | 0 | 0 | 0.56667 | 0 | N/A | N/A | N/A | Emergency Shut down availed for removing foreign object hanging from Y-phase conductor at location no. 05 vide SRLDC code no. CR-01/92. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.56667 | 0
40 | SR2L42 | KOLAR - HOSUR - II | 69 | SR-II | -- | 2017-01-04 | 11:55 | 2017-01-04 | 12:38 | -- | -- | -- | 0 | 0 | 0.71667 | 0 | N/A | N/A | N/A | Emergency Shut down availed for removing foreign object hanging from Y-phase conductor at location no. 05 vide SRLDC code no. CR-01/91. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.71667 | 0
41 | SR2L43 | KOLAR - THIRUVALAM - I | 153.195 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L99 | KUDGI - KOLHAPUR - I | 189.799 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
43 | SR2L100 | KUDGI - KOLHAPUR - II | 189.799 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L44 | MADURAI - TUTICORIN POOLING STN I | 115.602 | SR-II | -- | 2017-01-11 | 11:37 | 2017-01-11 | 15:27 | -- | -- | -- | 3.8333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of R-ph CVT at Madurai end having violation in voltage drift vide SRLDC code no. CR-01/322. |  | 99.4848
[6 empty] | Sub Total --> | [6 empty] | 3.8333 | 0 | 0 | 0
45 | SR2L45 | MADURAI - TUTICORIN POOLING STN II | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L46 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L47 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2017-01-31 | 10:28 | 2017-01-31 | 19:23 | -- | -- | -- | 0 | 0 | 0 | 8.9167 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for wavetrap, LA and CVT insulator cleaning at Kudamkulam end vide SRLDC code no. CR-01/891. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.9167
48 | SR2L97 | MYSORE - KOZHIKODE I | 215.524 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR2L98 | MYSORE - KOZHIKODE II | 215.524 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR2L48 | 'NAGAPATTINAM PS - TRICHY - I | 158.7 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L96 | 'NAGAPATTINAM PS - TRICHY - II | 158.7 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
52 | SR2L49 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-18 | 10:54 | -- | -- | -- | 0 | 0 | 0 | 418.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/829. |  | 100
[6 empty] | 2017-01-20 | 23:19 | 2017-01-24 | 7:19 |  |  |  | 0 | 0 | 0 | 80 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/574.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 498.9
53 | SR2L50 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2017-01-24 | 7:45 | 2017-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 184.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/638. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 184.25
54 | SR2L101 | NARENDRA - KUDGI I | 176.133 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-03 | 12:50 | -- | -- | -- | 0 | 0 | 0 | 60.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/637. |  | 100
[6 empty] | 2017-01-11 | 11:13 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 492.7833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/321.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 553.6167
55 | SR2L102 | NARENDRA - KUDGI II | 176.133 | SR-II | -- | 2017-01-04 | 21:51 | 2017-01-11 | 10:51 | -- | -- | -- | 0 | 0 | 0 | 157 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/120. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 157
56 | SR2L51 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
57 | SR2L52 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
58 | SR2L53 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | 2017-01-20 | 9:00 | 2017-01-20 | 13:54 | -- | -- | -- | 4.9 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for conductor repair works vide SRLDC code no. CR-01/539. |  | 99.3414
[6 empty] | Sub Total --> | [6 empty] | 4.9 | 0 | 0 | 0
59 | SR2L54 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | 2017-01-21 | 9:03 | 2017-01-21 | 12:12 | -- | -- | -- | 3.15 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for jumper tightening works at loc no. 340 vide SRLDC code no. CR-01/579. |  | 99.5766
[6 empty] | Sub Total --> | [6 empty] | 3.15 | 0 | 0 | 0
60 | SR2L55 | NEYVELI - BAHOOR | 52.5 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SRL56 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SRL57 | NEYVELI TS II - NAGAPATTINAM PS - I | 49.217 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L58 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L59 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2017-01-25 | 9:09 | 2017-01-25 | 18:04 | -- | -- | -- | 0 | 0 | 0 | 8.9167 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-01/682. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.9167
65 | SR2L60 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L61 | NEYVELI TS-I EXPANSION - NAGAPATTINAM PS - I | 171.95 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L62 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2017-01-17 | 9:10 | 2017-01-18 | 16:22 | -- | -- | -- | 0 | 0 | 0 | 31.2 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-01/423. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 31.2
68 | SR2L63 | NEYVELI-SALEM - I | 174.949 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L64 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
70 | SR2L103 | NP KUNTA - KOLAR I | 130.702 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
71 | SR2L65 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | 2017-01-05 | 14:16 | 2017-01-05 | 17:13 | -- | -- | -- | 0 | 0 | 2.95 | 0 | N/A | N/A | N/A | Tripped on R-B (ph-ph) fault due to a foreign object getting entangled in line at a distance of 10 Km from Trichur end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 2.95 | 0
72 | SR2L66 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L67 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | 2017-01-21 | 9:02 | 2017-01-21 | 18:34 | -- | -- | -- | 0 | 0 | 9.5333 | 0 | N/A | N/A | N/A | Shut down availed for replacement of flash over string with CLR insulator in polluted stretch affected during Vardah cyclone at loc. 541 vide SRLDC code no. CR-01/577. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 9.5333 | 0
74 | SR2L68 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
75 | SR2L69 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L105 | SALEM - SALEM POOLING STN I | 59.04 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L106 | SALEM - SALEM POOLING STN II | 59.04 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L70 | SALEM - UDUMALPET I | 150.543 | SR-II | Insulator decapping | 2017-01-21 | 12:33 | 2017-01-21 | 19:07 | -- | -- | 0.27361 | 6.5667 | 0 | 0 | 0 | 1 | N | -0.72639 | Tripped due to B-phase insulator decapping at loc No. 423. |  | 99.1174
[6 empty] | Sub Total --> | [6 empty] | 6.5667 | 0 | 0 | 0
79 | SR2L71 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L72 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L73 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | 2017-01-10 | 10:52 | 2017-01-10 | 16:08 | -- | -- | -- | 0 | 0 | 0 | 5.2667 | N/A | N/A | N/A | Shut down availed by M/s TNEB for maintenance works at SV Chatram end vide SRLDC code no. CR-01/287. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.2667
82 | SR2L74 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | 2017-01-28 | 23:29 | 2017-01-29 | 23:17 | -- | -- | -- | 0 | 0 | 0 | 23.8 | N/A | N/A | N/A | Shut down availed by M/s KSEB for bus strengthening works at Edamon end vide SRLDC code no. CR-01/831. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.8
83 | SR2L75 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2017-01-28 | 23:29 | 2017-01-29 | 23:14 | -- | -- | -- | 0 | 0 | 0 | 23.75 | N/A | N/A | N/A | Shut down availed by M/s KSEB for bus strengthening works at Edamon end vide SRLDC code no. CR-01/832. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.75
84 | SR2L110 | THIRUNELVELI - EDAMON - III | 81.94 | SR-II | -- | 2017-01-28 | 23:29 | 2017-01-29 | 23:17 | -- | -- | -- | 0 | 0 | 0 | 23.8 | N/A | N/A | N/A | Shut down availed by M/s KSEB for bus strengthening works at Edamon end vide SRLDC code no. CR-01/831. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.8
85 | SR2L111 | THIRUNELVELI - EDAMON - IV | 81.94 | SR-II | -- | 2017-01-28 | 23:29 | 2017-01-29 | 23:14 | -- | -- | -- | 0 | 0 | 0 | 23.75 | N/A | N/A | N/A | Shut down availed by M/s KSEB for bus strengthening works at Edamon end vide SRLDC code no. CR-01/832. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.75
86 | SR2L76 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2017-01-31 | 10:28 | 2017-01-31 | 19:23 | -- | -- | -- | 0 | 0 | 0 | 8.9167 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for wavetrap, LA and CVT insulator cleaning at Kudamkulam end vide SRLDC code no. CR-01/891. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.9167
87 | SR2L77 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2L78 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2017-01-02 | 8:40 | 2017-01-04 | 17:50 | -- | -- | -- | 0 | 0 | 0 | 57.1667 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for cleaning of support insulators at Kudankulam end vide SRLDC code no. CR-01/20. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 57.1667
89 | SR2L79 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2L80 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2L81 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
92 | SR2L82 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | ` | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2L83 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2L84 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2L85 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2L86 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2L87 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | 2017-01-07 | 10:20 | 2017-01-07 | 11:20 | -- | -- | -- | 0 | 0 | 1 | 0 | N/A | N/A | N/A | Emergency Shutdown availed for removing foreign object in the middle phase between location No. 213-214 vide SRLDC code no. CR01/202. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1 | 0
98 | SR2L88 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-03 | 12:51 | -- | -- | -- | 0 | 0 | 0 | 60.85 | -- | -- | -- | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-12/623. |  | 100
[6 empty] | 2017-01-21 | 21:50 | 2017-01-28 | 18:14 |  |  |  | 0 | 0 | 0 | 164.4 |  |  |  | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-01/383.
[6 empty] | 2017-01-21 | 21:45 | 2017-01-21 | 21:50 |  |  |  | 0 | 0 | 0.083333 | 0 |  |  |  | Line tripped on operation of over voltage protection at Karaikudi end. Direct trip signal received at Trichy end.
[6 empty] | 2017-01-29 | 0:19 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 71.6833 |  |  |  | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-01/538.
[6 empty] | 2017-01-29 | 0:13 | 2017-01-29 | 0:19 |  |  |  | 0 | 0 | 0.1 | 0 |  |  |  | Line tripped on operation of over voltage protection at Karaikudi end. Direct trip signal received at Trichy end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.18333 | 296.9333
99 | SR2L89 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2L90 | TUTICORIN JV TPS - TUTICORIN POOLING STN I | 127.232 | SR-II | -- | 2017-01-30 | 13:56 | 2017-01-30 | 16:10 | -- | -- | -- | 0 | 0 | 0 | 2.2333 | -- | -- | -- | Shut down availed by M/s NTPL for attending oil leakage in CVT at NTPL end vide SRLDC code no. CR-01/871. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.2333
101 | SR2L107 | TUTICORIN JV TPS - TUTICORIN POOLING STN II | 127.232 | SR-II |  | 2017-01-01 | 18:10 | 2017-01-01 | 23:26 |  |  |  | 0 | 0 | 0 | 5.2667 | N/A | N/A | N/A | Shut Down availed by M/s NTPL for replacement of R-ph LA at NTPL end vide SRLDC code no. CR-01/08. |  | 100
[6 empty] | 2017-01-02 | 10:56 | 2017-01-02 | 19:20 |  |  |  | 0 | 0 | 0 | 8.4 |  |  |  | Shut down availed by M/s NTPL for replacement of Lightning Arrester conductor at NTPL end vide SRLDC code no. CR-01/26.
[6 empty] | 2017-01-20 | 10:32 | 2017-01-20 | 13:02 |  |  |  | 0 | 0 | 0 | 2.5 |  |  |  | Shut down availed by M/s NTPL for attending hot spot in R phase wave trap at NTPL end vide SRLDC code no. CR-01/548.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16.1667
102 | SR2L108 | TUTICORIN POOLING STN - SALEM POOLING STN I | 368.84 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2L109 | TUTICORIN POOLING STN - SALEM POOLING STN II | 368.84 | SR-II |  | 2017-01-26 | 20:51 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 123.15 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/737. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 123.15
104 | SR2L91 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2L92 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2L93 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | 2017-01-24 | 11:21 | 2017-01-24 | 16:34 | -- | -- | -- | 5.2167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending critical hotspot at Y-Phase wavetrap top terminal connector vide SRLDC code no. CR-01/652. |  | 99.2988
[6 empty] | Sub Total --> | [6 empty] | 5.2167 | 0 | 0 | 0
107 | SR2L94 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | 2017-01-13 | 18:29 | 2017-01-13 | 18:29 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-G (Ph-earth) transient fault. FLR: 6.20 KM from Kalivanthapattu end. |  | 99.5811
[6 empty] | 2017-01-19 | 10:22 | 2017-01-19 | 13:29 |  |  |  | 3.1167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of CVT at Kalivantapattu end vide SRLDC code no. CR-01/512.
[6 empty] | Sub Total --> | [6 empty] | 3.1167 | 0 | 0 | 0
108 | SR2L95 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | 2017-01-29 | 10:00 | 2017-01-29 | 17:07 | -- | -- | -- | 0 | 0 | 0 | 7.1167 | N/A | N/A | N/A | Shut down availed for construction works in connection with replacement of ICT-1 vide SRLDC code no. CR-01/837. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.1167
112 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2017-01-20 | 14:37 | 2017-01-20 | 15:06 | -- | -- | -- | 0 | 0.48333 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of Bus Bar protection at 230KV Somanahalli SS of M/s KPTCL. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.48333 | 0 | 0
113 | SR2T51 | BANGALORE ICT - III | 501 | SR-II | -- | 2017-01-20 | 14:37 | 2017-01-20 | 15:11 | -- | -- | -- | 0 | 0.56667 | 0 | 0 | N/A | N/A | N/A | Tripped due to operation of Bus Bar protection at 230KV Somanahalli SS of M/s KPTCL. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.56667 | 0 | 0
114 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T50 | KALIVANDAPATTU ICT - III | 500 | SR-II | -- | 2017-01-01 | 0:00 | 2017-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | -- | -- | -- | Hand tripped as per SRLDC instruction for power regulation in the system vide SRLDC code no. CR-10/230. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
126 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-11/767. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
129 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-11/767. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T46 | KOZHIKODE - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2T47 | KOZHIKODE - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
135 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
136 | SR2T53 | MADURAI ICT - III | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
139 | SR2T52 | MYSORE ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-11/ 798. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
140 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
141 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for measurement of dummy plates in connection with replacement of 315 MVA ICT by 500 MVA vide SRLDC code no. CR-11/364. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | 2017-01-19 | 8:56 | 2017-01-19 | 13:38 | -- | -- | -- | 4.7 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC Code no. CR-01/498. |  | 99.3683
[6 empty] | Sub Total --> | [6 empty] | 4.7 | 0 | 0 | 0
143 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | 2017-01-20 | 9:09 | 2017-01-20 | 13:27 | -- | -- | -- | 4.3 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-01/541. |  | 99.422
[6 empty] | Sub Total --> | [6 empty] | 4.3 | 0 | 0 | 0
144 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | 2017-01-06 | 10:21 | 2017-01-06 | 14:44 | -- | -- | -- | 4.3833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-01/171. |  | 99.4108
[6 empty] | Sub Total --> | [6 empty] | 4.3833 | 0 | 0 | 0
145 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
147 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
150 | SR2T36 | THIRUVALAM ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2T37 | THIRUVALAM ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
152 | SR2T38 | TRICHY ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
153 | SR2T39 | TRICHY ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
154 | SR2T40 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
155 | SR2T41 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.9 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-11/311. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.9
156 | SR2T42 | TRIVANDRUM - ICT III | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
157 | SR2T48 | TUMKUR - ICT I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
158 | SR2T49 | TUMKUR - ICT II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
159 | SR2T43 | UDUMALPET ICT - I | 315 | SR-II | -- | 2017-01-25 | 10:22 | 2017-01-25 | 13:16 | -- | -- | -- | 0 | 0 | 0 | 2.9 | N/A | N/A | N/A | Shut down availed by M/s TNEB for rewiring of busbar CT circuit to new busbar panel vide SRLDC code no. CR-01/685. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.9
160 | SR2T44 | UDUMALPET ICT - II | 315 | SR-II | -- | 2017-01-25 | 14:48 | 2017-01-25 | 18:17 | -- | -- | -- | 0 | 0 | 0 | 3.4833 | N/A | N/A | N/A | Shut down availed by M/s TNEB for rewiring of busbar CT circuit to new busbar panel vide SRLDC code no. CR-01/703. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.4833
161 | SR2T45 | UDUMALPET ICT - III | 315 | SR-II | -- | 2017-01-17 | 10:04 | 2017-01-17 | 17:12 | -- | -- | -- | 0 | 0 | 0 | 7.1333 | N/A | N/A | N/A | Shut down availed by M/s TNEB for busbar protection wiring checking at 230kV Myvadi SS vide SRLDC code no. CR-01/425. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.1333
162 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-01 | 22:13 | -- | -- | -- | 0 | 0 | 0 | 22.2167 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/939. |  | 100
[6 empty] | 2017-01-02 | 9:14 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 710.7667 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/02.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 732.9833
163 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-01 | 6:44 | -- | -- | -- | 0 | 0 | 0 | 6.7333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/626. |  | 100
[5 empty] | -- | 2017-01-02 | 9:36 | 2017-01-14 | 2:20 | -- | -- | -- | 0 | 0 | 0 | 280.7333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/03.
[6 empty] | 2017-01-16 | 10:51 | 2017-01-19 | 23:34 |  |  |  | 0 | 0 | 0 | 84.7167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/15.
[6 empty] | 2017-01-27 | 8:45 | 2017-01-29 | 0:03 |  |  |  | 0 | 0 | 0 | 39.3 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/750.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 411.4833
164 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2017-01-02 | 10:24 | 2017-01-05 | 3:29 | -- | -- | -- | 0 | 0 | 0 | 65.0833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/04. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 65.0833
165 | SR2R31 | HASSAN BUS REACTOR - II | 125 | SR-II | -- | 2017-01-27 | 11:07 | 2017-01-28 | 19:12 | -- | -- | -- | 0 | 0 | 0 | 32.0833 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/32. |  | 100
[6 empty] | 2017-01-30 | 11:05 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 36.9167 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/39.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 69
166 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
167 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2017-01-01 | 0:00 | 2017-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/950. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
168 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
169 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-14 | 2:36 | -- | -- | -- | 0 | 0 | 0 | 314.6 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/16. |  | 100
[6 empty] | 2017-01-17 | 10:52 | 2017-01-22 | 0:22 |  |  |  | 0 | 0 | 0 | 109.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/18.
[6 empty] | 2017-01-24 | 14:27 | 2017-01-24 | 22:39 |  |  |  | 0 | 0 | 0 | 8.2 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/660.
[6 empty] | 2017-01-31 | 14:54 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 9.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/909.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 441.4
170 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-01 | 21:27 | -- | -- | -- | 0 | 0 | 0 | 21.45 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/17. |  | 100
[6 empty] | 2017-01-02 | 10:43 | 2017-01-21 | 2:56 |  |  |  | 0 | 0 | 0 | 448.2167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/06.
[6 empty] | 2017-01-27 | 10:34 | 2017-01-29 | 0:02 |  |  |  | 0 | 0 | 0 | 37.4667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/30.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 507.1333
171 | SR2R28 | KUDGI BUS REACTOR - I | 125 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
172 | SR2R32 | KUDGI BUS REACTOR - II | 125 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
173 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2017-01-02 | 10:33 | 2017-01-14 | 2:05 | -- | -- | -- | 0 | 0 | 0 | 279.5333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/05. |  | 100
[5 empty] | -- | 2017-01-16 | 11:48 | 2017-01-26 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 246.4333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/16.
[6 empty] | 2017-01-27 | 10:30 | 2017-01-29 | 0:04 |  |  |  | 0 | 0 | 0 | 37.5667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/29.
[6 empty] | 2017-01-30 | 11:09 | 2017-02-01 | 0:00 |  |  |  | 0 | 0 | 0 | 36.85 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/38.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 600.3833
174 | SR2R30 | NAGAPATTINAM PS BUS REACTOR - I | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
175 | SR2R10 | NARENDRA BUS REACTOR | 50 / 125 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-23 | 19:24 | -- | -- | -- | 0 | 0 | 0 | 547.4 | N/A | N/A | N/A | Shut down availed for replacement of existing 50 MVAR reactor with 125 MVAR reactor vide SRLDC code no. CR-09/370. |  | 100
[6 empty] | 2017-01-27 | 10:37 | 2017-01-28 | 17:58 |  |  |  | 0 | 0 | 0 | 31.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/31.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 578.75
176 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2017-01-01 | 0:00 | 2017-01-14 | 2:40 | -- | -- | -- | 0 | 0 | 0 | 314.6667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-12/949. |  | 100
[6 empty] | 2017-01-17 | 10:54 | 2017-01-22 | 0:19 |  |  |  | 0 | 0 | 0 | 109.4167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/17.
[6 empty] | 2017-01-24 | 10:29 | 2017-01-24 | 22:36 |  |  |  | 0 | 0 | 0 | 12.1167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/649.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 436.2
177 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
178 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
179 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
180 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
181 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
182 | SR2R33 | TRIVENDRUM BUS REACTOR - I | 125 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
183 | SR2R29 | TUMKUR BUS REACTOR - I | 63 | SR-II | -- | 2017-01-13 | 10:41 | 2017-01-13 | 21:26 | -- | -- | -- | 0 | 0 | 0 | 10.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/331. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.75
184 | SR2R17 | TUTICORIN POOLING STN BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
185 | SR2R18 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2017-01-01 | 0:00 | 2017-02-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-08/331. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
186 | SR2R26 | Mysore 1 Line Reactor at Kozhikode | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
187 | SR2R27 | Mysore 2 Line Reactor at Kozhikode | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
188 | SR2R19 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
189 | SR2R20 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
190 | SR2R21 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2017-01-19 | 10:54 | 2017-01-22 | 23:12 | -- | -- | -- | 0 | 0 | 0 | 84.3 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/514. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 84.3
191 | SR2R22 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
192 | SR2R23 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
193 | SR2R24 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
194 | SR2R25 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
195 | SR2P1 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
196 | SR2P2 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0