## SOP
[20 empty] | Prepared by | Sarat Chandra D., Dy. Mgr.
Standard of Performance data for the month of MAY - 2018
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl.No | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2018-05-08 | 14:53 | 2018-05-08 | 15:31 | -- | -- | -- | 0 | 0 | 0 | 0.63 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of hybrid module for erection works vide SRLDC code no. CR-05/433. |  | 100
[5 empty] | -- | 2018-05-09 | 10:50 | 2018-05-09 | 11:27 | -- | -- | -- | 0 | 0 | 0 | 0.62 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of hybrid module for erection works vide SRLDC code no. CR-05/487.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.25
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2018-05-03 | 8:15 | 2018-05-03 | 17:34 | -- | -- | -- | 0 | 0 | 0 | 9.32 | N/A | N/A | N/A | Shut down availed by M/s KSEB for AMP works at Edappon end vide SRLDC code no. CR-05/106. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.32
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2018-05-09 | 10:07 | 2018-05-09 | 10:26 | -- | -- | -- | 0 | 0 | 0 | 0.32 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of hybrid module for erection works vide SRLDC code no. CR-05/482. |  | 100
[5 empty] | -- | 2018-05-09 | 11:42 | 2018-05-09 | 11:57 | -- | -- | -- | 0 | 0 | 0 | 0.25 | N/A | N/A | N/A | Shut down availed by M/s KSEB for shifting of hybrid module for erection works vide SRLDC code no. CR-05/495.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.57
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | 2018-05-16 | 7:48 | 2018-05-16 | 16:52 | -- | -- | -- | 0 | 0 | 0 | 9.07 | N/A | N/A | N/A | Shut down availed by M/s KSEB for routine maintenance works at Punnapra end vide SRLDC code no. CR-05/814. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.07
8 | SR2L114 | ALAMATHY - THIRUVALAM TN - I | 40.969 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
9 | SR2L115 | ALAMATHY - THIRUVALAM TN - II | 40.969 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
10 | SR2L112 | ALAMATHY - VALLUR - I | 36.348 | SR-II | -- | 2018-05-22 | 9:26 | 2018-05-22 | 17:35 | -- | -- | -- | 0 | 0 | 0 | 8.15 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1174. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.15
11 | SR2L113 | ALAMATHY - VALLUR - II | 36.348 | SR-II | -- | 2018-05-22 | 9:27 | 2018-05-22 | 17:37 |  |  |  | 0 | 0 | 0 | 8.17 |  |  |  | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1175. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.17
12 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | 2018-05-12 | 20:08 | 2018-05-12 | 20:08 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 2 kM from Udumalpet end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | 2018-05-17 | 19:49 | 2018-05-17 | 19:49 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 24.2 kM from Udumalpet end. |  | 100
[5 empty] | -- | 2018-05-18 | 9:20 | 2018-05-18 | 18:03 | -- | -- | -- | 0 | 0 | 0 | 8.72 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/957.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.72
14 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | 2018-05-01 | 0:00 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | Shut down availed for tower erection & stringing in multicircuit portion of 400kV Dharmapuri-Somanahalli D/C line vide SRLDC code no. CR-02/94. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
15 | SR2L120 | BELLARY - PAVAGADA I | 55.74 | SR-II | -- | 2018-05-21 | 21:22 | 2018-05-21 | 21:22 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 112.5 kM from Pavagada end (KPTCL portion). |  | 100
[5 empty] | -- | 2018-05-29 | 17:41 | 2018-05-29 | 17:41 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 191.8 kM from Pavagada end (KPTCL portion).
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
16 | SR2L121 | BELLARY - PAVAGADA II | 55.74 | SR-II | -- | 2018-05-19 | 13:30 | 2018-05-19 | 13:30 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 152.7 kM from Pavagada end (KPTCL portion). |  | 100
[5 empty] | -- | 2018-05-20 | 0:41 | 2018-05-20 | 0:41 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 109.4 kM from Pavagada end (KPTCL portion).
[5 empty] | -- | 2018-05-21 | 20:36 | 2018-05-21 | 20:36 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 139.9 kM from Pavagada end (KPTCL portion).
[5 empty] | -- | 2018-05-25 | 0:11 | 2018-05-25 | 0:11 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 102 kM from Ballary PS end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
18 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
20 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
21 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
24 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | 2018-05-19 | 9:36 | 2018-05-19 | 15:54 | -- | -- | -- | 6.3 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/1005. |  | 99.1532
[6 empty] | Sub Total --> | [6 empty] | 6.3 | 0 | 0 | 0
25 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
28 | SR2L24 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L25 | CUDDAPAH - NP KUNTA I | 61.233 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
30 | SR2L26 | GOOTY - BANGALORE | 301.667 | SR-II | -- | 2018-05-19 | 21:34 | 2018-05-19 | 21:34 | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 126.48 kM from Bangalore end. |  | 100
[5 empty] | -- | 2018-05-21 | 14:26 | 2018-05-21 | 16:41 | -- | -- | -- | 0 | 2.25 | 0 | 0 | -- | -- | -- | Emergency Shut down availed to remove foreign object at loc. 490 vide SRLDC code no. CR-05/1123.
[5 empty] | -- | 2018-05-30 | 7:42 | 2018-05-30 | 20:44 | -- | -- | -- | 0 | 0 | 0 | 13.03 | -- | -- | -- | Shut down availed by M/s APTRANSCO for construction works of 400kV Uravakonda - Hindupur line vide SRLDC code no. CR-05/1580.
[6 empty] | Sub Total --> | [6 empty] | 0 | 2.25 | 0 | 13.03
31 | SR2L27 | HASSAN - MYSORE I | 95.875 | SR-II | -- | 2018-05-22 | 3:11 | 2018-05-22 | 8:22 | -- | -- | -- | 0 | 0 | 0 | 5.18 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1162. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.18
32 | SR2L28 | HASSAN - MYSORE II | 95.875 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L29 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 15:03 | -- | -- | -- | 0 | 15.05 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR:79.3 kM from Hassan end. Fault occurred in KPTCL portion of the line. |  | 100
[5 empty] | -- | 2018-05-04 | 1:28 | 2018-05-04 | 18:22 | -- | -- | -- | 0 | 16.9 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-G fault. FLR: 184 km from Hassan end. Fault is in KPTCL portion of the line.
[5 empty] | -- | 2018-05-09 | 11:04 | 2018-05-14 | 9:16 | -- | -- | -- | 0 | 118.2 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-N Fault due to insulator decapping at Loc No 622 (KPTCL Portion)-
[5 empty] | -- | 2018-05-14 | 16:48 | 2018-05-14 | 16:58 | -- | -- | -- | 0 | 0.17 | 0 | 0 | N/A | N/A | N/A | Tripped during over voltage relay testing work by M/s KPTCL at Nelamangala end.
[5 empty] | -- | 2018-05-16 | 10:36 | 2018-05-16 | 16:33 | -- | -- | -- | 0 | 0 | 0 | 5.95 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for isolator alignment work at Nelamangala end vide SRLDC code no. CR-05/832.
[6 empty] | Sub Total --> | [6 empty] | 0 | 150.32 | 0 | 5.95
34 | SR2L30 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2018-05-03 | 22:53 | 2018-05-04 | 14:19 | -- | -- | -- | 0 | 15.43 | 0 | 0 | N/A | N/A | N/A | Tripped on B-G fault. FLR: 138.6 km from Hassan end. Fault is in KPTCL portion of the line. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 15.43 | 0 | 0
35 | SR2L118 | HOODY - YELAHANKA I | 66.098 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
36 | SR2L31 | HOSUR-SALEM II | 125.325 | SR-II | -- | 2018-05-24 | 9:28 | 2018-05-24 | 18:48 | -- | -- | -- | 0 | 0 | 0 | 9.33 | N/A | N/A | N/A | Shut down availed for replacement of isolator at salem end under ADD CAP vide SRLDC code no. CR-05/1307. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.33
37 | SR2L32 | HOSUR-SALEM | 126.339 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L33 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L34 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L35 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2018-05-08 | 17:52 | 2018-05-08 | 18:41 | -- | -- | -- | 0 | 0.82 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR: 104.9 kM from Kaiga end. Fault occurred in KPTCL portion of the line. |  | 100
[5 empty] | -- | 2018-05-17 | 11:12 | 2018-05-17 | 14:35 | -- | -- | -- | 0 | 0 | 0 | 3.38 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for isolator repair works at Guttor end vide SRLDC code no. CR-05/914.
[5 empty] | -- | 2018-05-27 | 18:39 | 2018-05-27 | 19:11 | -- | -- | -- | 0 | 0.53 | 0 | 0 | N/A | N/A | N/A | Tripped at Kaiga end only on failure of auto-reclosure on R-N fault. Guttur end A/R successful.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.35 | 0 | 3.38
41 | SR2L36 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L37 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
43 | SR2L38 | KOLAR - BANGALORE | 97.391 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L39 | KOLAR - HOODY - I | 51.067 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L40 | KOLAR - HOODY - II | 51.067 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L41 | KOLAR - HOSUR - I | 69 | SR-II | -- | 2018-05-17 | 18:22 | 2018-05-17 | 19:40 | -- | -- | -- | 1.3 | 0 | 0 | 0 | N/A | N/A | N/A | Emergency shut down availed to attend line isolator problem at Hosur end vide SRLDC code no. CR-05/944. |  | 99.8253
[6 empty] | Sub Total --> | [6 empty] | 1.3 | 0 | 0 | 0
47 | SR2L42 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L43 | KOLAR - THIRUVALAM - I | 153.195 | SR-II | -- | 2018-05-03 | 23:40 | 2018-05-03 | 23:46 | -- | -- | -- | 0 | 0 | 0.1 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Kolar end. Direct trip signal received at Thiruvalam end. |  | 100
[5 empty] | -- | 2018-05-03 | 23:46 | 2018-05-04 | 5:52 | -- | -- | -- | 0 | 0 | 0 | 6.1 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.1 | 6.1
49 | SR2L116 | KUDANKULAM - TUTICORIN - I | 66.098 | SR-II | -- | 2018-05-16 | 6:43 | 2018-05-16 | 18:56 |  |  |  | 0 | 0 | 0 | 12.22 |  |  |  | Shut down availed by M/s NPCIL for insulator cleaning works at Kudamkulam end vide SRLDC code no. CR-05/810. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.22
50 | SR2L117 | KUDANKULAM - TUTICORIN - II | 66.098 | SR-II | -- | 2018-05-23 | 6:51 | 2018-05-23 | 18:22 |  |  |  | 0 | 0 | 0 | 11.52 |  |  |  | Shut down availed by M/s NPCIL for cleaning insulaotrs at Kudamkulam end vide SRLDC code no. CR-05/1228. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.52
51 | SR2L99 | KUDGI - KOLHAPUR - I | 189.799 | SR-II | -- | 2018-05-17 | 16:26 | 2018-05-17 | 16:59 | -- | -- | -- | 0 | 0 | 0.55 | 0 | -- | -- | -- | Tripped on R-N fault due to heavy lightning and thundering storm. FLR: 9.5km from Kolhapur end (WR-I Portion). |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.55 | 0
52 | SR2L100 | KUDGI - KOLHAPUR - II | 189.799 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L44 | MADURAI - TUTICORIN POOLING STN I | 115.602 | SR-II | -- | 2018-05-10 | 14:18 | 2018-05-10 | 14:18 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 48.6 kM from Tuticorin end. |  | 100
[5 empty] | -- | 2018-05-13 | 16:58 | 2018-05-13 | 16:58 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 45.5 kM from Tuticorin end.
[5 empty] | -- | 2018-05-26 | 5:36 | 2018-05-26 | 5:36 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 46.6 kM from Madurai end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR2L45 | MADURAI - TUTICORIN POOLING STN II | 152.167 | SR-II | -- | 2018-05-25 | 10:17 | 2018-05-25 | 15:19 | -- | -- | -- | 5.03 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/1371. |  | 99.3239
[6 empty] | Sub Total --> | [6 empty] | 5.03 | 0 | 0 | 0
55 | SR2L46 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
56 | SR2L47 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
57 | SR2L97 | MYSORE - KOZHIKODE I | 215.524 | SR-II | -- | 2018-05-30 | 2:05 | 2018-05-30 | 7:43 | -- | -- | -- | 0 | 0 | 0 | 5.63 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1576. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.63
58 | SR2L98 | MYSORE - KOZHIKODE II | 215.524 | SR-II | -- | 2018-05-04 | 2:09 | 2018-05-04 | 2:15 | -- | -- | -- | 0 | 0 | 0.1 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Mysore end. Direct trip signal received at Kozhikode end. |  | 100
[5 empty] | -- | 2018-05-04 | 2:15 | 2018-05-04 | 5:51 | -- | -- | -- | 0 | 0 | 0 | 3.6 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system.
[5 empty] | -- | 2018-05-13 | 17:09 | 2018-05-13 | 17:09 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 183.8 kM from Mysore end.
[5 empty] | -- | 2018-05-23 | 15:07 | 2018-05-23 | 15:16 | -- | -- | -- | 0 | 0 | 0.15 | 0 | N/A | N/A | N/A | Tripped on on B-N fault due to "Mekunu" cyclone. FLR=93 km from Mysore end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.25 | 3.6
59 | SR2L48 | 'NAGAPATTINAM PS - TRICHY - I | 158.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L96 | 'NAGAPATTINAM PS - TRICHY - II | 158.7 | SR-II | -- | 2018-05-21 | 16:44 | 2018-05-21 | 16:44 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 75 kM from Trichy end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L49 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2018-05-03 | 22:09 | 2018-05-05 | 13:19 | -- | -- | -- | 0 | 0 | 0 | 39.17 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/182. |  | 100
[5 empty] | -- | 2018-05-14 | 22:39 | 2018-05-21 | 9:45 | -- | -- | -- | 0 | 0 | 0 | 155.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/750.
[5 empty] | -- | 2018-05-22 | 0:02 | 2018-05-28 | 10:05 | -- | -- | -- | 0 | 0 | 0 | 154.05 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1159.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 348.32
62 | SR2L50 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2018-05-10 | 21:04 | 2018-05-11 | 15:12 | -- | -- | -- | 0 | 0 | 0 | 18.13 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/597. |  | 100
[5 empty] | -- | 2018-05-17 | 18:00 | 2018-05-17 | 18:00 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 10.9 kM from Narendra end.
[5 empty] | -- | 2018-05-30 | 9:09 | 2018-05-30 | 20:24 | -- | -- | -- | 0 | 0 | 0 | 11.25 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1584.
[5 empty] | -- | 2018-05-31 | 8:31 | 2018-05-31 | 19:46 | -- | -- | -- | 0 | 0 | 0 | 11.25 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1644.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 40.63
63 | SR2L101 | NARENDRA - KUDGI I | 176.133 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L102 | NARENDRA - KUDGI II | 176.133 | SR-II | -- | 2018-05-11 | 17:04 | 2018-05-11 | 17:04 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 10.2 kM from Kudgi end. |  | 100
[5 empty] | -- | 2018-05-29 | 18:18 | 2018-05-29 | 18:18 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 57.5 kM from Narendra end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L51 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L52 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L53 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | 2018-05-04 | 1:28 | 2018-05-04 | 2:24 | -- | -- | -- | 0 | 0 | 0.93 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Nelamangala end. Direct trip signal received at Mysore end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.93 | 0
68 | SR2L54 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | 2018-05-04 | 1:07 | 2018-05-04 | 1:15 | -- | -- | -- | 0 | 0 | 0.13 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Mysore end. Direct trip signal received at Nelamangala end. |  | 100
[5 empty] | -- | 2018-05-04 | 1:15 | 2018-05-04 | 6:17 | -- | -- | -- | 0 | 0 | 0 | 5.03 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.13 | 5.03
69 | SR2L55 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
70 | SRL56 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | 2018-05-30 | 8:42 | 2018-05-30 | 9:47 | -- | -- | -- | 0 | 1.08 | 0 | 0 | N/A | N/A | N/A | Tripped due to failure of R-ph CT of ICT-2 at Villianur end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.08 | 0 | 0
71 | SRL57 | NEYVELI TS II - NAGAPATTINAM PS - I | 49.217 | SR-II | -- | 2018-05-28 | 13:17 | 2018-05-28 | 13:43 | -- | -- | -- | 0 | 0.43 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N transient fault due to fault in Nagapattinam - ILFS line 2. FLR: 58.9 km from Neyveli end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.43 | 0 | 0
72 | SR2L58 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L59 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L60 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | 2018-05-03 | 5:50 | 2018-05-03 | 6:10 | -- | -- | -- | 0 | 0.33 | 0 | 0 | N/A | N/A | N/A | Tripped on receipt of direct trip signal from Neyveli TS-2 Exp end while line CBs were attempting for auto-reclosure on B-N fault. FLR:128.7km from Pugalur end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.33 | 0 | 0
75 | SR2L61 | NEYVELI TS-I EXPANSION - NAGAPATTINAM PS - I | 171.95 | SR-II | -- | 2018-05-26 | 9:46 | 2018-05-28 | 18:23 | -- | -- | -- | 0 | 0 | 0 | 56.62 | N/A | N/A | N/A | Shut down availed for replacement of jack bus with HTLS vide SRLDC code no. CR-05/1430. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 56.62
76 | SR2L62 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2018-05-25 | 10:06 | 2018-05-28 | 16:51 | -- | -- | -- | 0 | 0 | 0 | 78.75 | N/A | N/A | N/A | Shut down availed by M/s NLC for AMP works vide SRLDC code no. CR-05/1370. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 78.75
77 | SR2L63 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2018-05-14 | 12:37 | 2018-05-14 | 17:28 | -- | -- | -- | 0 | 4.85 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-G Fault due to line clearance problem with TNEB lines. |  | 100
[5 empty] | -- | 2018-05-15 | 11:16 | 2018-05-15 | 20:59 | -- | -- | -- | 0 | 9.72 | 0 | 0 | N/A | N/A | N/A | Tripped on Y-N fault due to suspected clearance issue with TNEB line crossing. FLR : 134.4kM fom Salem.
[5 empty] | -- | 2018-05-16 | 10:00 | 2018-05-16 | 14:15 | -- | -- | -- | 0 | 0 | 0 | 4.25 | N/A | N/A | N/A | Shut down availed to resolve clearance issue with TNEB lines vide SRLDC code no.CR-05/824.
[5 empty] | -- | 2018-05-21 | 8:47 | 2018-05-21 | 18:15 | -- | -- | -- | 0 | 0 | 0 | 9.47 | N/A | N/A | N/A | Shut down availed by M/s NLC for AMP works at Neyveli end vide SRLDC code no. CR-05/1090.
[6 empty] | Sub Total --> | [6 empty] | 0 | 14.57 | 0 | 13.72
78 | SR2L64 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | 2018-05-22 | 9:37 | 2018-05-22 | 9:45 | -- | -- | -- | 0 | 0.13 | 0 | 0 | N/A | N/A | N/A | Tripped at Neyveli end only on receipt of DT signal. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.13 | 0 | 0
79 | SR2L103 | NP KUNTA - KOLAR I | 130.702 | SR-II | -- | 2018-05-13 | 14:49 | 2018-05-13 | 14:49 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 129.7 kM from Kolar end. |  | 99.2177
[5 empty] | -- | 2018-05-21 | 10:27 | 2018-05-21 | 16:16 | -- | -- | -- | 5.82 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/1103.
[6 empty] | Sub Total --> | [6 empty] | 5.82 | 0 | 0 | 0
80 | SR2L65 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | 2018-05-23 | 9:45 | 2018-05-23 | 19:23 | -- | -- | -- | 0 | 0 | 0 | 9.63 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1237. |  | 100
[5 empty] | -- | 2018-05-24 | 8:12 | 2018-05-24 | 18:51 | -- | -- | -- | 0 | 0 | 0 | 10.65 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1302.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 20.28
81 | SR2L66 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | 2018-05-25 | 8:22 | 2018-05-25 | 17:07 | -- | -- | -- | 0 | 0 | 0 | 8.75 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1359. |  | 100
[5 empty] | -- | 2018-05-26 | 8:05 | 2018-05-26 | 18:05 | -- | -- | -- | 0 | 0 | 0 | 10 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-05/1428.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 18.75
82 | SR2L122 | PAVAGADA - TUMKUR I | 104.7 | SR-II | -- | 2018-05-10 | 20:54 | 2018-05-11 | 14:28 | -- | -- | -- | 0 | 0 | 0 | 17.57 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/596. |  | 100
[5 empty] | -- | 2018-05-21 | 22:51 | 2018-05-22 | 10:58 | -- | -- | -- | 0 | 0 | 0 | 12.12 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1152.
[5 empty] | -- | 2018-05-29 | 1:38 | 2018-05-30 | 7:21 | -- | -- | -- | 0 | 0 | 0 | 29.72 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1527.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 59.41
83 | SR2L123 | PAVAGADA - TUMKUR II | 104.7 | SR-II | -- | 2018-05-03 | 22:02 | 2018-05-04 | 17:19 | -- | -- | -- | 0 | 0 | 0 | 19.28 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/183. |  | 100
[5 empty] | -- | 2018-05-11 | 18:21 | 2018-05-14 | 11:38 | -- | -- | -- | 0 | 0 | 0 | 65.28 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/665.
[5 empty] | -- | 2018-05-18 | 0:38 | 2018-05-21 | 10:34 | -- | -- | -- | 0 | 0 | 0 | 81.93 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/950.
[5 empty] | -- | 2018-05-24 | 1:10 | 2018-05-24 | 16:26 | -- | -- | -- | 0 | 0 | 0 | 15.27 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1296.
[5 empty] | -- | 2018-05-28 | 1:13 | 2018-05-28 | 8:10 | -- | -- | -- | 0 | 0 | 0 | 6.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1487.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 188.71
84 | SR2L116 | PAVAGADA - TUMKUR III | 104.7 | SR-II | -- | 2018-05-03 | 19:57 | 2018-05-03 | 20:21 | -- | -- | -- | 0 | 0.4 | 0 | 0 | N/A | N/A | N/A | Tripped on B-G fault due to foreign object at loc 317. |  | 100
[5 empty] | -- | 2018-05-14 | 22:43 | 2018-05-17 | 10:45 | -- | -- | -- | 0 | 0 | 0 | 60.03 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/751.
[5 empty] | -- | 2018-05-18 | 20:04 | 2018-05-18 | 20:04 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 13.4 kM from Pavagada end.
[5 empty] | -- | 2018-05-24 | 23:39 | 2018-05-25 | 12:09 | -- | -- | -- | 0 | 0 | 0 | 12.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1354.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.4 | 0 | 72.53
85 | SR2L117 | PAVAGADA - TUMKUR IV | 104.7 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2L67 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | 2018-05-01 | 2:46 | 2018-05-01 | 2:46 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 53.8 kM from Pondy end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2L68 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2L69 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | 2018-05-04 | 19:34 | 2018-05-04 | 19:34 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 47.1 kM from Madurai end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
89 | SR2L105 | SALEM - SALEM POOLING STN I | 59.04 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2L106 | SALEM - SALEM POOLING STN II | 59.04 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2L70 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | 2018-05-22 | 9:37 | 2018-05-22 | 19:01 | -- | -- | -- | 0 | 0 | 0 | 9.4 | N/A | N/A | N/A | Shut down availed for replacement of isolator under Addcap vide SRLDC code no. CR-05/1176. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.4
92 | SR2L71 | SALEM - UDUMALPET II | 137.91 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2L72 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2L73 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2L74 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2L75 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2L110 | THIRUNELVELI - EDAMON - III | 81.94 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2L111 | THIRUNELVELI - EDAMON - IV | 81.94 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2L76 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2018-05-30 | 17:17 | 2018-05-30 | 17:50 | -- | -- | -- | 0 | 0 | 0 | 0.55 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for charging Unit - II Generating Transformer at Kudankulam end vide SRLDC ocde no. CR-05/1625. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.55
100 | SR2L77 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2L78 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2L79 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2L80 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | 2018-05-23 | 14:59 | 2018-05-23 | 14:59 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 63.8 kM from Trivandram end. |  | 99.5968
[5 empty] | -- | 2018-05-29 | 14:09 | 2018-05-29 | 17:09 | -- | -- | -- | 3 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for jumper rectification works at Loc.No.199 vide SRLDC code no. CR-05 /1550.
[6 empty] | Sub Total --> | [6 empty] | 3 | 0 | 0 | 0
104 | SR2L81 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
105 | SR2L82 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | 2018-05-07 | 18:00 | 2018-05-07 | 18:00 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 109 kM from Tirunelveli end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2L83 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | 2018-05-22 | 17:23 | 2018-05-22 | 17:23 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 98.6 kM from Tirunelveli end. |  | 100
[5 empty] | -- | 2018-05-22 | 20:11 | 2018-05-22 | 20:11 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 110.6 kM from Tirunelveli end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2L84 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2L85 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2L86 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
110 | SR2L87 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2L88 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | 2018-05-24 | 20:56 | 2018-05-24 | 21:00 | -- | -- | -- | 0 | 0 | 0.07 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Karaikudi end. Direct trip signal received at Trichy end. |  | 100
[5 empty] | -- | 2018-05-24 | 21:00 | 2018-05-29 | 9:32 | -- | -- | -- | 0 | 0 | 0 | 108.53 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide SRLDC code no. CR-05/1349.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.07 | 108.53
112 | SR2L89 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2L90 | TUTICORIN JV TPS - TUTICORIN POOLING STN I | 127.232 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2L107 | TUTICORIN JV TPS - TUTICORIN POOLING STN II | 127.232 | SR-II | -- | 2018-05-10 | 12:05 | 2018-05-10 | 12:05 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on R-N (Ph-earth) transient fault. FLR: 11.2 kM from Tuticorin end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2L108 | TUTICORIN POOLING STN - SALEM POOLING STN I | 368.84 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2L109 | TUTICORIN POOLING STN - SALEM POOLING STN II | 368.84 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2L91 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2L92 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2L93 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2L94 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2L95 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | 2018-05-16 | 9:42 | 2018-05-16 | 10:35 | -- | -- | -- | 0 | 0.88 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of B-phase CVT at Kalivindapattu end, NBFC delayed by NTECL Vallur. |  | 99.566
[5 empty] | -- | 2018-05-16 | 10:35 | 2018-05-16 | 13:48 | -- | -- | -- | 3.22 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of B-phase CVT at Kalivindapattu end vide SRLDC code no. CR-05/825.
[5 empty] | -- | 2018-05-16 | 13:48 | 2018-05-16 | 14:55 | -- | -- | -- | 0 | 1.12 | 0 | 0 | N/A | N/A | N/A | Charging delayed by NTECL Vallur.
[6 empty] | Sub Total --> | [6 empty] | 3.22 | 2 | 0 | 0
122 | SR2L119 | YELAHANKA - NELAMANGALA I | 66.098 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T59 | ARASUR ICT - III | 500 | SR-II | -- | 2018-05-23 | 9:32 | 2018-05-23 | 20:48 | -- | -- | -- | 0 | 0 | 0 | 11.27 | N/A | N/A | N/A | Shut down availed for CSD commissioning works of tie bay vide SRLDC code no. CR-05/1240. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.27
126 | SR2T3 | BANGALORE ICT - I | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T4 | BANGALORE ICT - II | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
128 | SR2T51 | BANGALORE ICT - III | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
129 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | [7 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
135 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
136 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
137 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | 2018-05-19 | 9:46 | 2018-05-19 | 14:06 | -- | -- | -- | 4.33 | 0 | 0 | 0 |  |  |  | Shut down availed for AMP works vide SRLDC code no. CR-05/1006. |  | 99.418
[6 empty] | Sub Total --> | [6 empty] | 4.33 | 0 | 0 | 0
139 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | 2018-05-18 | 9:35 | 2018-05-18 | 14:01 | -- | -- | -- | 4.43 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/958. |  | 99.4046
[6 empty] | Sub Total --> | [6 empty] | 4.43 | 0 | 0 | 0
140 | SR2T50 | KALIVANDAPATTU ICT - III | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
141 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
143 | SR2T60 | KARAIKUDI ICT - III | 500 | SR-II | -- | 2018-05-21 | 9:14 | 2018-05-21 | 23:29 | -- | -- | -- | 0 | 0 | 0 | 14.25 | N/A | N/A | N/A | Shut down availed for CSD commissioning works of main CB vide SRLDC code no. CR-05/1092. |  | 100
[5 empty] | -- | 2018-05-24 | 12:08 | 2018-05-24 | 20:15 | -- | -- | -- | 0 | 0 | 0 | 8.12 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-05/1225.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 22.37
144 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | 2018-05-23 | 9:14 | 2018-05-23 | 13:45 | -- | -- | -- | 4.52 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attedning hotdpot vide SRLDC code no. CR-05/1235. |  | 99.3925
[6 empty] | Sub Total --> | [6 empty] | 4.52 | 0 | 0 | 0
145 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
147 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | 2018-05-24 | 11:02 | 2018-05-24 | 11:06 | -- | -- | -- | 0.07 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-05/1316. |  | 99.9906
[6 empty] | Sub Total --> | [6 empty] | 0.07 | 0 | 0 | 0
148 | SR2T46 | KOZHIKODE - ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2T47 | KOZHIKODE - ICT II | 315 | SR-II | -- | 2018-05-20 | 9:31 | 2018-05-20 | 15:55 | -- | -- | -- | 0 | 0 | 0 | 6.4 | N/A | N/A | N/A | Shut down availed for jumper removal of temporary ICT vide SRLDC code no. CR-05/1094. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.4
150 | SR2T61 | KOZHIKODE - ICT III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | 2018-05-21 | 10:00 | 2018-05-21 | 18:32 | -- | -- | -- | 0 | 0 | 0 | 8.53 | N/A | N/A | N/A | Shut down availed for 33 kV insulation works vide SRLDC code no. CR-05/1098. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.53
152 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | 2018-05-23 | 12:05 | 2018-05-23 | 13:27 | -- | -- | -- | 0 | 0 | 0 | 1.37 | N/A | N/A | N/A | Shut down availed by M/s TNEB for attending hotspot at chekkanurani SS vide SRLDC code no. CR-05/1264. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.37
153 | SR2T53 | MADURAI ICT - III | 500 | SR-II | -- | 2018-05-22 | 9:10 | 2018-05-22 | 16:06 |  |  |  | 0 | 0 | 0 | 6.93 |  |  |  | Shut down availed for 33 kV insulation works vide SRLDC code no. CR-05/1173. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.93
154 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
155 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | 2018-05-04 | 2:31 | 2018-05-04 | 4:27 | -- | -- | -- | 0 | 0 | 0 | 1.93 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation in the system vide SRLDC code no. CR-05/197. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.93
156 | SR2T52 | MYSORE ICT III | 315 | SR-II | -- | 2018-05-04 | 2:11 | 2018-05-04 | 6:42 | -- | -- | -- | 0 | 0 | 0 | 4.52 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation in the system vide SRLDC code no. CR-05/195. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.52
157 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
158 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
159 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
160 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
161 | SR2T56 | PAVAGADA ICT - I | 500 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
162 | SR2T57 | PAVAGADA ICT - II | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
163 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | 2018-05-27 | 9:05 | 2018-05-27 | 13:04 | -- | -- | -- | 0 | 0 | 0 | 3.98 | N/A | N/A | N/A | Shut down availed for 33kV insulation works vide SRLDC code no. CR-05/1463. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.98
164 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | 2018-05-27 | 13:31 | 2018-05-27 | 15:11 | -- | -- | -- | 1.67 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending hotspot vide SRLDC code no. CR-05/1468. |  | 99.7755
[6 empty] | Sub Total --> | [6 empty] | 1.67 | 0 | 0 | 0
165 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | 2018-05-16 | 9:36 | 2018-05-16 | 14:26 | -- | -- | -- | 4.83 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/822. |  | 99.3508
[6 empty] | Sub Total --> | [6 empty] | 4.83 | 0 | 0 | 0
166 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | 2018-05-17 | 9:58 | 2018-05-17 | 14:52 | -- | -- | -- | 4.9 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/903. |  | 99.3414
[6 empty] | Sub Total --> | [6 empty] | 4.9 | 0 | 0 | 0
167 | SR2T54 | PUGALUR ICT - III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
168 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | 2018-05-21 | 9:17 | 2018-05-21 | 13:02 | -- | -- | -- | 3.75 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/1093. |  | 99.496
[6 empty] | Sub Total --> | [6 empty] | 3.75 | 0 | 0 | 0
169 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | 2018-05-22 | 9:04 | 2018-05-22 | 12:27 | -- | -- | -- | 3.38 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-05/1172. |  | 99.5457
[6 empty] | Sub Total --> | [6 empty] | 3.38 | 0 | 0 | 0
170 | SR2T58 | THIRUNELVELI ICT - III | 500 | SR-II | -- | 2018-05-30 | 10:27 | 2018-05-30 | 15:02 |  |  |  | 0 | 0 | 0 | 4.58 | N/A | N/A | N/A | Shut down availed for commissioning of CSD of tie CB vide SRLDC code no. CR-05/1598. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.58
171 | SR2T36 | THIRUVALAM ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
172 | SR2T37 | THIRUVALAM ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
173 | SR2T38 | TRICHY ICT - I | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
174 | SR2T39 | TRICHY ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
175 | SR2T55 | TRICHY ICT - III | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
176 | SR2T40 | TRIVANDRUM ICT - I | 315 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | -- | -- | -- |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
177 | SR2T41 | TRIVANDRUM ICT - II | 315 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
178 | SR2T42 | TRIVANDRUM ICT - III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
179 | SR2T48 | TUMKUR ICT I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
180 | SR2T49 | TUMKUR ICT II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
181 | SR2T43 | UDUMALPET ICT - I | 315 | SR-II | -- | 2018-05-27 | 16:10 | 2018-05-27 | 17:18 | -- | -- | -- | 1.13 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to spurious operation of PRV. |  | 99.8481
[6 empty] | Sub Total --> | [6 empty] | 1.13 | 0 | 0 | 0
182 | SR2T44 | UDUMALPET ICT - II | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
183 | SR2T45 | UDUMALPET ICT - III | 315 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
184 | SR2T62 | YELAHANKA ICT - I | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
185 | SR2T63 | YELAHANKA ICT - II | 500 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
186 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 70.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/955. |  | 100
[5 empty] | -- | 2018-05-04 | 9:04 | 2018-05-10 | 20:47 | -- | -- | -- | 0 | 0 | 0 | 155.72 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/220.
[5 empty] | -- | 2018-05-11 | 8:42 | 2018-05-11 | 18:14 | -- | -- | -- | 0 | 0 | 0 | 9.53 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/611.
[5 empty] | -- | 2018-05-14 | 8:47 | 2018-05-19 | 23:12 | -- | -- | -- | 0 | 0 | 0 | 134.42 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/714.
[5 empty] | -- | 2018-05-21 | 9:00 | 2018-05-23 | 1:22 | -- | -- | -- | 0 | 0 | 0 | 40.37 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1087.
[5 empty] | -- | 2018-05-23 | 10:06 | 2018-05-25 | 0:15 | -- | -- | -- | 0 | 0 | 0 | 38.15 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/ 1251.
[5 empty] | -- | 2018-05-25 | 10:00 | 2018-05-25 | 23:15 | -- | -- | -- | 0 | 0 | 0 | 13.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1368.
[5 empty] | -- | 2018-05-28 | 7:34 | 2018-05-29 | 0:11 | -- | -- | -- | 0 | 0 | 0 | 16.62 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1491.
[5 empty] | -- | 2018-05-29 | 9:29 | 2018-05-30 | 23:56 | -- | -- | -- | 0 | 0 | 0 | 38.45 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1532.
[5 empty] | -- | 2018-05-31 | 10:42 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 13.3 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1655.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 530.71
187 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 1:06 | -- | -- | -- | 0 | 0 | 0 | 49.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/961. |  | 100
[5 empty] | -- | 2018-05-03 | 7:36 | 2018-05-03 | 21:23 | -- | -- | -- | 0 | 0 | 0 | 13.78 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/105.
[5 empty] | -- | 2018-05-04 | 9:31 | 2018-05-19 | 22:42 | -- | -- | -- | 0 | 0 | 0 | 373.18 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/222.
[5 empty] | -- | 2018-05-21 | 9:54 | 2018-05-21 | 23:47 | -- | -- | -- | 0 | 0 | 0 | 13.88 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1100.
[5 empty] | -- | 2018-05-23 | 10:03 | 2018-05-24 | 2:04 | -- | -- | -- | 0 | 0 | 0 | 16.02 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1249.
[5 empty] | -- | 2018-05-25 | 9:58 | 2018-05-25 | 23:11 | -- | -- | -- | 0 | 0 | 0 | 13.22 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1369.
[5 empty] | -- | 2018-05-28 | 7:28 | 2018-05-29 | 0:01 | -- | -- | -- | 0 | 0 | 0 | 16.55 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1492.
[5 empty] | -- | 2018-05-30 | 11:01 | 2018-05-30 | 23:46 | -- | -- | -- | 0 | 0 | 0 | 12.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1600.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 508.48
188 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-02 | 2:40 | -- | -- | -- | 0 | 0 | 0 | 26.67 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/1262. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 26.67
189 | SR2R31 | HASSAN BUS REACTOR - II | 125 | SR-II | -- | 2018-05-02 | 10:16 | 2018-05-03 | 0:40 | -- | -- | -- | 0 | 0 | 0 | 14.4 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/49. |  | 100
[5 empty] | -- | 2018-05-11 | 10:42 | 2018-05-11 | 18:13 | -- | -- | -- | 0 | 0 | 0 | 7.52 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/628.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 21.92
190 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | 2018-05-21 | 10:02 | 2018-05-22 | 5:47 | -- | -- | -- | 0 | 0 | 0 | 19.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1102. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 19.75
191 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 22:24 | -- | -- | -- | 0 | 0 | 0 | 70.4 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/888. |  | 100
[5 empty] | -- | 2018-05-05 | 9:15 | 2018-05-10 | 21:04 | -- | -- | -- | 0 | 0 | 0 | 131.82 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/309.
[5 empty] | -- | 2018-05-14 | 9:55 | 2018-05-19 | 23:56 | -- | -- | -- | 0 | 0 | 0 | 134.02 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/717.
[5 empty] | -- | 2018-05-21 | 9:06 | 2018-05-28 | 0:27 | -- | -- | -- | 0 | 0 | 0 | 159.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1088.
[5 empty] | -- | 2018-05-30 | 9:15 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 38.75 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1586.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 534.34
192 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
193 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 0:57 | -- | -- | -- | 0 | 0 | 0 | 48.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/195. |  | 100
[5 empty] | -- | 2018-05-03 | 14:22 | 2018-05-04 | 2:51 | -- | -- | -- | 0 | 0 | 0 | 12.48 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/130.
[5 empty] | -- | 2018-05-05 | 10:26 | 2018-05-20 | 0:16 | -- | -- | -- | 0 | 0 | 0 | 349.83 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/312.
[5 empty] | -- | 2018-05-23 | 10:10 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 205.83 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1252.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 617.09
194 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 21:19 | -- | -- | -- | 0 | 0 | 0 | 69.32 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/954. |  | 100
[5 empty] | -- | 2018-05-04 | 9:39 | 2018-05-10 | 20:53 | -- | -- | -- | 0 | 0 | 0 | 155.23 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/223.
[5 empty] | -- | 2018-05-11 | 9:12 | 2018-05-11 | 18:16 | -- | -- | -- | 0 | 0 | 0 | 9.07 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/614.
[5 empty] | -- | 2018-05-14 | 9:49 | 2018-05-19 | 22:43 | -- | -- | -- | 0 | 0 | 0 | 132.9 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/718.
[5 empty] | -- | 2018-05-21 | 8:45 | 2018-05-23 | 0:42 | -- | -- | -- | 0 | 0 | 0 | 39.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1089.
[5 empty] | -- | 2018-05-28 | 9:45 | 2018-05-28 | 23:55 | -- | -- | -- | 0 | 0 | 0 | 14.17 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1502.
[5 empty] | -- | 2018-05-30 | 9:09 | 2018-05-31 | 2:53 | -- | -- | -- | 0 | 0 | 0 | 17.73 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1585.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 438.37
195 | SR2R28 | KUDGI BUS REACTOR - I | 125 | SR-II | -- | 2018-05-15 | 9:21 | 2018-05-15 | 18:55 | -- | -- | -- | 0 | 0 | 0 | 9.57 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/759. |  | 100
[5 empty] | -- | 2018-05-16 | 11:12 | 2018-05-17 | 2:00 | -- | -- | -- | 0 | 0 | 0 | 14.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/842.
[5 empty] | -- | 2018-05-28 | 10:23 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 85.62 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1506.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 109.99
196 | SR2R32 | KUDGI BUS REACTOR - II | 125 | SR-II | -- | 2018-05-29 | 11:03 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 60.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1542. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 60.95
197 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 6:05 | -- | -- | -- | 0 | 0 | 0 | 6.08 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/1292. |  | 100
[5 empty] | -- | 2018-05-02 | 10:12 | 2018-05-03 | 0:38 | -- | -- | -- | 0 | 0 | 0 | 14.43 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/48.
[5 empty] | -- | 2018-05-04 | 15:50 | 2018-05-07 | 2:11 | -- | -- | -- | 0 | 0 | 0 | 58.35 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/266.
[5 empty] | -- | 2018-05-07 | 9:32 | 2018-05-08 | 17:15 | -- | -- | -- | 0 | 0 | 0 | 31.72 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/365.
[5 empty] | -- | 2018-05-10 | 11:08 | 2018-05-10 | 20:14 | -- | -- | -- | 0 | 0 | 0 | 9.1 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/542.
[5 empty] | -- | 2018-05-11 | 10:41 | 2018-05-11 | 18:11 | -- | -- | -- | 0 | 0 | 0 | 7.5 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/627.
[5 empty] | -- | 2018-05-16 | 11:15 | 2018-05-18 | 0:31 | -- | -- | -- | 0 | 0 | 0 | 37.27 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/839.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 164.45
198 | SR2R30 | NAGAPATTINAM PS BUS REACTOR - I | 50 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
199 | SR2R10 | NARENDRA BUS REACTOR | 125 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
200 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 1:18 | -- | -- | -- | 0 | 0 | 0 | 1.3 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/754. |  | 100
[5 empty] | -- | 2018-05-02 | 10:24 | 2018-05-03 | 0:55 | -- | -- | -- | 0 | 0 | 0 | 14.52 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/50.
[5 empty] | -- | 2018-05-03 | 14:24 | 2018-05-04 | 3:16 | -- | -- | -- | 0 | 0 | 0 | 12.87 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/131.
[5 empty] | -- | 2018-05-05 | 9:14 | 2018-05-08 | 17:19 | -- | -- | -- | 0 | 0 | 0 | 80.08 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/308.
[5 empty] | -- | 2018-05-16 | 12:08 | 2018-05-19 | 23:48 | -- | -- | -- | 0 | 0 | 0 | 83.67 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/846.
[5 empty] | -- | 2018-05-23 | 10:03 | 2018-05-23 | 19:36 | -- | -- | -- | 0 | 0 | 0 | 9.55 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1248.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 201.99
201 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 0:56 | -- | -- | -- | 0 | 0 | 0 | 0.93 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/447. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.93
202 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 10:40 | -- | -- | -- | 0 | 0 | 0 | 10.67 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/393. |  | 100 | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.67
203 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2018-05-02 | 14:42 | 2018-05-04 | 4:56 | -- | -- | -- | 0 | 0 | 0 | 38.23 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/66. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 38.23
204 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 1:20 | -- | -- | -- | 0 | 0 | 0 | 49.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/396. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 49.33
205 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-02 | 14:14 | -- | -- | -- | 0 | 0 | 0 | 38.23 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/481. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 38.23
206 | SR2R33 | TRIVENDRUM BUS REACTOR - I | 125 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-11 | 21:40 | -- | -- | -- | 0 | 0 | 0 | 261.67 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/704. |  | 100
[5 empty] | -- | 2018-05-23 | 10:16 | 2018-05-24 | 21:06 | -- | -- | -- | 0 | 0 | 0 | 34.83 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1253.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 296.5
207 | SR2R29 | TUMKUR BUS REACTOR - I | 63 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
208 | SR2R17 | TUTICORIN POOLING STN BUS REACTOR - I | 63 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
209 | SR2R46 | YELAHANKA BUS REACTOR - I | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-07 | 2:07 | -- | -- | -- | 0 | 0 | 0 | 146.12 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/1129. |  | 100
[5 empty] | -- | 2018-05-07 | 9:37 | 2018-05-08 | 23:26 | -- | -- | -- | 0 | 0 | 0 | 37.82 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/367.
[5 empty] | -- | 2018-05-15 | 9:59 | 2018-05-15 | 21:58 | -- | -- | -- | 0 | 0 | 0 | 11.98 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/765.
[5 empty] | -- | 2018-05-16 | 11:20 | 2018-05-19 | 23:30 | -- | -- | -- | 0 | 0 | 0 | 84.17 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/838.
[5 empty] | -- | 2018-05-21 | 9:57 | 2018-05-21 | 23:55 | -- | -- | -- | 0 | 0 | 0 | 13.97 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1101.
[5 empty] | -- | 2018-05-23 | 10:05 | 2018-05-27 | 23:36 | -- | -- | -- | 0 | 0 | 0 | 109.52 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/1250.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 403.58
210 | SR2R36 | Chittor Line Reactor at Sriperumbudur | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/348. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
211 | SR2R37 | Hosur-2 Line Reactor at Salem | 50 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
212 | SR2R38 | Karaikudi Line Reactor at Madurai | 63 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
213 | SR2R18 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-10 | 20:57 | -- | -- | -- | 0 | 0 | 0 | 236.95 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/701. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 236.95
214 | SR2R26 | Mysore 1 Line Reactor at Kozhikode | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-04 | 1:20 | -- | -- | -- | 0 | 0 | 0 | 73.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/818. |  | 100
[5 empty] | -- | 2018-05-07 | 9:44 | 2018-05-08 | 17:32 | -- | -- | -- | 0 | 0 | 0 | 31.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/370.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 105.13
215 | SR2R27 | Mysore 2 Line Reactor at Kozhikode | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-04 | 1:20 | -- | -- | -- | 0 | 0 | 0 | 73.33 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/965. |  | 100
[5 empty] | -- | 2018-05-07 | 9:36 | 2018-05-08 | 17:34 | -- | -- | -- | 0 | 0 | 0 | 31.97 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/366.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 105.3
216 | SR2R39 | Nagapattinam-1 Line Reactor at Trichy | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/397. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
217 | SR2R40 | Nagapattinam-2 Line Reactor at Trichy | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/398. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
218 | SR2R41 | Nellore-1 Line Reactor at Thiruvalam | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
219 | SR2R42 | Nellore-2 Line Reactor at Thiruvalam | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
220 | SR2R19 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | [16 empty] | 100 |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
221 | SR2R20 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
222 | SR2R34 | Palakkad 1 Line Reactor at Trichur | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 0:58 | -- | -- | -- | 0 | 0 | 0 | 48.97 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/446. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.97
223 | SR2R35 | Palakkad 2 Line Reactor at Trichur | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-03 | 0:58 | -- | -- | -- | 0 | 0 | 0 | 48.97 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-01/57. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.97
224 | SR2R43 | Salem-2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-08 | 17:46 | -- | -- | -- | 0 | 0 | 0 | 185.77 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/974. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 185.77
225 | SR2R44 | SV Chatram Line Reactor at Sriperumbudur | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-04/347. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
226 | SR2R21 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 2:14 | -- | -- | -- | 0 | 0 | 0 | 2.23 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/679. |  | 100
[5 empty] | -- | 2018-05-08 | 19:01 | 2018-05-24 | 22:35 | -- | -- | -- | 0 | 0 | 0 | 387.57 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/460.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 389.8
227 | SR2R22 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2018-05-01 | 0:00 | 2018-05-01 | 2:15 | -- | -- | -- | 0 | 0 | 0 | 2.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/679. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.25
228 | SR2R45 | Trichy Line Reactor at Madurai | 50 | SR-II | -- |  |  |  |  | -- | -- | -- | [9 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
229 | SR2R23 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
230 | SR2R24 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | N/A | N/A | N/A |  |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
231 | SR2R25 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | 2018-05-01 | 0:00 | 2018-06-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 744 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-03/02. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 744
232 | SR2P1 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | 2018-05-03 | 19:33 | 2018-05-03 | 20:08 | -- | -- | -- | 0.58 | 0 | 0 | 0 | N/A | N/A | N/A | Pole blocked due to line fault. FLR: 145kM from Kolar, location no: 3301 ( Fault in SRTS-I portion). |  | 99.8347
[5 empty] | -- | 2018-05-16 | 15:35 | 2018-05-16 | 16:14 | -- | -- | -- | 0.65 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to receipt of ESOF signal at Kolar end due to operation of differential protection at Talcher end.
[6 empty] | Sub Total --> | [6 empty] | 1.23 | 0 | 0 | 0
233 | SR2P2 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | 2018-05-26 | 17:53 | 2018-05-26 | 18:19 | -- | -- | -- | 0.43 | 0 | 0 | 0 | N/A | N/A | N/A | Pole bolcked due to receipt of ESOF signal from Talcher end. |  | 99.9421
[5 empty] | -- | 2018-05-31 | 18:19 | 2018-05-31 | 19:03 | -- | -- | -- | 0 | 0 | 0.73 | 0 | N/A | N/A | N/A | Tripped due to DC line fault due to heavy rain and thunderstorm. FLR: 490.9 km from Talcher (Loc. 1332) SR-1 portion.
[6 empty] | Sub Total --> | [6 empty] | 0.43 | 0 | 0.73 | 0
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse