## SOP
[20 empty] | Prepared by | D Sammaiah DM,CPCC
Standard of Performance data for the month of JULY-2015
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2015-07-14 | 8:18 | 2015-07-14 | 17:00 | -- | -- | -- | 0 | 0 | 0 | 8.7 | N/A | N/A | N/A | Shut down availed by M/s KSEB for maintenance works at Edappon SS vide SRLDC code no. CR-07/406. | SRPC | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.7
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2015-07-21 | 9:09 | 2015-07-21 | 18:43 | -- | -- | -- | 0 | 0 | 0 | 9.5667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for routine maintenance works at Kundra end vide SRLDC code no. CR-07/576. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.5667
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | [17 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | 2015-07-16 | 8:36 | 2015-07-16 | 18:34 | -- | -- | -- | 0 | 0 | 0 | 9.9667 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacing flashed disc insulator at loc.7 (KSEB portion) vide SRLDC code no. CR-07/463. |  | 100
[5 empty] | -- | 2015-07-23 | 8:44 | 2015-07-23 | 17:51 | -- | -- | -- | 0 | 0 | 0 | 9.1167 | N/A | N/A | N/A | Shut down availed by M/s KSEB for routine maintenance works at Kundra end vide SRLDC code no. CR-07/614.
[6 empty] | 2015-07-31 | 9:06 | 2015-07-31 | 14:36 | -- | -- | -- | 0 | 0 | 0 | 5.5 | N/A | N/A | N/A | Shut down availed by M/s KSEB to attend hot spot in CT terminal at Kundra SS vide SRLDC code no. CR-07/827.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 24.5833
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
8 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | 2015-07-08 | 9:52 | 2015-07-08 | 16:09 | -- | -- | -- | 0 | 0 | 0 | 6.2833 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-07/221. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.2833
9 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | 2015-07-09 | 9:34 | 2015-07-09 | 15:53 | -- | -- | -- | 0 | 0 | 0 | 6.3167 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-07/260. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.3167
10 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
11 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
12 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
15 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
16 | SR2L22 | COASTAL ENERGEN - TUTICORIN POOLING STN I | 36.304 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR2L23 | COASTAL ENERGEN-TUTICORIN JV TPS 1 | 36.304 | SR-II | -- | 2015-07-17 | 14:56 | 2015-07-17 | 16:17 | -- | -- | -- | 0 | 0 | 0 | 1.35 | N/A | N/A | N/A | Shut down availed by M/s NTPL for changing of CT ratio for metering and protection vide SRLDC code no. CR-07/502. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.35
18 | SR2L24 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L25 | CUDDAPAH - KOLAR | 174.073 | SR-II | -- | 2015-07-13 | 4:21 | 2015-07-13 | 5:09 | -- | -- | -- | 0.8 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped due to maloperation of over voltage relay at Kolar end. |  | 99.8925
[6 empty] | Sub Total --> | [6 empty] | 0.8 | 0 | 0 | 0
20 | SR2L26 | GOOTY - BANGALORE | 301.667 | SR-II | -- | 2015-07-25 | 10:15 | 2015-07-25 | 17:36 | -- | -- | -- | 0 | 0 | 0 | 7.35 | N/A | N/A | N/A | Shut down availed for line reactor CSD commissioning works at Gooty SS vide SRLDC code no. CR-07/675. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.35
21 | SR2L27 | HASSAN - MYSORE I | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L28 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L29 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | 2015-07-29 | 19:09 | 2015-07-30 | 13:25 | -- | -- | -- | 0 | 18.2667 | 0 | 0 | N/A | N/A | N/A | Tripped due to flash over of B-phase LA at KPTCL Nelamangala end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 18.2667 | 0 | 0
24 | SR2L30 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L31 | HOSUR-SALEM II | 125.325 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L32 | HOSUR-SALEM | 126.339 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L33 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2015-07-16 | 10:32 | 2015-07-16 | 11:22 | -- | -- | -- | 0.83333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for isolator alignment work at Narendra end vide SRLDC code no. CR-07/466. |  | 99.888
[6 empty] | Sub Total --> | [6 empty] | 0.83333 | 0 | 0 | 0
28 | SR2L34 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | 2015-07-30 | 3:51 | 2015-07-30 | 4:41 | -- | -- | -- | 0 | 0.83333 | 0 | 0 | N/A | N/A | N/A | Hand tripped by mistake while isolating unit-4 at Kaiga end. Direct trip received at Narendra end. |  | 100
[6 empty] | 2015-07-30 | 11:21 | 2015-08-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 36.65 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for bay maintenance works at Kaiga end vide SRLDC code no. CR-07/810.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.83333 | 0 | 36.65
29 | SR2L35 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2015-07-28 | 9:48 | 2015-07-28 | 19:19 | -- | -- | -- | 0 | 0 | 0 | 9.5167 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for CVT testing at Guttur end vide SRLDC code no. CR-07/741. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 9.5167
30 | SR2L36 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2015-07-09 | 16:54 | 2015-07-09 | 17:35 | -- | -- | -- | 0 | 0.68333 | 0 | 0 | N/A | N/A | N/A | Tripped on receipt of direct trip signal at NPCIL Kaiga end. |  | 100
[6 empty] | 2015-07-29 | 9:40 | 2015-07-29 | 13:33 | -- | -- | -- | 0 | 0 | 0 | 3.8833 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for CVT testing at Guttur end vide SRLDC code no. CR-07/762.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.68333 | 0 | 3.8833
31 | SR2L37 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | 2015-07-16 | 9:05 | 2015-07-16 | 13:37 | -- | -- | -- | 4.5333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for measuring tan delta of line reactor bushings at variable frequency at Madurai SS vide SRLDC code no. CR-07/464A. |  | 99.3906
[6 empty] | 2015-07-26 | 23:06 | 2015-07-27 | 12:48 | -- | -- | -- | 0 | 0 | 0 | 13.7 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-07/779.
[6 empty] | 2015-07-26 | 23:02 | 2015-07-26 | 23:06 | -- | -- | -- | 0 | 0 | 0.066667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Karaikudi end. Direct trip signal received at Madurai end.
[6 empty] | Sub Total --> | [6 empty] | 4.5333 | 0 | 0.066667 | 13.7 | 0 | 0 | 0
32 | SR2L38 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
33 | SR2L39 | KOLAR - HOODY - I | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
34 | SR2L40 | KOLAR - HOODY - II | 51.067 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
35 | SR2L41 | KOLAR - HOSUR - I | 69 | SR-II | -- | 2015-07-26 | 10:02 | 2015-07-26 | 18:08 | -- | -- | -- | 8.1 | 0 | 0 | 0 | -- | -- | -- | -- |  | 98.9113
[6 empty] | Sub Total --> | [6 empty] | 8.1 | 0 | 0 | 0
36 | SR2L42 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
37 | SR2L43 | KOLAR - THIRUVALAM - I | 153.195 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
38 | SR2L44 | MADURAI - TUTICORIN POOLING STN I | 115.602 | SR-II | -- | 2015-07-28 | 17:34 | 2015-07-28 | 17:34 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 51.04 kM from Madurai end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L45 | MADURAI - TUTICORIN 2 | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
40 | SR2L46 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
41 | SR2L47 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | 2015-07-24 | 12:01 | 2015-07-25 | 11:55 | -- | -- | -- | 0 | 0 | 0 | 23.9 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for insulator cleaning works at Kuadamkulam end vide SRLDC code no. CR-07/646. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.9
42 | SR2L48 | 'NAGAPATTINAM PS - TRICHY - I | 161.7 | SR-II | -- | 2015-07-14 | 10:48 | 2015-07-14 | 11:06 | -- | -- | -- | 0.3 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Trichy end only on receipt of DT due to opertion of gas density monitor relay operation at Nagapattinam. |  | 99.9597
[6 empty] | Sub Total --> | [6 empty] | 0.3 | 0 | 0 | 0
43 | SR2L49 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
44 | SR2L50 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | 2015-07-10 | 12:14 | 2015-07-10 | 20:23 | -- | -- | -- | 0 | 0 | 0 | 8.15 | N/A | N/A | N/A | Shut down availed for bay extension works at Narendra end vide SRLDC code no. CR-07/312. |  | 100
[6 empty] | 2015-07-23 | 10:45 | 2015-07-23 | 19:45 | -- | -- | -- | 0 | 0 | 0 | 9 | N/A | N/A | N/A | Shut down availed for bay extension works at Narendra end vide SRLDC code no. CR-07/620.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 17.15
45 | SR2L51 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L52 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L53 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L54 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR2L55 | NEYVELI - BAHOOR | 52.5 | SR-II | conductor snapping | 2015-07-26 | 17:20 | 2015-07-27 | 7:29 | -- | -- | 0.33194 | 0 | 0 | 14.15 | 0 | 2 | N | -1.6681 | Tripped on R-N fault due to conductor came out of insulator pin at Loc. No. 143 due to heavy cyclonic wind. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 14.15 | 0
50 | SRL56 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
51 | SR2L57 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
52 | SR2L58 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2015-07-26 | 23:58 | 2015-07-27 | 0:05 | -- | -- | -- | 0 | 0 | 0.11667 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Pugalur end. Direct trip signal received at Neyveli TS-2 end. |  | 100
[6 empty] | 2015-07-27 | 0:05 | 2015-07-27 | 10:32 | -- | -- | -- | 0 | 0 | 0 | 10.45 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-07/781.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.11667 | 10.45
53 | SR2L59 | NEYVELI TS II - TRICHY - I | 164.175 | SR-II | -- | 2015-07-17 | 16:13 | 2015-07-17 | 16:28 | -- | -- | -- | 0.25 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped for taking Line reactor at Trichy into service vide code no. CR-07/506. |  | 99.9327
[6 empty] | 2015-07-17 | 12:46 | 2015-07-17 | 12:51 | -- | -- | -- | 0.083333 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Trichy end only during testing of line reactor at Trichy.
[6 empty] | 2015-07-17 | 10:57 | 2015-07-17 | 11:07 | -- | -- | -- | 0.16667 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped for taking out Line reactor at Trichy end for measurement of Bushing tan delta at veriable frequency vide SRLDC code no. CR-07/494.
[6 empty] | 2015-07-24 | 3:02 | 2015-07-24 | 4:19 | -- | -- | -- | 0 | 0 | 1.2833 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Neyveli TS-2 end. Direct trip signal received at Trichy end.
[6 empty] | 2015-07-26 | 23:32 | 2015-07-27 | 7:37 | -- | -- | -- | 0 | 0 | 0 | 8.0833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-07/780.
[6 empty] | 2015-07-26 | 23:27 | 2015-07-26 | 23:32 | -- | -- | -- | 0 | 0 | 0.083333 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Neyveli TS-2 end. Direct trip signal received at Trichy end.
[6 empty] | Sub Total --> | [6 empty] | 0.5 | 0 | 1.3667 | 8.0833
54 | SR2L60 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
55 | SR2L61 | NEYVELI TS-I EXPANSION - NAGAPATTINAM PS - I | 171.95 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
56 | SR2L62 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
57 | SR2L63 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2015-07-21 | 9:45 | 2015-07-21 | 16:15 | -- | -- | -- | 0 | 0 | 0 | 6.5 | N/A | N/A | N/A | Shut down availed by M/s NLC for routine maintenance works at Neyveli TS-2 end vide SRLDC code no. CR-07/575. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.5
58 | SR2L64 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L65 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L66 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | 2015-07-05 | 22:05 | 2015-07-05 | 22:18 | -- | -- | -- | 0.21667 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Palakkad end only due to suspected PLCC maloperation at Palakkad end. |  | 99.9709
[6 empty] | Sub Total --> | [6 empty] | 0.21667 | 0 | 0 | 0
61 | SR2L67 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L68 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SR2L69 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SR2L70 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L71 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | 2015-07-07 | 9:50 | 2015-07-07 | 17:44 | -- | -- | -- | 0 | 0 | 0 | 7.9 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-07/185. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.9
66 | SR2L72 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
67 | SR2L73 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | 2015-07-10 | 9:43 | 2015-07-10 | 14:03 | -- | -- | -- | 0 | 0 | 0 | 4.3333 | N/A | N/A | N/A | Shut down availed by M/s TNEB for monthly maintenance works at SV Chatram end vide SRLDC code no. CR-07/303. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.3333
68 | SR2L74 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | 2015-07-14 | 11:21 | 2015-07-14 | 14:09 | -- | -- | -- | 0 | 0 | 0 | 2.8 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacing broken conductor of bus section isolator at Edamon SS vide SRLDC code no. CR-07/414. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.8
69 | SR2L75 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | 2015-07-14 | 11:21 | 2015-07-14 | 14:08 | -- | -- | -- | 0 | 0 | 0 | 2.7833 | N/A | N/A | N/A | Shut down availed by M/s KSEB for replacing broken conductor of bus section isolator at Edamon SS vide SRLDC code no. CR-07/415. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.7833
70 | SR2L76 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | 2015-07-24 | 12:01 | 2015-07-25 | 11:55 | -- | -- | -- | 0 | 0 | 0 | 23.9 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for insulator cleaning works at Kuadamkulam end vide SRLDC code no. CR-07/646. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.9
71 | SR2L77 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | 2015-07-13 | 23:28 | 2015-07-17 | 7:44 | -- | -- | -- | 0 | 0 | 0 | 80.2667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/404. |  | 100
[6 empty] | 2015-07-23 | 15:21 | 2015-07-24 | 16:28 | -- | -- | -- | 0 | 0 | 0 | 25.1167 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for insulator cleaning works at Kuadamkulam end vide SRLDC code no. CR-07/625.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 105.3833
72 | SR2L78 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | 2015-07-09 | 22:40 | 2015-07-13 | 7:32 | -- | -- | -- | 0 | 0 | 0 | 80.8667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/297. |  | 100
[6 empty] | 2015-07-17 | 10:51 | 2015-07-23 | 11:47 | -- | -- | -- | 0 | 0 | 0 | 144.9333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/495.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 225.8
73 | SR2L79 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | 2015-07-01 | 0:00 | 2015-07-09 | 10:23 | -- | -- | -- | 0 | 0 | 0 | 202.3833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/740. |  | 100
[6 empty] | 2015-07-23 | 11:55 | 2015-07-23 | 19:23 | -- | -- | -- | 0 | 0 | 0 | 7.4667 | N/A | N/A | N/A | Shut down availed by M/s NPCIL for insulator cleaning works at Kuadamkulam end vide SRLDC code no. CR-07/622.
[6 empty] | 2015-07-27 | 22:22 | 2015-08-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 97.6333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/733.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 307.4833
74 | SR2L80 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | 2015-07-30 | 8:42 | 2015-07-30 | 8:56 | -- | -- | -- | 0.23333 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped for taking out Line reactor at Trivemdrum end for tan delta mesurement of bushing vide SRLDC code no. CR-07/797. |  | 99.953
[6 empty] | 2015-07-31 | 13:24 | 2015-07-31 | 13:31 | -- | -- | -- | 0.11667 | 0 | 0 | 0 | N/A | N/A | N/A | Hand tripped for taking Line reactor at Trivendrum into service vide SRLDC code no. CR-07/833.
[6 empty] | Sub Total --> | [6 empty] | 0.35 | 0 | 0 | 0
75 | SR2L81 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
76 | SR2L82 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L83 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | 2015-07-28 | 16:48 | 2015-07-28 | 17:10 | -- | -- | -- | 0 | 0 | 0.36667 | 0 | N/A | N/A | N/A | Tripped on operation of O/V stage-II(instantanous) protection at Thirunelveli end while line CBs were attempting for auto-reclosure on B-N fault. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.36667 | 0
78 | SR2L84 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II | -- | 2015-07-03 | 10:34 | 2015-07-03 | 19:42 | -- | -- | -- | 9.1333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for warranty tests of terminal equipments at Thiruvalam end vide SRLDC code no. CR-07/66. |  | 98.7724
[6 empty] | Sub Total --> | [6 empty] | 9.1333 | 0 | 0 | 0
79 | SR2L85 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | 2015-07-04 | 10:12 | 2015-07-04 | 16:35 | -- | -- | -- | 6.3833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for warranty tests of terminal equipments at Thiruvalam end vide SRLDC code no. CR-07/113. |  | 99.142
[6 empty] | Sub Total --> | [6 empty] | 6.3833 | 0 | 0 | 0
80 | SR2L86 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
81 | SR2L87 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
82 | SR2L88 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L89 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR2L90 | TUTICORIN JV TPS - TUTICORIN POOLING STN I | 127.232 | SR-II | -- | 2015-07-03 | 10:02 | 2015-07-03 | 13:23 | -- | -- | -- | 0 | 0 | 0 | 3.35 | N/A | N/A | N/A | Shut down availed by M/s NTPL for changing CT secondary ratios at NTPL end vide SRLDC code no. CR-07/63. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 3.35
85 | SR2L91 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | 2015-07-03 | 14:27 | 2015-07-03 | 17:46 | -- | -- | -- | 3.3167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of conductor from line to line isolator at Udumalpet end vide SRLDC code no. CR-07/80. |  | 99.5542
[6 empty] | Sub Total --> | [6 empty] | 3.3167 | 0 | 0 | 0
86 | SR2L92 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2L93 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2L94 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | 2015-07-01 | 6:47 | 2015-07-01 | 19:09 | -- | -- | -- | 0 | 0 | 0 | 12.3667 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-06/915. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.3667
89 | SR2L95 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | 2015-07-01 | 6:50 | 2015-07-01 | 19:11 | -- | -- | -- | 0 | 0 | 0 | 12.35 | N/A | N/A | N/A | Shut down availed for replacement of porcelain insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-06/916. |  | 100
[6 empty] | 2015-07-27 | 16:56 | 2015-07-27 | 18:00 | -- | -- | -- | 0 | 0 | 1.0667 | 0 | N/A | N/A | N/A | Tripped on Y-N fault due to heavy rain and thunderstorm due to heavy pollution near NTECL Vallur. FLR : 125.1 kM from Kalivindapattu end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 1.0667 | 12.35
90 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | 2015-07-13 | 9:26 | 2015-07-13 | 16:11 | -- | -- | -- | 6.75 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for measuring bushings tan delta at variable frequency vide SRLDC code no. CR-07/384. |  | 99.0927
[6 empty] | Sub Total --> | [6 empty] | 6.75 | 0 | 0 | 0
91 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | 2015-07-14 | 9:36 | 2015-07-14 | 15:02 | -- | -- | -- | 5.4333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for measuring bushings tan delta at variable frequency vide SRLDC code no. CR-07/410. |  | 99.2697
[6 empty] | Sub Total --> | [6 empty] | 5.4333 | 0 | 0 | 0
92 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | 2015-07-05 | 0:15 | 2015-07-05 | 4:17 | -- | -- | -- | 0 | 0 | 0 | 4.0333 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending hot spot at 220 kV Somanahalli SS vide SRLDC code no. CR-07/131. |  | 98.8217
[6 empty] | 2015-07-12 | 9:14 | 2015-07-12 | 18:00 |  |  |  | 8.7667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/367.
[6 empty] | Sub Total --> | [6 empty] | 8.7667 | 0 | 0 | 4.0333
93 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | 2015-07-11 | 16:26 | 2015-07-11 | 18:35 | -- | -- | -- | 0 | 0 | 0 | 2.15 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for attending hotspots in 220kV switch yard vide SRLDC code no. CR-07/352. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.15
94 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | 2015-07-01 | 9:04 | 2015-07-01 | 18:17 | -- | -- | -- | 9.2167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/01. |  | 98.7612
[6 empty] | Sub Total --> | [6 empty] | 9.2167 | 0 | 0 | 0
96 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
100 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
101 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
104 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | 2015-07-01 | 9:25 | 2015-07-01 | 17:51 | -- | -- | -- | 8.4333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/02. |  | 98.8665
[6 empty] | Sub Total --> | [6 empty] | 8.4333 | 0 | 0 | 0
105 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
106 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | 2015-07-02 | 7:18 | 2015-07-02 | 7:45 | -- | -- | -- | 0 | 0 | 0.45 | 0 | N/A | N/A | N/A | Tripped on operation of PRD due to group of monkeys climbed on ICT and disturbed PRD. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.45 | 0
110 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | 2015-07-01 | 0:00 | 2015-07-03 | 12:56 | -- | -- | -- | 60.9333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for overhauling works vide SRLDC code no. CR-06/848. |  | 91.81
[6 empty] | Sub Total --> | [6 empty] | 60.9333 | 0 | 0 | 0
113 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | 2015-07-19 | 9:44 | 2015-07-19 | 15:24 | -- | -- | -- | 5.6667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/533. |  | 99.2384
[6 empty] | Sub Total --> | [6 empty] | 5.6667 | 0 | 0 | 0
115 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | 2015-07-15 | 9:37 | 2015-07-15 | 18:52 | -- | -- | -- | 9.25 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/437. |  | 98.7567
[6 empty] | Sub Total --> | [6 empty] | 9.25 | 0 | 0 | 0
116 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | 2015-07-16 | 11:40 | 2015-07-16 | 18:31 | -- | -- | -- | 6.85 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/471. |  | 99.0793
[6 empty] | Sub Total --> | [6 empty] | 6.85 | 0 | 0 | 0
117 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | 2015-07-31 | 9:36 | 2015-07-31 | 19:17 | -- | -- | -- | 9.6833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/828. |  | 98.6985
[6 empty] | Sub Total --> | [6 empty] | 9.6833 | 0 | 0 | 0
120 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
122 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
123 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
125 | SR2T36 | THIRUVALAM ICT - I | 315 | SR-II | -- | 2015-07-16 | 9:58 | 2015-07-16 | 19:48 | -- | -- | -- | 9.8333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for warranty checks vide SRLDC code no. CR-07/464. |  | 96.2753
[6 empty] | Sub Total --> | [6 empty] | 9.8333 | 0 | 0 | 0
126 | SR2T37 | THIRUVALAM ICT - II | 315 | SR-II | -- | 2015-07-14 | 9:42 | 2015-07-14 | 19:32 | -- | -- | -- | 9.8333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for warranty checks vide SRLDC code no. CR-07/409. |  | 96.2753
[6 empty] | Sub Total --> | [6 empty] | 9.8333 | 0 | 0 | 0
127 | SR2T38 | TRICHY ICT - I | 315 | SR-II | -- | 2015-07-29 | 18:04 | 2015-07-29 | 18:24 | -- | -- | -- | 0 | 0 | 0 | 0.33333 | N/A | N/A | N/A | Hand tripped for tap changing as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/777. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.33333
128 | SR2T39 | TRICHY ICT - II | 315 | SR-II | -- | 2015-07-06 | 11:15 | 2015-07-06 | 13:16 | -- | -- | -- | 2.0167 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed to attend hotspot in 400 kV B-Phase bushing terminal connector vide SRLDC code no. CR-07/163. |  | 99.7289
[6 empty] | 2015-07-29 | 18:30 | 2015-07-29 | 18:46 | -- | -- | -- | 0 | 0 | 0 | 0.26667 | N/A | N/A | N/A | Hand tripped for tap changing as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-07/789.
[6 empty] | Sub Total --> | [6 empty] | 2.0167 | 0 | 0 | 0.26667
129 | SR2T40 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T41 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T42 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T43 | UDUMALPET ICT - I | 315 | SR-II | -- | 2015-07-17 | 10:37 | 2015-07-17 | 14:45 | -- | -- | -- | 4.1333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for cheking isolator alignment and operation of 230 kV side isolators vide SRLDC code no. CR-07/493. |  | 99.4444
[6 empty] | Sub Total --> | [6 empty] | 4.1333 | 0 | 0 | 0
133 | SR2T44 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T45 | UDUMALPET ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
135 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2015-07-03 | 7:18 | 2015-07-26 | 18:25 | -- | -- | -- | 0 | 0 | 0 | 563.1166 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2015-07-27 | 11:03 | 2015-08-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 108.95 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 672.0666
136 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2015-07-03 | 7:16 | 2015-07-19 | 23:26 | -- | -- | -- | 0 | 0 | 0 | 400.1667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 400.1667
137 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | 2015-07-01 | 0:00 | 2015-07-02 | 22:48 | -- | -- | -- | 0 | 0 | 0 | 46.8 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 46.8
139 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2015-07-01 | 0:00 | 2015-07-26 | 18:16 | -- | -- | -- | 0 | 0 | 0 | 618.2667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 618.2667
140 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | 2015-07-16 | 14:54 | 2015-07-16 | 18:41 | -- | -- | -- | 3.7833 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for measuring tan delta of bushings at variable frequency vide SRLDC code no. CR-07/474. |  | 98.7209
[6 empty] | 2015-07-30 | 11:47 | 2015-07-30 | 17:31 | -- | -- | -- | 5.7333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for measuring bushings tan delta at variable frequency vide SRLDC code no. CR-07/806.
[6 empty] | Sub Total --> | [6 empty] | 9.5167 | 0 | 0 | 0 | 0 | 0 | 0
141 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2015-07-07 | 16:59 | 2015-07-18 | 22:27 | -- | -- | -- | 0 | 0 | 0 | 269.4667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 269.4667
142 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2015-07-03 | 9:01 | 2015-07-09 | 19:03 | -- | -- | -- | 0 | 0 | 0 | 154.0333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2015-07-16 | 10:40 | 2015-07-20 | 22:38 |  |  |  | 0 | 0 | 0 | 107.9667 |  |  |  | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 154.0333
143 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2015-07-09 | 10:01 | 2015-07-09 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 12.8833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 12.8833
144 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | 2015-07-22 | 10:48 | 2015-07-22 | 21:51 | -- | -- | -- | 0 | 0 | 0 | 11.05 | N/A | N/A | N/A | Shut down availed for bay extension works vide SRLDC code no. CR-07/600. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.05
145 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2015-07-03 | 7:13 | 2015-07-18 | 22:26 | -- | -- | -- | 0 | 0 | 0 | 375.2167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2015-07-30 | 19:43 | 2015-08-01 | 0:00 |  |  |  | 0 | 0 | 0 | 28.2833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 403.5
146 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2015-07-03 | 9:01 | 2015-07-27 | 22:16 | -- | -- | -- | 0 | 0 | 0 | 589.25 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 589.25
147 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2015-07-03 | 15:40 | 2015-07-03 | 22:52 | -- | -- | -- | 0 | 0 | 0 | 7.2 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2015-07-24 | 11:44 | 2015-07-24 | 12:40 | -- | -- | -- | 0 | 0 | 0 | 0.93333 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-07/645.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 8.1333
149 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2015-07-03 | 15:41 | 2015-07-03 | 22:54 | -- | -- | -- | 0 | 0 | 0 | 7.2167 | N/A | N/A | N/A | H/T for voltage regulation |  | 98.759
[6 empty] | 2015-07-08 | 9:25 | 2015-07-08 | 18:39 | -- | -- | -- | 9.2333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-07/216.
[6 empty] | 2015-07-25 | 10:10 | 2015-07-25 | 12:34 | -- | -- | -- | 0 | 0 | 0 | 2.4 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-07/674.
[6 empty] | Sub Total --> | [6 empty] | 9.2333 | 0 | 0 | 9.6167
150 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2R17 | TUTICORIN POOLING STN BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
152 | SR2R18 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
153 | SR2R19 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
154 | SR2R20 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
155 | SR2R21 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
156 | SR2R22 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
157 | SR2R23 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2015-07-28 | 10:40 | 2015-07-28 | 13:23 | -- | -- | -- | 0 | 0 | 0 | 2.7167 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-07/742. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 2.7167
158 | SR2R24 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2015-07-28 | 15:02 | 2015-07-28 | 16:30 | -- | -- | -- | 0 | 0 | 0 | 1.4667 | N/A | N/A | N/A | Shut down availed for CSD commissioning works vide SRLDC code no. CR-07/748. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.4667
159 | SR2R25 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
160 | SR2R26 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
161 | SR2R27 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | 2015-07-05 | 3:30 | 2015-07-05 | 3:30 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 273.29 kM from Talcher end (Tower no. 743). |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
[22 empty] | 16066.9656 | 16080.8405
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse