## SOP
[20 empty] | Prepared by | Ch, Venkatrao, Dy. Manager
Standard of Performance data for the month of JUNE - 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., SOUTHERN REGION - II
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | SR2L1 | EDAPPON - EDAMON | 58.562 | SR-II | -- | 2016-06-21 | 9:59 | 2016-06-21 | 15:30 | -- | -- | -- | 0 | 0 | 0 | 5.5167 | N/A | N/A | N/A | Shut down availed by M/s KSEB for attending hot spot on Y-Ph CT terminal at 220KV Edappon (KSEB) SS vide SRLDC code no. CR-06/692. | Yet to be issued by SRPC | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.5167
2 | SR2L2 | KAYAMKULAM - EDAPPON | 19.764 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-01 | 14:48 | -- | -- | -- | 0 | 0 | 0 | 14.8 | N/A | N/A | N/A | Shut down availed by M/s NTPC for retrofitting of main-1 relay at Kayamkulam end vide SRLDC code no. CR-05/1130. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 14.8
3 | SR2L3 | KAYAMKULAM - KUNDRA | 41 | SR-II | -- | 2016-06-06 | 9:20 | 2016-06-07 | 11:58 | -- | -- | -- | 0 | 0 | 0 | 26.6333 | N/A | N/A | N/A | Shut down availed by M/s NTPC for retrofitting work of Main-I relay at Kayamkulam end vide SRLDC code no. CR-06/195. |  | 100
[5 empty] | -- | 2016-06-08 | 1:54 | 2016-06-08 | 4:03 | -- | -- | -- | 0 | 2.15 | 0 | 0 | N/A | N/A | N/A | Tripped at Kundra end only due to receipt of direct trip signal from Kayamkulam end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 2.15 | 0 | 26.6333
4 | SR2L4 | KAYAMKULAM - POLLAM - II | 47 | SR-II | -- | 2016-06-04 | 8:42 | 2016-06-04 | 20:18 | -- | -- | -- | 0 | 0 | 0 | 11.6 | N/A | N/A | N/A | Shut down availed by M/s NTPC for Relay retrofitting works at Kayamkulam end vide SRLDC code no. CR06/131. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.6
5 | SR2L5 | KAYAMKULAM - PUNNAPRA - I | 12.476 | SR-II | -- | 2016-06-01 | 14:53 | 2016-06-01 | 17:07 | -- | -- | -- | 0 | 0 | 0 | 2.2333 | N/A | N/A | N/A | Shut down availed by M/s KSEB for attending arcing on bus isolator connector at Punnapura SS vide SRLDC code no. CR-06/15. |  | 100
[6 empty] | 2016-06-02 | 9:34 | 2016-06-02 | 22:22 | -- | -- | -- | 0 | 0 | 0 | 12.8 | N/A | N/A | N/A | Shut down availed by M/s NTPC for relay retrofitting works at Kayamkulam end vide SRLDC code no. CR-06/47.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 15.0333
6 | SR2L6 | KUNDRA - EDAMON | 37 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
7 | SR2L7 | PUNNAPRA - POLLAM - I | 34.184 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
8 | SR2L8 | ARASUR-UDUMALPET-I | 65.116 | SR-II | -- | 2016-06-03 | 9:35 | 2016-06-03 | 14:55 | -- | -- | -- | 5.3333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for line AMP works & attending critical hotspots vide SRLDC code no. CR-06/88. |  | 99.2593
[6 empty] | Sub Total --> | [6 empty] | 5.3333 | 0 | 0 | 0
9 | SR2L9 | ARASUR-UDUMALPET-II | 65.116 | SR-II | -- | 2016-06-04 | 9:48 | 2016-06-04 | 13:44 | -- | -- | -- | 3.9333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-06/132. |  | 99.4537
[6 empty] | Sub Total --> | [6 empty] | 3.9333 | 0 | 0 | 0
10 | SR2L10 | BANGALORE - HOSUR I | 79.756 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
11 | SR2L11 | BHAVINI - ARANI I | 106.452 | SR-II | -- | 2016-06-02 | 10:02 | 2016-06-02 | 18:34 | -- | -- | -- | 8.5333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-06/52. |  | 98.8148
[6 empty] | Sub Total --> | [6 empty] | 8.5333 | 0 | 0 | 0
12 | SR2L12 | BHAVINI - ARANI II | 106.452 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
13 | SR2L13 | BHAVINI - KANCHEEPURAM I | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
14 | SR2L14 | BHAVINI - KANCHEEPURAM II | 80.316 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
15 | SR2L15 | BHAVINI - SIRUSERI I | 36.243 | SR-II | -- |  |  |  |  | -- | -- | -- |  |  |  |  | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
16 | SR2L16 | BHAVINI - SIRUSERI II | 36.243 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
17 | SR2L17 | BIDADI - SOMANAHALLI I | 16.97 | SR-II | -- | 2016-06-03 | 23:13 | 2016-06-03 | 23:13 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | Auto reclosed successfully on Y-N (Ph-earth) transient fault. FLR: 2.5 kM from Bidadi end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
18 | SR2L18 | BIDADI - SOMANAHALLI II | 16.97 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
19 | SR2L19 | CHITTOOR - CHENNAI | 95.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
20 | SR2L20 | CHITTOOR - THIRUVALAM I | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
21 | SR2L21 | CHITTOOR - THIRUVALAM II | 21.002 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
22 | SR2L22 | COASTAL ENERGEN - TUTICORIN POOLING STN I | 36.304 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
23 | SR2L23 | COASTAL ENERGEN-TUTICORIN JV TPS 1 | 36.304 | SR-II | -- | 2016-06-09 | 10:54 | 2016-06-09 | 16:19 | -- | -- | -- | 0 | 0 | 0 | 5.4167 | N/A | N/A | N/A | Shut down availed by M/s NTPL for preventive maintenance and testing of circuit breaker at NTPL end vide SRLDC code no. CR-06/305. |  | 100
[5 empty] | -- | 2016-06-18 | 10:59 | 2016-06-19 | 13:06 | -- | -- | -- | 0 | 0 | 0 | 26.1167 | N/A | N/A | N/A | Shut down availed by M/s NTPL for putting silicon coating on porcelain insulators and bushings at NTPL end vide SRLDC code no. CR-06/606.
[5 empty] | -- | 2016-06-25 | 8:37 | 2016-06-29 | 4:26 | -- | -- | -- | 0 | 0 | 0 | 91.8167 | N/A | N/A | N/A | Shut down availed by M/s NTPL for silicon coating works at NTPL switchyard vide SRLDC code no. CR-06/845.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 123.35
24 | SR2L24 | CUDDAPAH - CHITTOOR | 147.14 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
25 | SR2L25 | CUDDAPAH - NP KUNTA I | 61.233 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
26 | SR2L26 | GOOTY - BANGALORE | 301.667 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
27 | SR2L27 | HASSAN - MYSORE I | 95.875 | SR-II | -- | 2016-06-01 | 23:07 | 2016-06-02 | 11:57 | -- | -- | -- | 0 | 0 | 0 | 12.8333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/26. |  | 100
[5 empty] | -- | 2016-06-04 | 0:03 | 2016-06-04 | 7:47 | -- | -- | -- | 0 | 0 | 0 | 7.7333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/114.
[5 empty] | -- | 2016-06-24 | 2:08 | 2016-06-24 | 7:35 | -- | -- | -- | 0 | 0 | 0 | 5.45 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/791.
[6 empty] | 2016-06-30 | 0:57 | 2016-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 23.05 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/981.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 49.0667
28 | SR2L28 | HASSAN - MYSORE II | 95.875 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
29 | SR2L29 | HASSAN - NELAMANGALA I | 74.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
30 | SR2L30 | HASSAN - TALAGUPPA I | 74.35 | SR-II | -- | 2016-06-02 | 16:52 | 2016-06-03 | 11:08 | -- | -- | -- | 0 | 18.2667 | 0 | 0 | N/A | N/A | N/A | Tripped on B-N (Ph-earth) transient fault. FLR: 231.1 kM from Hassan end. Fault occured in KPTCL portion of the line. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 18.2667 | 0 | 0
31 | SR2L31 | HOSUR-SALEM II | 125.325 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
32 | SR2L32 | HOSUR-SALEM | 126.339 | SR-II | -- | 2016-06-25 | 12:25 | 2016-06-25 | 15:28 | -- | -- | -- | 3.05 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for replacement of Y-ph Lightning Arrester at Salem end vide SRLDC code no. CR-06/855. |  | 99.5764
[6 empty] | Sub Total --> | [6 empty] | 3.05 | 0 | 0 | 0
33 | SR2L33 | KAIGA - NARENDRA I | 107.662 | SR-II | -- | 2016-06-03 | 23:57 | 2016-06-07 | 19:53 | -- | -- | -- | 0 | 0 | 0 | 91.9333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/112. |  | 100
[5 empty] | -- | 2016-06-09 | 23:16 | 2016-06-10 | 9:14 |  |  |  | 0 | 0 | 0 | 9.9667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/320.
[5 empty] | -- | 2016-06-11 | 1:35 | 2016-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 478.4167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/373.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 580.3167
34 | SR2L34 | KAIGA - NARENDRA II | 107.662 | SR-II | -- | 2016-06-07 | 22:00 | 2016-06-09 | 9:19 | -- | -- | -- | 0 | 0 | 0 | 35.3167 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/245. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 35.3167
35 | SR2L35 | KAIGA - SIRSI - I | 61.432 | SR-II | -- | 2016-06-04 | 4:00 | 2016-06-04 | 7:34 | -- | -- | -- | 0 | 0 | 0 | 3.5667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/117. |  | 100
[5 empty] | -- | 2016-06-08 | 14:18 | 2016-06-13 | 19:04 | -- | -- | -- | 0 | 124.7667 | 0 | 0 | N/A | N/A | N/A | Tripped on R-N (Ph-earth) transient fault. FLR: 88.5 kM from Kaiga end. Fault occured in KPTCL portion of the line. R-phase Insulator decapped at loc.186.
[5 empty] | -- | 2016-06-19 | 23:29 | 2016-06-24 | 16:42 | -- | -- | -- | 0 | 0 | 0 | 113.2167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/657.
[5 empty] | -- | 2016-06-25 | 22:10 | 2016-06-26 | 11:30 | -- | -- | -- | 0 | 0 | 0 | 13.3333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/873.
[6 empty] | 2016-06-25 | 0:09 | 2016-06-25 | 7:32 |  |  |  | 0 | 0 | 0 | 7.3833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/839.
[6 empty] | Sub Total --> | [6 empty] | 0 | 124.7667 | 0 | 137.5
36 | SR2L36 | KAIGA - SIRSI - II | 61.432 | SR-II | -- | 2016-06-26 | 16:23 | 2016-06-27 | 10:03 | -- | -- | -- | 0 | 0 | 0 | 17.6667 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/883. |  | 100
[5 empty] | -- | 2016-06-28 | 22:25 | 2016-07-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 49.5833 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/934.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 67.25
37 | SR2L37 | KARAIKUDI - MADURAI - I | 129.761 | SR-II | -- | 2016-06-24 | 3:01 | 2016-07-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 164.9833 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide message no. CP-06/510. |  | 100
[5 empty] | -- | 2016-06-24 | 2:49 | 2016-06-24 | 3:01 |  |  |  | 0 | 0 | 0.2 | 0 | N/A | N/A | N/A | Line tripped on operation of over voltage protection at Karaikudi end. Direct trip signal received at Madurai end.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.2 | 164.9833 | -- | -- | --
38 | SR2L38 | KOLAR - BANGALORE | 97.391 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
39 | SR2L39 | KOLAR - HOODY - I | 51.067 | SR-II | -- | 2016-06-02 | 5:03 | 2016-06-02 | 9:07 | -- | -- | -- | 0 | 0 | 0 | 4.0667 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for extinguishing fire in ICT-II at Hoody (KPTCL) SS vide SRLDC code no. CR-06/31. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.0667
40 | SR2L40 | KOLAR - HOODY - II | 51.067 | SR-II | -- | 2016-06-02 | 5:02 | 2016-06-02 | 9:08 | -- | -- | -- | 0 | 0 | 0 | 4.1 | N/A | N/A | N/A | Shut down availed by M/s KPTCL for extinguishing fire in ICT-II at Hoody (KPTCL) SS vide SRLDC code no. CR-06/32. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.1
41 | SR2L41 | KOLAR - HOSUR - I | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
42 | SR2L42 | KOLAR - HOSUR - II | 69 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
43 | SR2L43 | KOLAR - THIRUVALAM - I | 153.195 | SR-II |  | 2016-06-15 | 9:12 | 2016-06-15 | 15:30 | -- | -- | -- | 0 | 0 | 0 | 6.3 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-06/479. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.3
44 | SR2L99 | KUDGI - KOLHAPUR - I | 189.799 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
45 | SR2L100 | KUDGI - KOLHAPUR - II | 189.799 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
46 | SR2L44 | MADURAI - TUTICORIN POOLING STN I | 115.602 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
47 | SR2L45 | MADURAI - TUTICORIN POOLING STN II | 152.167 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
48 | SR2L46 | MADURAI-THIRUNELVELI - I | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
49 | SR2L47 | MADURAI-THIRUNELVELI - II | 161.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
50 | SR2L97 | MYSORE - KOZHIKODE I | 215.524 | SR-II | -- | 2016-06-24 | 23:47 | 2016-06-25 | 6:51 | -- | -- | -- | 0 | 0 | 0 | 7.0667 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/838. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.0667
51 | SR2L98 | MYSORE - KOZHIKODE II | 215.524 | SR-II | -- | 2016-06-02 | 14:02 | 2016-06-02 | 14:17 | -- | -- | -- | 0 | 0.25 | 0 | 0 | -- | -- | -- | Tripped on R-N (Phase-earth) fault. FLR= 166 KM from Mysore end. A/R unsuccessful as the same was kept in Non auto mode for OPGW stringing works. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.25 | 0 | 0
52 | SR2L48 | 'NAGAPATTINAM PS - TRICHY - I | 158.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
53 | SR2L96 | 'NAGAPATTINAM PS - TRICHY - II | 158.7 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
54 | SR2L49 | NARENDRA - DAVANGERE I | 156.5 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-17 | 10:47 | -- | -- | -- | 0 | 0 | 0 | 394.7833 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-05/580. |  | 100
[5 empty] | -- | 2016-06-17 | 21:08 | 2016-06-17 | 21:48 |  |  |  | 0 | 0.66667 | 0 | 0 | -- | -- | -- | Tripped at Guttur (KPTCL) end only due to suspected DC earth fault at Guttur KPTCL SS.
[6 empty] | 2016-06-18 | 18:24 | 2016-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 293.6 | -- | -- | -- | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/625.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.66667 | 0 | 688.3833
55 | SR2L50 | NARENDRA - DAVANGERE II | 156.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
56 | SR2L101 | NARENDRA - KUDGI I | 176.133 | SR-II | -- | 2016-06-03 | 18:13 | 2016-06-08 | 15:28 | -- | -- | -- | 0 | 0 | 0 | 117.25 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/101. |  | 100
[5 empty] | -- | 2016-06-08 | 17:29 | 2016-06-10 | 9:49 | -- | -- | -- | 0 | 0 | 0 | 40.3333 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/278.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 157.5833
57 | SR2L102 | NARENDRA - KUDGI II | 176.133 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-03 | 11:43 | -- | -- | -- | 0 | 0 | 0 | 59.7167 | N/A | N/A | N/A | Line was kept open as per SRLDC instruction to contain over voltage in the system vide SRLDC email dated 30.05.2016. |  | 100
[5 empty] | -- | 2016-06-10 | 21:47 | 2016-07-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 482.2167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR-06/371.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 541.9333
58 | SR2L51 | NELAMANGALA - BIDADI I | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
59 | SR2L52 | NELAMANGALA - BIDADI II | 34.75 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
60 | SR2L53 | NELAMANGALA - MYSORE I | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
61 | SR2L54 | NELAMANGALA - MYSORE II | 132.897 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
62 | SR2L55 | NEYVELI - BAHOOR | 52.5 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
63 | SRL56 | NEYVELI - VILLIANUR | 63.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
64 | SRL97 | NEYVELI TS II - NAGAPATTINAM PS - I | 49.217 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
65 | SR2L57 | NEYVELI TS II - PUDUCHERRY-I | 68 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
66 | SR2L58 | NEYVELI TS II - PUGALUR | 198.047 | SR-II | -- | 2016-06-04 | 16:36 | 2016-06-04 | 16:59 | -- | -- | -- | 0 | 0.38333 | 0 | 0 | N/A | N/A | N/A | Line tripped on B-N (Ph-earth) transient fault. FLR: 164.9 Km from Puagalur end. Auto-reclose unsuccessful due to receipt of Direct Trip from Neyveli TS2 end. |  | 100
[5 empty] | -- | 2016-06-11 | 10:06 | 2016-06-11 | 16:48 | -- | -- | -- | 0 | 0 | 0 | 6.7 | N/A | N/A | N/A | Shut down availed by M/s NLC for Annual maintenance works at Neyveli end vide SRLDC code no. CR-06/381.
[5 empty] | -- | 2016-06-15 | 10:05 | 2016-06-15 | 15:54 | -- | -- | -- | 0 | 0 | 0 | 5.8167 | N/A | N/A | N/A | Shut down availed by M/s NLC for replacement of bus isolator operating mechanism at Neyveli TS2 end vide SRLDC code no. CR-06/488.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.38333 | 0 | 12.5167
67 | SR2L60 | NEYVELI TS II EXP - PUGALUR | 199.671 | SR-II | -- | 2016-06-09 | 15:28 | 2016-06-09 | 16:37 | -- | -- | -- | 0 | 0 | 0 | 1.15 | N/A | N/A | N/A | Shut down availed by M/s NLC for installation of PMU panel at TS2 Exp end vide SRLDC code no. CR-06/308. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 1.15
68 | SR2L61 | NEYVELI TS-I EXPANSION - NAGAPATTINAM PS - I | 171.95 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
69 | SR2L62 | NEYVELI TS-II - NEYVELI TS-I EXPANSION | 13.939 | SR-II | -- | 2016-06-25 | 14:49 | 2016-06-25 | 19:53 | -- | -- | -- | 0 | 0 | 0 | 5.0667 | N/A | N/A | N/A | Shut down availed by M/s NLC for attending hotspot in wave trap connector at Neyveli TS1 Expansion end vide SRLDC code no. CR-06/857. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.0667
70 | SR2L63 | NEYVELI-SALEM - I | 174.949 | SR-II | -- | 2016-06-06 | 7:52 | 2016-06-10 | 19:08 | -- | -- | -- | 0 | 0 | 0 | 107.2667 | N/A | N/A | N/A | Shut down availed by M/s NLC for isolator rejunavation works at Neyveli end vide SRLDC code no. CR-06/189. |  | 100
[6 empty] | 2016-06-16 | 12:24 | 2016-06-16 | 15:14 | -- | -- | -- | 0 | 0 | 0 | 2.8333 | N/A | N/A | N/A | Shut down availed by M/s NLC for attending jumper cut in Y-phase wave trap at Neyveli TS-2 end vide SRLDC code no. CR-06/532.
[6 empty] | 2016-06-18 | 14:17 | 2016-06-18 | 17:31 | -- | -- | -- | 0 | 0 | 0 | 3.2333 | N/A | N/A | N/A | Shut down availed by M/s NLC for replacement of bus isolator at Neyveli end vide SRLDC code no. CR-06/615.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 113.3333
71 | SR2L64 | NEYVELI-SALEM - II | 178.72 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
72 | SR2L103 | NP KUNTA - KOLAR I | 130.702 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
73 | SR2L65 | PALAKKAD - TRICHUR I | 84.785 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
74 | SR2L66 | PALAKKAD - TRICHUR II | 84.785 | SR-II | -- | 2016-06-03 | 8:25 | 2016-06-03 | 14:34 | -- | -- | -- | 6.15 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-06/87. |  | 97.5278
[5 empty] | Insulator decapping | 2016-06-18 | 2:18 | 2016-06-18 | 13:57 |  | 1 string | 0.48542 | 11.65 | 0 | 0 | 0 | 1 | N | -0.51458 | Tripped on B-N (Ph-Ground) fault. FLR: 36.166km from Palakkad end. Insulator decapping occurred at Loc. 232.
[6 empty] | Sub Total --> | [6 empty] | 17.8 | 0 | 0 | 0
75 | SR2L67 | PUDUCHERRY-SVCHATRAM-I | 128.594 | SR-II | -- | 2016-06-10 | 10:17 | 2016-06-10 | 15:01 | -- | -- | -- | 0 | 0 | 0 | 4.7333 | N/A | N/A | N/A | Shut down availed by M/s TNEB for monthly maintenance works at SV Chatram end vide SRLDC code no. CR-06/339. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 4.7333
76 | SR2L68 | PUGALUR - MADURAI - I | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
77 | SR2L69 | PUGALUR - MADURAI - II | 123.643 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
78 | SR2L70 | SALEM - UDUMALPET I | 150.543 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
79 | SR2L71 | SALEM - UDUMALPET II | 137.91 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
80 | SR2L72 | SRIPERUMBUDUR - THIRUVALAM I | 85.039 | SR-II | -- | 2016-06-14 | 9:09 | 2016-06-14 | 16:27 | -- | -- | -- | 0 | 0 | 0 | 7.3 | N/A | N/A | N/A | Shut down availed for replacement of disc insulators with CLR insulators in polluted stretch vide SRLDC code no. CR-06/445. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 7.3
81 | SR2L73 | SVCHATRAM-SRIPERUMBUDUR-I | 10.08 | SR-II | -- | 2016-06-17 | 9:55 | 2016-06-17 | 15:33 | -- | -- | -- | 0 | 0 | 0 | 5.6333 | N/A | N/A | N/A | Shut down availed by M/s TNEB for monthly maintenance works at SV Chatram end vide SRLDC code no. CR-06/559. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.6333
82 | SR2L74 | THIRUNELVELI - EDAMON - I | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
83 | SR2L75 | THIRUNELVELI - EDAMON - II | 81.94 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
84 | SR2L76 | THIRUNELVELI - KUDAMKULAM-I | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
85 | SR2L77 | THIRUNELVELI - KUDAMKULAM-II | 72.489 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
86 | SR2L78 | THIRUNELVELI - KUDAMKULAM-III | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
87 | SR2L79 | THIRUNELVELI - KUDAMKULAM-IV | 79.534 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
88 | SR2L80 | THIRUNELVELI - TRIVANDRUM - I | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
89 | SR2L81 | THIRUNELVELI - TRIVANDRUM - II | 160.4 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
90 | SR2L82 | THIRUNELVELI - UDUMALPET I | 264.987 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
91 | SR2L83 | THIRUNELVELI - UDUMALPET II | 264.987 | SR-II | -- | 2016-06-16 | 18:56 | 2016-06-16 | 19:05 | -- | -- | -- | 0.15 | 0 | 0 | 0 | N/A | N/A | N/A | Tripped at Tirunelveli end only on Zone-4 fault which was enabled during testing of Main-2 relay due to some other fault in the system. |  | 99.9792
[6 empty] | Sub Total --> | [6 empty] | 0.15 | 0 | 0 | 0
92 | SR2L84 | THIRUVALAM - KALIVANDAPATTU I | 114.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
93 | SR2L85 | THIRUVALAM - KALIVANDAPATTU II | 114.35 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
94 | SR2L86 | TRICHUR - KOCHI I | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
95 | SR2L87 | TRICHUR - KOCHI II | 78.197 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
96 | SR2L88 | TRICHY - KARAIKUDI - I | 97.699 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
97 | SR2L89 | TRICHY - MADURAI - I | 130.486 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
98 | SR2L90 | TUTICORIN JV TPS - TUTICORIN POOLING STN I | 127.232 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
99 | SR2L91 | UDUMALPET - MADURAI | 127.232 | SR-II | -- | 2016-06-02 | 6:56 | 2016-06-02 | 18:18 | -- | -- | -- | 0 | 0 | 0 | 11.3667 | N/A | N/A | N/A | Shut down availed for construction works of 765KV Tuticorin - Dharmapuri D/C line (Part-I) vide SRLDC code no. CR-06/35. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.3667
100 | SR2L92 | UDUMALPET - PALAKKAD I | 95.723 | SR-II | -- | 2016-06-02 | 9:18 | 2016-06-02 | 14:48 | -- | -- | -- | 5.5 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-06/55. |  | 99.2361
[6 empty] | Sub Total --> | [6 empty] | 5.5 | 0 | 0 | 0
101 | SR2L93 | UDUMALPET - PALAKKAD II | 95.723 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
102 | SR2L94 | VALLUR - KALIVANDAPATTU I | 133.846 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
103 | SR2L95 | VALLUR - KALIVANDAPATTU II | 133.846 | SR-II | -- | 2016-06-06 | 23:15 | 2016-06-06 | 23:35 | -- | -- | -- | 0 | 0 | 0.33333 | 0 | N/A | N/A | N/A | Auto reclosure unsuccessful on Y-G fault with powerswing detection in zone 1. FLR: 33.68kM from Kalivanthapattu end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.33333 | 0
104 | SR2T1 | ARASUR ICT - I | 315 | SR-II | -- | 2016-06-25 | 9:08 | 2016-06-25 | 14:54 | -- | -- | -- | 5.7667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending oil leakage vide SRLDC code no. CR-06/851. |  | 99.1991
[6 empty] | Sub Total --> | [6 empty] | 5.7667 | 0 | 0 | 0
105 | SR2T2 | ARASUR ICT - II | 315 | SR-II | -- | 2016-06-06 | 9:09 | 2016-06-06 | 14:38 | -- | -- | -- | 0 | 0 | 0 | 5.48 | N/A | N/A | N/A | Shut down availed for implementation of SPS scheme as per SRPC recommendations vide SRLDC code no. CR-06/193. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 5.48
106 | SR2T3 | BANGALORE ICT - I | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
107 | SR2T4 | BANGALORE ICT - II | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
108 | SR2T5 | BIDADI ICT-I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
109 | SR2T6 | BIDADI ICT-II | 500 | SR-II | -- | 2016-06-16 | 9:35 | 2016-06-16 | 15:09 | -- | -- | -- | 5.5667 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for AMP works vide SRLDC code no. CR-06/525. |  | 99.2269
[6 empty] | Sub Total --> | [6 empty] | 5.5667 | 0 | 0 | 0
110 | SR2T7 | HASSAN ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
111 | SR2T8 | HASSAN ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
112 | SR2T9 | HIRIYUR ICT | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
113 | SR2T10 | HIRIYUR ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
114 | SR2T11 | HOSUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
115 | SR2T12 | HOSUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
116 | SR2T13 | HOSUR ICT - III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
117 | SR2T14 | KALIVANDAPATTU ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
118 | SR2T15 | KALIVANDAPATTU ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
119 | SR2T16 | KARAIKUDI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
120 | SR2T17 | KARAIKUDI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
121 | SR2T18 | KOCHI ICT I | 315 | SR-II | -- | 2016-06-02 | 9:05 | 2016-06-02 | 15:53 | -- | -- | -- | 0 | 0 | 0 | 6.8 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-06/48. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 6.8
122 | SR2T19 | KOCHI ICT II | 315 | SR-II | -- | 2016-06-02 | 9:05 | 2016-06-02 | 19:18 | -- | -- | -- | 0 | 0 | 0 | 10.2167 | N/A | N/A | N/A | Hand tripped as per SRLDC instruction for power regulation vide SRLDC code no. CR-06/49. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 10.2167
123 | SR2T20 | KOLAR ICT | 501 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
124 | SR2T21 | KOLAR ICT-II | 501 | SR-II | -- | 2016-06-18 | 11:02 | 2016-06-18 | 12:29 | -- | -- | -- | 1.45 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changeover and attending hotspot vide SRLDC code no. CR-06/607. |  | 99.7801
[6 empty] | 2016-06-30 | 10:34 | 2016-06-30 | 10:42 |  |  |  | 0.13333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for combination changing vide SRLDC code no. CR-06/999.
[6 empty] | Sub Total --> | [6 empty] | 1.5833 | 0 | 0 | 0
125 | SR2T46 | KOZHIKODE - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
126 | SR2T47 | KOZHIKODE - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
127 | SR2T22 | MADURAI ICT - I | 315 | SR-II | -- | 2016-06-08 | 11:13 | 2016-06-08 | 11:40 | -- | -- | -- | 0 | 0 | 0 | 0.45 | N/A | N/A | N/A | Hand tripped for tap changing as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-06/263. |  | 100
[6 empty] | 2016-06-26 | 9:33 | 2016-06-26 | 9:45 |  |  |  | 0 | 0 | 0 | 0.2 | N/A | N/A | N/A | Shut down availed for transportation of new ICT-3 under strung bus of ICT-1 vide SRLDC code no. CR-06/876.
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.65
128 | SR2T23 | MADURAI ICT - II | 315 | SR-II | -- | 2016-06-08 | 10:51 | 2016-06-08 | 11:05 | -- | -- | -- | 0 | 0 | 0 | 0.23333 | N/A | N/A | N/A | Hand tripped for tap changing as per SRLDC instruction for voltage regulation vide SRLDC code no. CR-06/260. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0.23333
129 | SR2T24 | MYSORE ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
130 | SR2T25 | MYSORE ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
131 | SR2T26 | NARENDRA ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
132 | SR2T27 | NARENDRA ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
133 | SR2T28 | PALAKKAD ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
134 | SR2T29 | PALAKKAD ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
135 | SR2T30 | PUDUCHERRY ICT-I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
136 | SR2T31 | PUDUCHERRY ICT-II | 315 | SR-II | -- | 2016-06-15 | 16:58 | 2016-06-15 | 17:48 | -- | -- | -- | 0.83333 | 0 | 0 | 0 | N/A | N/A | N/A | Shut down availed for attending hotspot in 400 kV R-phase bushing terminal vide SRLDC code no. CR-06/502. |  | 99.8843
[6 empty] | Sub Total --> | [6 empty] | 0.83333 | 0 | 0 | 0
137 | SR2T32 | PUGALUR ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
138 | SR2T33 | PUGALUR ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
139 | SR2T34 | THIRUNELVELI ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
140 | SR2T35 | THIRUNELVELI ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
141 | SR2T36 | THIRUVALAM ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
142 | SR2T37 | THIRUVALAM ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
143 | SR2T38 | TRICHY ICT - I | 315 | SR-II | -- | 2016-06-18 | 11:08 | 2016-06-18 | 18:55 | -- | -- | -- | 7.7833 | 0 | 0 | 0 | -- | -- | -- | Shut down availed for AMP works and replacement of 220kV side CT vide SRLDC code no. CR-06/609. |  | 98.919
[6 empty] | Sub Total --> | [6 empty] | 7.7833 | 0 | 0 | 0
144 | SR2T39 | TRICHY ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
145 | SR2T40 | TRIVANDRUM - ICT I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
146 | SR2T41 | TRIVANDRUM - ICT II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
147 | SR2T42 | TRIVANDRUM - ICT III | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
148 | SR2T48 | TUMKUR - ICT I | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
149 | SR2T49 | TUMKUR - ICT II | 500 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
150 | SR2T43 | UDUMALPET ICT - I | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
151 | SR2T44 | UDUMALPET ICT - II | 315 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
152 | SR2T45 | UDUMALPET ICT - III | 315 | SR-II | -- | 2016-06-27 | 10:06 | 2016-06-27 | 21:11 | -- | -- | -- | 0 | 0 | 0 | 11.0833 | N/A | N/A | N/A | Shut down availed by TNEB for attending dropper jumper binding and tightness checking works at 230kV Myvadi TNEB SS vide SRLDC code no. CR-06/897. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 11.0833
153 | SR2R1 | BANGALORE BUS REACTOR | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-03 | 18:38 | -- | -- | -- | 0 | 0 | 0 | 66.6333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | 2016-06-04 | 10:33 | 2016-06-05 | 22:01 | -- | -- | -- | 0 | 0 | 0 | 35.4667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2016-06-08 | 7:30 | 2016-06-22 | 23:13 |  |  |  | 0 | 0 | 0 | 351.7167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2016-06-24 | 7:20 | 2016-06-25 | 22:08 |  |  |  | 0 | 0 | 0 | 38.8 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2016-06-28 | 9:07 | 2016-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 62.8833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 555.5
154 | SR2R2 | BIDADI BUS REACTOR - I | 63 | SR-II | -- | 2016-06-03 | 8:16 | 2016-06-03 | 21:53 | -- | -- | -- | 0 | 0 | 0 | 13.6167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-10 | 6:36 | 2016-06-10 | 22:02 | -- | -- | -- | 0 | 0 | 0 | 15.4333 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2016-06-15 | 9:49 | 2016-06-18 | 22:29 | -- | -- | -- | 0 | 0 | 0 | 84.6667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2016-06-20 | 10:52 | 2016-06-22 | 22:41 |  |  |  | 0 | 0 | 0 | 59.8167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2016-06-24 | 7:14 | 2016-07-01 | 0:00 |  |  |  | 0 | 0 | 0 | 160.7667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 334.3
155 | SR2R3 | HASSAN BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
156 | SR2R4 | HIRIYUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
157 | SR2R5 | HOSUR BUS REACTOR - I | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-07-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 720 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 720
158 | SR2R6 | KARAIKUDI BUS REACTOR - I | 80 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
159 | SR2R7 | KOCHI BUS REACTOR I | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-22 | 23:31 | -- | -- | -- | 0 | 0 | 0 | 527.5167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 527.5167
160 | SR2R8 | KOLAR BUS REACTOR - I | 63 | SR-II | -- | 2016-06-01 | 7:22 | 2016-06-01 | 23:04 | -- | -- | -- | 0 | 0 | 0 | 15.7 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-03 | 8:14 | 2016-06-03 | 23:43 | -- | -- | -- | 0 | 0 | 0 | 15.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2016-06-10 | 6:41 | 2016-06-10 | 22:02 | -- | -- | -- | 0 | 0 | 0 | 15.35 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2016-06-16 | 10:22 | 2016-06-18 | 22:29 | -- | -- | -- | 0 | 0 | 0 | 60.1167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 106.65
161 | SR2R28 | KUDGI BUS REACTOR - I | 125 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
162 | SR2R9 | MYSORE BUS REACTOR | 50 | SR-II | -- | 2016-06-03 | 8:19 | 2016-06-03 | 21:47 | -- | -- | -- | 0 | 0 | 0 | 13.4667 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-20 | 11:01 | 2016-06-20 | 21:54 | -- | -- | -- | 0 | 0 | 0 | 10.8833
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 24.35
163 | SR2R10 | NARENDRA BUS REACTOR | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
164 | SR2R11 | PALAKKAD BUS REACTOR - I | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-18 | 13:49 | -- | -- | -- | 0 | 0 | 0 | 421.8167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-20 | 11:01 | 2016-06-22 | 22:36 | -- | -- | -- | 0 | 0 | 0 | 59.5833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 481.4
165 | SR2R12 | SALEM BUS REACTOR - I | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-25 | 22:38 | -- | -- | -- | 0 | 0 | 0 | 598.6334 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 598.6334
166 | SR2R13 | SRIPERUMBUDUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
167 | SR2R14 | THIRUNELVELI BUS REACTOR - I | 63 | SR-II | -- | 2016-06-20 | 10:41 | 2016-06-20 | 21:58 | -- | -- | -- | 0 | 0 | 0 | 11.2833 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-21 | 9:14 | 2016-06-22 | 22:17 | -- | -- | -- | 0 | 0 | 0 | 37.05 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 48.3333
168 | SR2R15 | THIRUNELVELI BUS REACTOR - II | 63 | SR-II | -- | 2016-06-16 | 10:26 | 2016-06-18 | 22:47 | -- | -- | -- | 0 | 0 | 0 | 60.35 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-20 | 10:43 | 2016-06-20 | 21:59 | -- | -- | -- | 0 | 0 | 0 | 11.2667 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2016-06-21 | 9:17 | 2016-06-22 | 22:24 | -- | -- | -- | 0 | 0 | 0 | 37.1167 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 108.7333
169 | SR2R16 | THIRUVALAM BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
170 | SR2R29 | TUMKUR BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
171 | SR2R17 | TUTICORIN POOLING STN BUS REACTOR - I | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
172 | SR2R18 | Kolar Line Reactor at Bangalore | 50 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-05 | 22:12 | -- | -- | -- | 0 | 0 | 0 | 118.2 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-14 | 18:56 | 2016-07-01 | 0:00 | -- | -- | -- | 0 | 0 | 0 | 389.0667 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 507.2667
173 | SR2R26 | Mysore 1 Line Reactor at Kozhikode | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
174 | SR2R27 | Mysore 2 Line Reactor at Kozhikode | 50 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-05 | 0:27 | -- | -- | -- | 0 | 0 | 0 | 96.45 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 96.45
175 | SR2R19 | Neyveli TS II Exp Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
176 | SR2R20 | Neyveli TS II Line Reactor at Pugalur | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
177 | SR2R21 | Thirunelveli 1 Line Reactor at Udumalpet | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-09 | 23:06 | -- | -- | -- | 0 | 0 | 0 | 215.1 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-11 | 12:00 | 2016-06-18 | 22:29 | -- | -- | -- | 0 | 0 | 0 | 178.4833 | N/A | N/A | N/A | H/T for voltage regulation
[5 empty] | -- | 2016-06-21 | 10:22 | 2016-06-23 | 11:27 | -- | -- | -- | 0 | 0 | 0 | 49.0833 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | 2016-06-23 | 12:38 | 2016-06-25 | 22:02 |  |  |  | 0 | 0 | 0 | 57.4
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 500.0667
178 | SR2R22 | Thirunelveli 2 Line Reactor at Udumalpet | 63 | SR-II | -- | 2016-06-01 | 0:00 | 2016-06-09 | 23:07 | -- | -- | -- | 0 | 0 | 0 | 215.1167 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[5 empty] | -- | 2016-06-11 | 12:01 | 2016-06-23 | 12:39 | -- | -- | -- | 0 | 0 | 0 | 288.6333 | N/A | N/A | N/A | H/T for voltage regulation
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 503.75
179 | SR2R23 | Udumalpet 1 Line Reactor at Thirunelveli | 63 | SR-II | -- | 2016-06-20 | 10:48 | 2016-06-22 | 22:26 | -- | -- | -- | 0 | 0 | 0 | 59.6333 | N/A | N/A | N/A | H/T for voltage regulation |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 59.6333
180 | SR2R24 | Udumalpet 2 Line Reactor at Thirunelveli | 63 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
181 | SR2R25 | Vallur 1 Line Reactor at Kalivandapattu | 50 | SR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
182 | SR2P1 | TALCHER - KOLAR HVDC POLE - I | 1000 | SR-II | -- | 2016-06-03 | 4:21 | 2016-06-03 | 4:21 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 249.9 KM from Talcher end. (Tower No. 679). |  | 100
[6 empty] | 2016-06-17 | 16:29 | 2016-06-17 | 16:29 |  |  |  | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 501.16 kM from Kolar end (Tower no. 2325).
[6 empty] | 2016-06-17 | 16:35 | 2016-06-17 | 17:53 |  |  |  | 0 | 1.3 | 0 | 0 | N/A | N/A | N/A | Pole blocked on line fault. FLR : 501.16 KM from Kolar end (Tower no. 2325), due to flashover with OPGW wire of 220kV Vijayawada - Tallapalli APTRANSCO line, during heavy wind.
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.3 | 0 | 0
183 | SR2P2 | TALCHER - KOLAR HVDC POLE - II | 1000 | SR-II | -- | 2016-06-19 | 13:31 | 2016-06-19 | 13:31 | -- | -- | -- | 0 | 0 | 0 | 0 | N/A | N/A | N/A | LFL and DC line fault recovery sequence operated at 678 kM from Talcher end (Tower no. 1829). |  | 98.7523
[6 empty] | 2016-06-23 | 5:27 | 2016-06-23 | 14:26 |  |  |  | 8.9833 | 0 | 0 | 0 | N/A | N/A | N/A | Pole blocked due to operation of Y-ph OLTC diverter switch PRV of converter Transformer at Kolar end.
[6 empty] | Sub Total --> | [6 empty] | 8.9833 | 0 | 0 | 0
[22 empty] | 18289.6088 | 16080.8405
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse