## SOP
[20 empty] | Prepared by | Anil Vaddepally Manager
Standard of Performance data for the month of JUNE - 2021
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., PNMTL Transmission System
ANNEXURE - A
Sl.No | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency | Remarks
[6 empty] | Date | Time | Date | Time | No. of towers damaged | No. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | PNMTL1 | NAGAPATTINAM - SALEM POOLING STATION I | 203.947 | SR-II | -- | 2021-06-03 | 23:35 | 2021-06-03 | 23:35 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Auto reclosed successfully on B-N (Ph-earth) transient fault. FLR: 88.2kM from Nagapattinam end. |  | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
1 | PNMTL2 | NAGAPATTINAM - SALEM POOLING STATION II | 203.947 | SR-II | -- | [16 empty] | 100
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 0
1 | PNMTL3 | 765kV TUMKUR - SALEM POOLING STN II | 222.146 | SR-II | -- | 2021-06-01 | 0:00 | 2021-06-03 | 10:50 |  |  |  | 0 | 0 | 0 | 58.833 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code CR:05/349(432KV-431KV) CR-06/230(404-406) kV |  | 100
[6 empty] | 2021-06-03 | 20:57 | 2021-06-28 | 9:18 |  |  |  | 0 | 0 | 0 | 588.35 |  |  |  | Hand tripped as per SRLDC instruction for voltage regulation in the system vide SRLDC code no. CR- 06/274 (431 - 429 kV).CR-06/2694(401-404) kV
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 647.183
Note in type of failure column please indicate following :
1) Hardware failure like Earthwire failure, Jumper snapping, Conductor snapping, Insulator failure, Others etc
2) Transformer / Reactor failure like winding failure, Bushing failure, OLTC failure, Others etc
3) Tower collapse