## May15
|  | ELEMENT WISE AVAILABILITY OF = | 2015-05-01
744
|  | NAME OF LINE/ICT | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
SN | Unique ID of transmission Element |  |  |  |  | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | [6 empty] | CATEGORY
1 | WR1L2 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I |  | 2015-05-15 | 22:00 | 2015-05-15 | 22:10 |  |  |  | 0.0069444 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO EARTH FAULT. F.D 140 KM FROM KORBA,& 56 KM FROM BUDIPADAR | WRPC |  | LEFT
1 | WR1L2 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I |  | 2015-05-15 | 22:10 | 2015-05-16 | 22:17 |  |  |  | 0 | 0 | 0 | 1899-12-31 00:07 |  |  |  | KEPT UN CHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
1 | WR1L2 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I |  | 2015-05-21 | 18:12 | 2015-05-21 | 20:20 |  |  |  | 0 | 0.088889 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO PROBLEM AT BUDIPADAR S/S |  |  | OMSU
1 |  | 220kV KORBA(EAST)-BUDDHIPADAR III Total | [10 empty] | 0.0069444 | 0.088889 | 0 | 1899-12-31 00:07 | [5 empty] | 99.98%
2 | WR1L43 | 400kV RAIPUR-RAIGARH I | 217.02 | WRTS-I |  | 2015-05-29 | 15:13 | 2015-05-29 | 15:51 |  |  |  | 0.026389 | 0 | 0 | 0 |  |  |  | TRIPPED DUE TO RELAY MAL OPERATION AT RAIGARH. DT RECEIVED AT RAIPUR END |  |  | SRMT
2 |  | 400kV RAIPUR-RAIGARH I Total | [10 empty] | 0.026389 | 0 | 0 | 0 | [5 empty] | 99.91%
3 | WR1L44 | 400kV RAIPUR-KWPCL II | 203.02 | WRTS-I
3 |  | 400kV RAIPUR-KWPCL II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
4 | WR1L45 | 400kV KWPCL-RAIGARH II | 14 | WRTS-I
4 |  | 400kV KWPCL-RAIGARH II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
5 | WR1L110 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I
5 |  | 400kV RAIGARH-IBEUL I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
6 | WR1L111 | 400kV IBEUL-JHARSUGUDA I | 20.03 | WRTS-I
6 |  | 400kV IBEUL-JHARSUGUDA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
7 | WR1L49 | 400kV JHARSUGUDA-ROURKELA I | 142.45 | WRTS-I
7 |  | 400kV JHARSUGUDA-ROURKELA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
8 | WR1L98 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I |  | 2015-05-02 | 9:26 | 2015-05-02 | 19:39 |  |  |  | 0.42569 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED BY ER-II (ROURKELA) |  |  | OSPT
8 | WR1L98 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I |  | 2015-05-06 | 5:12 | 2015-05-06 | 11:24 |  |  |  | 0.25833 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED BY ER-II (ROURKELA) |  |  | OSPT
8 |  | 400kV RAIGARH-ROURKELA II Total | [10 empty] | 0.68403 | 0 | 0 | 0 | [5 empty] | 97.79%
9 | WR1L50 | 400KV RANCHI-SIPAT I | 405.77 | WRTS-I |  | 2015-05-03 | 10:03 | 2015-05-03 | 15:23 |  |  |  | 0 | 0 | 0.22222 | 0 |  |  |  | H/T FOR REPLACEMENT OF DAMAGED INSULATORS BY ER |  |  | LMAC
9 | WR1L50 | 400KV RANCHI-SIPAT I | 405.77 | WRTS-I |  | 2015-05-27 | 13:45 | 2015-05-27 | 19:51 |  |  |  | 0 | 0 | 0 | 0.25417 |  |  |  | EMERGENCY OUTAGE AVAILED BY NTPC SIPAT FOR L/R OTI REPLACEMENT WORK. |  |  | OSFD
9 |  | 400KV RANCHI-SIPAT I Total | [10 empty] | 0 | 0 | 0.22222 | 0.25417 | [5 empty] | 100%
10 | WR1L51 | 400KV RANCHI-SIPAT II | 405.77 | WRTS-I |  | 2015-05-04 | 9:22 | 2015-05-04 | 13:15 |  |  |  | 0 | 0 | 0.16181 | 0 |  |  |  | H/T FOR REPLACEMENT OF DAMAGED INSULATORS BY ER |  |  | LMAC
10 |  | 400KV RANCHI-SIPAT II Total | [10 empty] | 0 | 0 | 0.16181 | 0 | [5 empty] | 100%
11 | WR1L52 | 400kV RAIPUR-KSK III | 134.74 | WRTS-I |  | 2015-04-25 | 17:33 | 2015-05-06 | 20:34 |  |  |  | 0 | 0 | 1900-01-04 20:34 | 0 |  |  |  | LINE TRIPPED ON B PH TO E FAULT DUE TO THEFT OF LARGE BRACING MEMBERS FROM MAIN LEGS C AND D AT LOC. NO. 547 BY MISCREANT PEOPLES. THIS MAY CAUSE TOWER COLLAPSED AT LOC. NO. 547 DURING HEAVY LIGHTENING AND THUNDER STORM 69 KM FROM RAIPUR. |  |  | LAMC
11 |  | 400kV RAIPUR-KSK III Total | [10 empty] | 0 | 0 | 1900-01-04 20:34 | 0 | [5 empty] | 100%
12 | WR1L105 | 400kV KSK-RKKML III | 82.248 | WRTS-I |  | 2015-05-21 | 9:52 | 2015-05-21 | 17:35 |  |  |  | 0 | 0 | 0 | 0.32153 |  |  |  | H/T FOR RELAY REPLACEMENT WORKS AT RKKML END |  |  | OSPD
12 |  | 400kV KSK-RKKML III Total | [10 empty] | 0 | 0 | 0 | 0.32153 | [5 empty] | 100%
13 | WR1L106 | 400kV RKKML-RAIGARH III | 3.896 | WRTS-I |  | 2015-05-21 | 9:50 | 2015-05-21 | 17:22 |  |  |  | 0 | 0 | 0 | 0.31389 |  |  |  | H/T FOR RELAY REPLACEMENT WORKS AT RKKML END |  |  | OSPD
13 |  | 400kV RKKML-RAIGARH III Total | [10 empty] | 0 | 0 | 0 | 0.31389 | [5 empty] | 100%
14 | WR1L103 | 400kV RAIPUR-KSK IV | 161.82 | WRTS-I |  | 2015-04-25 | 17:33 | 2015-05-06 | 20:39 |  |  |  | 0 | 0 | 1900-01-04 20:39 | 0 |  |  |  | LINE TRIPPED ON B PH TO E FAULT DUE TO THEFT OF LARGE BRACING MEMBERS FROM MAIN LEGS C AND D AT LOC. NO. 547 BY MISCREANT PEOPLES. THIS MAY CAUSE TOWER COLLAPSED AT LOC. NO. 547 DURING HEAVY LIGHTENING AND THUNDER STORM 69 KM FROM RAIPUR. |  |  | LAMC
14 |  | 400kV RAIPUR-KSK IV Total | [10 empty] | 0 | 0 | 1900-01-04 20:39 | 0 | [5 empty] | 100%
15 | WR1L97 | 400kV KSK-RAIGARH IV | 113.389 | WRTS-I
15 |  | 400kV KSK-RAIGARH IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
16 | WR1L56 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I
16 |  | 400kV RAIGARH-JHARSUGUDA III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
17 | WR1L57 | 400kV JHARSUGUDA-ROURKELA III | 143.06 | WRTS-I
17 |  | 400kV JHARSUGUDA-ROURKELA III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
18 | WR1L58 | 400kV RAIGARH-STERLITE IV | 105 | WRTS-I
18 |  | 400kV RAIGARH-STERLITE IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
19 | WR1L59 | 400kV STERLITE-ROURKELA IV | 104.28 | WRTS-I
19 |  | 400kV STERLITE-ROURKELA IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
20 | WR1L60 | 765kV D'JAIGARH-BILASPUR | 90 | WRTS-I
20 |  | 765kV D'JAIGARH-BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
21 | WR1L61 | 765kV D'JAIGARH-RANCHI | 303 | WRTS-I |  | 2015-05-12 | 13:53 | 2015-05-13 | 20:37 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:44 |  |  |  | OUTAGE AVAILED FOR ERECTION OF AUXILARY BUS FOR SPARE REACTOR AT DHARAMJAYGARH END. |  |  | SCSD
21 |  | 765kV D'JAIGARH-RANCHI Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 06:44 | [5 empty] | 100%
22 | WR1L101 | 765kV D'JAIGARH- JHARSUGUDA I | 149.789 | WRTS-I
22 |  | 765kV D'JAIGARH- JHARSUGUDA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
23 | WR1L102 | 765kV D'JAIGARH- JHARSUGUDA II | 149.789 | WRTS-I
23 |  | 765kV D'JAIGARH- JHARSUGUDA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
24 | WR1L3 | 400kV KORBA-KORBA(WEST) | 14 | WRTS-I |  | 2015-05-29 | 9:30 | 2015-05-30 | 22:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:14 |  |  |  | TO ATTEND HOTSPOT BY KORBA(W) |  |  | OSFD
24 |  | 400kV KORBA-KORBA(WEST) Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 13:14 | [5 empty] | 100%
25 | WR1L4 | 400kV KORBA-BHILAI I | 197 | WRTS-I
25 |  | 400kV KORBA-BHILAI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
26 | WR1L5 | 400kV KORBA-BHILAI II | 192 | WRTS-I |  | 2015-05-04 | 10:56 | 2015-05-07 | 9:51 |  |  |  | 0 | 0 | 0 | 1900-01-01 22:55 |  |  |  | FOR CROSSING WORKS OF 765KV DHARAMJAYGARH-JABALPUR LINE BY JTCL |  |  | LCSD
26 |  | 400kV KORBA-BHILAI II Total | [10 empty] | 0 | 0 | 0 | 1900-01-01 22:55 | [5 empty] | 100%
27 | WR1L6 | 400kV BHILAI-KORADI | 272 | WRTS-I | Earthwire failure | 2015-05-31 | 19:09 | 2015-05-31 | 24:00 |  |  | 0.20208 | 0.20208 | 0 | 0 | 0 | 2 | N | -1.7979 | LINE TRIPPED ON B-PHASE TO E-FAULT. FL = 210 KM FROM KORADI. LINE TEST CHARGED AT 20:11 BUT LINE TRIPPED ON SOTF. LINE EARTH WIRE CAME OUT FROM CLAMP. FAULT IS UNDER CG(O&M) |  |  | LHWT
27 |  | 400kV BHILAI-KORADI Total | [10 empty] | 0.20208 | 0 | 0 | 0 | [5 empty] | 99.35%
28 | WR1L7 | 400kV KORADI-SATPURA | 149 | WRTS-I
28 |  | 400kV KORADI-SATPURA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
29 | WR1L8 | 400kV RAIPUR-BHILAI I | 13 | WRTS-I
29 |  | 400kV RAIPUR-BHILAI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
30 | WR1L9 | 400kV BHILAI-BHADRAVATI I | 322 | WRTS-I
30 |  | 400kV BHILAI-BHADRAVATI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
31 | WR1L10 | 400kV RAIPUR-BHADRAVATI I | 333 | WRTS-I |  | 2015-05-01 | 9:00 | 2015-05-01 | 17:23 |  |  |  | 0 | 0 | 0 | 0.34931 |  |  |  | LINE H/T FOR NTAMC & CSD WORKS AT RAIPUR SS |  |  | SCSD
31 |  | 400kV RAIPUR-BHADRAVATI I Total | [10 empty] | 0 | 0 | 0 | 0.34931 | [5 empty] | 100%
32 | WR1L11 | 400kV RAIPUR-BHADRAVATI II | 345.55 | WRTS-I |  | 2015-05-04 | 9:10 | 2015-05-04 | 19:23 |  |  |  | 0 | 0 | 0 | 0.42569 |  |  |  | LINE H/T FOR CSD & NTAMC WORKS AT RAIPUR END |  |  | SCSD
32 |  | 400kV RAIPUR-BHADRAVATI II Total | [10 empty] | 0 | 0 | 0 | 0.42569 | [5 empty] | 100%
33 | WR1L12 | 400kV RAIPUR-BHADRAVATI III | 345.55 | WRTS-I |  | 2015-05-10 | 10:35 | 2015-05-10 | 11:22 |  |  |  | 0 | 0 | 0 | 0.032639 |  |  |  | FOR TAKING LR IN SERVICE AT RAIPUR. |  |  | LVRD
33 |  | 400kV RAIPUR-BHADRAVATI III Total | [10 empty] | 0 | 0 | 0 | 0.032639 | [5 empty] | 100%
34 | WR1L13 | 400kV BHADRAVATI-CHANDRAPUR I | 20 | WRTS-I
34 |  | 400kV BHADRAVATI-CHANDRAPUR I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
35 | WR1L14 | 400kV BHADRAVATI-CHANDRAPUR II | 20 | WRTS-I
35 |  | 400kV BHADRAVATI-CHANDRAPUR II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
36 | WR1L15 | 400kV BHADRAVATI-CHANDRAPUR III | 22.42 | WRTS-I
36 |  | 400kV BHADRAVATI-CHANDRAPUR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
37 | WR1L16 | 400kV BHADRAVATI-CHANDRAPUR IV | 22.42 | WRTS-I
37 |  | 400kV BHADRAVATI-CHANDRAPUR IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-01 | 16:26 | 2015-05-02 | 07:00 |  |  |  | 0 | 0 | 0 | 0.60694 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-01 | 16:26 | 2015-05-02 | 07:00 |  |  |  | 0 | 0 | 0 | 0.60694 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-03 | 16:44 | 2015-05-04 | 7:10 |  |  |  | 0 | 0 | 0 | 0.60139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-06 | 17:57 | 2015-05-07 | 5:55 |  |  |  | 0 | 0 | 0 | 0.49861 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-08 | 17:49 | 2015-05-09 | 7:04 |  |  |  | 0 | 0 | 0 | 0.55208 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-09 | 17:34 | 2015-05-10 | 9:18 |  |  |  | 0 | 0 | 0 | 0.65556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-09 | 17:34 | 2015-05-10 | 9:18 |  |  |  | 0 | 0 | 0 | 0.65556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-10 | 16:40 | 2015-05-11 | 9:46 |  |  |  | 0 | 0 | 0 | 0.7125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-12 | 14:53 | 2015-05-12 | 15:10 |  |  |  | 0.011806 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON R-B PH TO E FAULT,F/L-39.85 KM FROM MAPUSA END HEAVY RAINS & LIGHTNING OCCURRED IN THAT AREA.. |  |  | LPPT
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-12 | 15:10 | 2015-05-12 | 21:47 |  |  |  | 0 | 0.27569 | 0 | 0 |  |  |  | LINE WAS READY FOR CHARGING FROM POWERGRID END,BUT LINE CHARGING WAS DELAYED AT MSETCL END. |  |  | OMSU
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-13 | 03:39 | 2015-05-13 | 07:08 |  |  |  | 0 | 0 | 0 | 0.14514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-15 | 16:19 | 2015-05-16 | 6:34 |  |  |  | 0 | 0 | 0 | 0.59375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-16 | 18:02 | 2015-05-17 | 16:01 |  |  |  | 0 | 0 | 0.91597 | 0 |  |  |  | LINE HAND TRIPPED DUE TO Y PHASE WAVETRAP BPI FAILURE AT MAPUSA DUE TO HEAVY RAIN & THUNDER NATURAL CALAMITY |  |  | SNCC
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-20 | 17:57 | 2015-05-20 | 20:11 |  |  |  | 0 | 0 | 0 | 0.093056 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-22 | 17:38 | 2015-05-23 | 7:30 |  |  |  | 0 | 0 | 0 | 0.57778 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-25 | 17:20 | 2015-05-26 | 08:20 |  |  |  | 0 | 0 | 0 | 0.625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-26 | 17:16 | 2015-05-27 | 08:29 |  |  |  | 0 | 0 | 0 | 0.63403 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-27 | 18:13 | 2015-05-28 | 06:31 |  |  |  | 0 | 0 | 0 | 0.5125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-30 | 17:55 | 2015-05-31 | 9:48 |  |  |  | 0 | 0 | 0 | 0.66181 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-05-31 | 16:10 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 0.32639 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 |  | 400kV KOLHAPUR-MAPUSA I Total | [10 empty] | 0.011806 | 0.27569 | 0.91597 | 1900-01-08 01:25 | [5 empty] | 99.96%
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-02 | 17:42 | 2015-05-03 | 7:37 |  |  |  | 0 | 0 | 0 | 0.57986 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-04 | 18:14 | 2015-05-05 | 6:13 |  |  |  | 0 | 0 | 0 | 0.49931 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-05 | 18:28 | 2015-05-06 | 7:05 |  |  |  | 0 | 0 | 0 | 0.52569 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-07 | 17:10 | 2015-05-08 | 6:57 |  |  |  | 0 | 0 | 0 | 0.57431 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-11 | 17:19 | 2015-05-12 | 08:27 |  |  |  | 0 | 0 | 0 | 0.63056 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-13 | 17:42 | 2015-05-14 | 8:14 |  |  |  | 0 | 0 | 0 | 0.60556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-14 | 17:11 | 2015-05-15 | 6:53 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-14 | 17:11 | 2015-05-15 | 6:53 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-16 | 16:54 | 2015-05-16 | 17:59 |  |  |  | 0 | 0 | 0 | 0.045139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-17 | 16:09 | 2015-05-18 | 09:16 |  |  |  | 0 | 0 | 0 | 0.71319 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-19 | 16:42 | 2015-05-20 | 08:38 |  |  |  | 0 | 0 | 0 | 0.66389 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-24 | 16:03 | 2015-05-24 | 23:16 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-28 | 17:29 | 2015-05-29 | 6:49 |  |  |  | 0 | 0 | 0 | 0.55556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-05-29 | 16:52 | 2015-05-30 | 10:49 |  |  |  | 0 | 0 | 0 | 0.74792 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 |  | 400kV KOLHAPUR-MAPUSA II Total | [10 empty] | 0 | 0 | 0 | 1900-01-06 14:00 | [5 empty] | 100%
40 | WR1L25 | 400kV MAHAN-VINDHYACHAL | 19 | WRTS-I
40 |  | 400kV MAHAN-VINDHYACHAL Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
41 | WR1L26 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2015-05-27 | 23:17 | 2015-05-27 | 23:32 |  |  |  | 0 | 0.010417 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO FAULT IN R PHASE BUSHING OF L/R AT KORBA END, AS ON R PH TO E FAULT,Z2 FAULT,FC- 1.704 KA,FL- 207.3 KM FROM MAHAN END. |  |  | SEFU
41 | WR1L26 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2015-05-27 | 23:17 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-03 00:43 |  |  |  | LINE UNABLE TO RESTORED AFTER OUTAGE DUE TO FAILURE OF REACTOR BUSHING AT KORBA NTPC END. |  |  | GOMD
41 |  | 400kV KORBA-MAHAN Total | [10 empty] | 0 | 0.010417 | 0 | 1900-01-03 00:43 | [5 empty] | 100%
42 | WR1L27 | 400kV VINDHYACHAL-KORBA II | 288.994 | WRTS-I
42 |  | 400kV VINDHYACHAL-KORBA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
43 | WR1L28 | 400kV SATPURA-SEONI | 1.5 | WRTS-I
43 |  | 400kV SATPURA-SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
44 | WR1L29 | 400kV BHILAI-SEONI | 1.5 | WRTS-I
44 |  | 400kV BHILAI-SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
45 | WR1L30 | 400kV BHILAI-BHATAPARA | 90.453 | WRTS-I
45 |  | 400kV BHILAI-BHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
46 | WR1L31 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I |  | 2015-05-31 | 20:42 | 2015-05-31 | 22:41 |  |  |  | 0 | 0.082639 | 0 | 0 |  |  |  | LINE A/R SUCCESSFUL AT BHATAPARA END BUT TRIPPED AT KORBA END. |  |  | SEFU
46 |  | 400kV BHATAPARA-KORBA Total | [10 empty] | 0 | 0.082639 | 0 | 0 | [5 empty] | 100%
47 | WR1L34 | 400kV RAIPUR-SIPAT I | 149.12 | WRTS-I |  | 2015-05-15 | 9:07 | 2015-05-15 | 19:38 |  |  |  | 0 | 0 | 0 | 0.43819 |  |  |  | FOR NTAMC WORKS AT RAIPUR END |  |  | SCSD
47 |  | 400kV RAIPUR-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 0.43819 | [5 empty] | 100%
48 | WR1L35 | 765kV TAMNAR PS-KOTRA PS I | 47.97 | WRTS-I
48 |  | 765kV TAMNAR PS-KOTRA PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
49 | WR1L36 | 765kV TAMNAR PS-KOTRA PS II | 47.97 | WRTS-I
49 |  | 765kV TAMNAR PS-KOTRA PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
50 | WR1L37 | 765kV KOTRA PS-DURG PS I | 239.84 | WRTS-I
50 |  | 765kV KOTRA PS-DURG PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
51 | WR1L38 | 765kV KOTRA PS-DURG PS II | 239.84 | WRTS-I
51 |  | 765kV KOTRA PS-DURG PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
52 | WR1L39 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 52.56 | WRTS-I
52 |  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
53 | WR1L40 | 400kV BHADRAVATI-DHARIWAL TPP II | 18.14 | WRTS-I |  | 2015-05-25 | 8:18 | 2015-05-25 | 19:48 |  |  |  | 0 | 0.47917 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
53 | WR1L40 | 400kV BHADRAVATI-DHARIWAL TPP II | 18.14 | WRTS-I |  | 2015-05-29 | 8:08 | 2015-05-29 | 20:08 |  |  |  | 0 | 0.5 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
53 |  | 400kV BHADRAVATI-DHARIWAL TPP II Total | [10 empty] | 0 | 0.97917 | 0 | 0 | [5 empty] | 100%
54 | WR1L41 | 400kV DHARIWAL TPP-PARLI II | 391 | WRTS-I |  | 2015-05-04 | 18:42 | 2015-05-04 | 20:10 |  |  |  | 0 | 0.061111 | 0 | 0 |  |  |  | LINE TRIPPED ON B PH TO E FAULT AND DT RECIVED AT PARLI END F.L. R OF 191 KM FROM PARLI. LINE TRIPPED DUE TO FALLING OF OPGW PILOT WIRE DURING ONLINE STRINGING OF OPGW WIRE. THIS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. FOR REPLACEMENT OF GI EARTHWIRE BY OPGW . |  |  | OMSU
54 | WR1L41 | 400kV DHARIWAL TPP-PARLI II | 391 | WRTS-I |  | 2015-05-24 | 10:17 | 2015-05-24 | 17:57 |  |  |  | 0 | 0.31944 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
54 | WR1L41 | 400kV DHARIWAL TPP-PARLI II | 391 | WRTS-I |  | 2015-05-25 | 8:20 | 2015-05-25 | 19:58 |  |  |  | 0 | 0.48472 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
54 | WR1L41 | 400kV DHARIWAL TPP-PARLI II | 391 | WRTS-I |  | 2015-05-29 | 8:12 | 2015-05-29 | 20:25 |  |  |  | 0 | 0.50903 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
54 |  | 400kV DHARIWAL TPP-PARLI II Total | [10 empty] | 0 | 1899-12-31 08:59 | 0 | 0 | [5 empty] | 100%
55 | WR1L42 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 52.56 | WRTS-I
55 |  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
56 | WR1L62 | 400KV RAIPUR-SIPAT II | 149.12 | WRTS-I |  | 2015-05-13 | 09:43 | 2015-05-13 | 22:33 |  |  |  | 0 | 0 | 0 | 0.53472 |  |  |  | LINE H/T FOR NTAMC WORKS AT RAIPUR. |  |  | SCSD
56 |  | 400KV RAIPUR-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0.53472 | [5 empty] | 100%
57 | WR1L63 | 400kV RAIPUR-SIPAT III | 162.04 | WRTS-I
57 |  | 400kV RAIPUR-SIPAT III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
58 | WR1L64 | 765kV BILASPUR-SIPAT I | 21.51 | WRTS-I |  | 2015-05-31 | 20:17 | 2015-05-31 | 24:00 |  |  |  | 0.15486 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON - PHASE TO PHASE FAULT- FAULT CURRENT -10K.A. FL = 30KM FROM BILASPUR END. FAULT IS UNDER CG(O&M) |  |  | LPPT
58 |  | 765kV BILASPUR-SIPAT I Total | [10 empty] | 0.15486 | 0 | 0 | 0 | [5 empty] | 99.5%
59 | WR1L65 | 765kV SEONI-BILASPUR I | 337.05 | WRTS-I
59 |  | 765kV SEONI-BILASPUR I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
60 | WR1L66 | 765kV BILASPUR-SIPAT II | 22.22 | WRTS-I
60 |  | 765kV BILASPUR-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
61 | WR1L67 | 765kV SEONI-BILASPUR II | 338.33 | WRTS-I
61 |  | 765kV SEONI-BILASPUR II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I
62 |  | 765kV SEONI-WARDHA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
63 | WR1L69 | 765kV SEONI-WARDHA II | 260.76 | WRTS-I
63 |  | 765kV SEONI-WARDHA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
64 | WR1L70 | 400kV WARDHA-AKOLA I | 161.87 | WRTS-I
64 |  | 400kV WARDHA-AKOLA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
65 | WR1L71 | 400kV WARDHA-AKOLA II | 161.87 | WRTS-I
65 |  | 400kV WARDHA-AKOLA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
66 | WR1L72 | 400kV AURANGABAD (PG) -AKOLA I | 241.23 | WRTS-I
66 |  | 400kV AURANGABAD (PG) -AKOLA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
67 | WR1L73 | 400kV AURANGABAD (PG) -AKOLA II | 289.97 | WRTS-I
67 |  | 400kV AURANGABAD (PG) -AKOLA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
68 | WR1L74 | 400kV BHADRAVATI-PARLI I | 378.67 | WRTS-I |  | 2015-05-09 | 17:47 | 2015-05-09 | 19:39 |  |  |  | 0 | 0.077778 | 0 | 0 |  |  |  | LINE TRIPPED ON B-PH TO EARTH FAULT F/L=139.05 KM FROM BHADRAWATI. DURING ON LINE OPGW WORK.THIS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. FOR REPLACEMENT OF GI EARTHWIRE BY OPGW.LINE CHARGING ATTEMPTED BUT TRIPPED ON OVERVOLATGE AT BHADRAWATI END HENCE KEPT OUT ON VOLTAGE REGULATION THEN CHARGED FROM PARLI END. |  |  | OMSU
68 | WR1L74 | 400kV BHADRAVATI-PARLI I | 378.67 | WRTS-I |  | 2015-05-11 | 12:24 | 2015-05-11 | 20:17 |  |  |  | 0 | 0.32847 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY & FOR RECTIFICATION WORKS OF BROKEN EARTH WIRE AT LOC NO 411 |  |  | OMSU
68 | WR1L74 | 400kV BHADRAVATI-PARLI I | 378.67 | WRTS-I |  | 2015-05-23 | 9:25 | 2015-05-23 | 17:56 |  |  |  | 0 | 0.35486 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
68 | WR1L74 | 400kV BHADRAVATI-PARLI I | 378.67 | WRTS-I |  | 2015-05-26 | 10:23 | 2015-05-26 | 20:27 |  |  |  | 0 | 0.41944 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY |  |  | OMSU
68 |  | 400kV BHADRAVATI-PARLI I Total | [10 empty] | 0 | 1899-12-31 04:20 | 0 | 0 | [5 empty] | 100%
69 | WR1L76 | 400kV PARLI(PG)-PARLI(MSETCL) I | 4.96 | WRTS-I
69 |  | 400kV PARLI(PG)-PARLI(MSETCL) I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
70 | WR1L77 | 400kV PARLI(PG)-PARLI(MSETCL) II | 4.96 | WRTS-I
70 |  | 400kV PARLI(PG)-PARLI(MSETCL) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
71 | WR1L78 | 400kV KORBA-RAIPUR III | 211.86 | WRTS-I
71 |  | 400kV KORBA-RAIPUR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
72 | WR1L79 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I
72 |  | 400kV KORBA-RAIPUR IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
73 | WR1L80 | 400kV WARDHA-PARLI I | 336.94 | WRTS-I
73 |  | 400kV WARDHA-PARLI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
74 | WR1L81 | 400kV WARDHA-PARLI II | 336.94 | WRTS-I
74 |  | 400kV WARDHA-PARLI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
75 | WR1L82 | 400KV KORBA-BALCO | 7.45 | WRTS-I |  | 2015-05-31 | 20:30 | 2015-05-31 | 21:15 |  |  |  | 0 | 0.03125 | 0 | 0 |  |  |  | LINE TRIPPED. NO INDICATION FOUND IN RELAY. |  |  | OMSU
75 |  | 400KV KORBA-BALCO Total | [10 empty] | 0 | 0.03125 | 0 | 0 | [5 empty] | 100%
76 | WR1L83 | 400kV BALCO-BIRSINGHPUR | 219.19 | WRTS-I |  | 2015-05-17 | 16:01 | 2015-05-17 | 17:17 |  |  |  | 0 | 0.052778 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO A/R UNSUCCESSFUL AT BOTH ENDS ON R PH TO E FAULT,FL- 137 KM FROM BIRSINGHPUR END. |  |  | SEFU
76 |  | 400kV BALCO-BIRSINGHPUR Total | [10 empty] | 0 | 0.052778 | 0 | 0 | [5 empty] | 100%
77 | WR1L84 | 400kV WARDHA-MAUDA II | 123.84 | WRTS-I |  | 2015-05-04 | 22:00 | 2015-05-04 | 23:03 |  |  |  | 0.04375 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON B PH TO E FAULT AT F/L= 12 KM FROM WARDHA. |  |  | LEFT
77 |  | 400kV WARDHA-MAUDA II Total | [10 empty] | 0.04375 | 0 | 0 | 0 | [5 empty] | 99.86%
78 | WR1L85 | 400kV KORBA-VANDANA | 14.77 | WRTS-I
78 |  | 400kV KORBA-VANDANA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
79 | WR1L86 | 400KV VANDANA-BIRSINGHPUR | 211.87 | WRTS-I
79 |  | 400KV VANDANA-BIRSINGHPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
80 | WR1L87 | 400KV RAIPUR-WARDHA I | 370.57 | WRTS-I
80 |  | 400KV RAIPUR-WARDHA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
81 | WR1L88 | 400KV RAIPUR-WARDHA II | 370.57 | WRTS-I |  | 2015-05-15 | 13:49 | 2015-05-15 | 13:49 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LINE A/R FROM BOTH END SUCESSFULLY ON B-PH TO EARTH FAULT. F/L=79.2KM FROM WARDHA. |  |  | LART
81 | WR1L88 | 400KV RAIPUR-WARDHA II | 370.57 | WRTS-I |  | 2015-05-20 | 08:40 | 2015-05-20 | 12:00 |  |  |  | 0 | 0 | 0.13889 | 0 |  |  |  | LINE TRIPPED DUE TO FIRE ON COTTON NEAR TO LINE ON R PHASE TO E FAULT,FC-9.8 KA,FL-22.5 KM FROM WARDHA AND FL-339KM FROM RAIPUR END. |  |  | LMAC
81 |  | 400KV RAIPUR-WARDHA II Total | [10 empty] | 0 | 0 | 0.13889 | 0 | [5 empty] | 100%
82 | WR1L89 | 400KV WARDHA-IEPL | 52.62 | WRTS-I |  | 2015-05-04 | 20:23 | 2015-05-04 | 22:39 |  |  |  | 0 | 0.094444 | 0 | 0 |  |  |  | LINE A/R SUCCESSFUL ON B PH TO E FAULT AT WARDHA BUT A/R FAIL TO OPERATE AT IEPL END. |  |  | SEFU
82 |  | 400KV WARDHA-IEPL Total | [10 empty] | 0 | 0.094444 | 0 | 0 | [5 empty] | 100%
83 | WR1L90 | 400KV IEPL-MAUDA | 70.83 | WRTS-I |  | 2015-05-04 | 22:01 | 2015-05-04 | 22:52 |  |  |  | 0 | 0.035417 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO UNDER VOLTAGE AT MAUDA END |  |  | OMSU
83 |  | 400KV IEPL-MAUDA Total | [10 empty] | 0 | 0.035417 | 0 | 0 | [5 empty] | 100%
84 | WR1L91 | 400kV RAIPUR-DURG I | 21.5 | WRTS-I
84 |  | 400kV RAIPUR-DURG I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
85 | WR1L92 | 400kV RAIPUR-DURG II | 21.5 | WRTS-I
85 |  | 400kV RAIPUR-DURG II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
86 | WR1L93 | 400kV RAIGARH-KOTRA PS I | 6.29 | WRTS-I |  | 2015-05-11 | 9:14 | 2015-05-11 | 18:55 |  |  |  | 0.40347 | 0 | 0 | 0 |  |  |  | H/T FOR LINE AMP WORKS. |  |  | OSPT
86 |  | 400kV RAIGARH-KOTRA PS I Total | [10 empty] | 0.40347 | 0 | 0 | 0 | [5 empty] | 98.7%
87 | WR1L94 | 400kV RAIGARH-KOTRA PS II | 6.29 | WRTS-I |  | 2015-05-18 | 11:20 | 2015-05-18 | 19:00 |  |  |  | 0.31944 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS AT KOTRA |  |  | OSPT
87 |  | 400kV RAIGARH-KOTRA PS II Total | [10 empty] | 0.31944 | 0 | 0 | 0 | [5 empty] | 98.97%
88 | WR1L95 | 765KV DURG PS - D'JAIGARH | 357.62 | WRTS-I |  | 2015-05-16 | 10:10 | 2015-05-22 | 21:28 |  |  |  | 0 | 0 | 0 | 1900-01-05 11:18 |  |  |  | KEPT OUT AS WRLDC INSTRUCTIONS FOR LINE CROSSING WORKS OF 765KV CHAMPA LINE |  |  | LCSD
88 |  | 765KV DURG PS - D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 1900-01-05 11:18 | [5 empty] | 100%
89 | WR1L99 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2015-04-26 | 11:36 | 2015-05-05 | 0:34 |  |  |  | 0 | 0 | 0 | 1900-01-03 00:34 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | LPRD
89 | WR1L99 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2015-05-05 | 10:30 | 2015-05-05 | 10:40 |  |  |  | 0 | 0 | 0.0069444 | 0 |  |  |  | LINE TRIPPED ON OVER VOLTAGE AT AURANGABAD |  |  | GOVC
89 | WR1L99 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2015-05-05 | 10:40 | 2015-05-21 | 15:10 |  |  |  | 0 | 0 | 0 | 1900-01-15 04:30 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
89 |  | 765kV WARDHA - AURANGABAD(PG) I Total | [10 empty] | 0 | 0 | 0.0069444 | 1900-01-19 05:04 | [5 empty] | 100%
90 | WR1L100 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2015-05-06 | 18:45 | 2015-05-06 | 19:18 |  |  |  | 0.022917 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON B-PH TO E FAULT. F/L= 67KM FROM WARDHA & 248KM FROM A'BAD |  |  | LEFT
90 | WR1L100 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2015-05-22 | 16:44 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-08 07:16 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
90 |  | 765kV WARDHA - AURANGABAD(PG) II Total | [10 empty] | 0.022917 | 0 | 0 | 1900-01-08 07:16 | [5 empty] | 99.93%
91 | WR1L104 | 400KV KORBA-SIPAT | 68.653 | WRTS-I |  | 2015-05-31 | 20:17 | 2015-05-31 | 21:44 |  |  |  | 0 | 0.060417 | 0 | 0 |  |  |  | LINE TRIPPED. NO INDICATION FOUND IN RELAY. |  |  | OMSU
91 |  | 400KV KORBA-SIPAT Total | [10 empty] | 0 | 0.060417 | 0 | 0 | [5 empty] | 100%
92 | WR1L108 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2015-05-30 | 11:25 | 2015-05-30 | 19:43 |  |  |  | 0 | 0 | 0 | 0.34583 |  |  |  | OUTAGE AVAILED FOR NTAMC WORKS. |  |  | SCSD
92 | WR1L108 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2015-05-31 | 9:16 | 2015-05-31 | 21:18 |  |  |  | 0 | 0 | 0 | 0.50139 |  |  |  | OUTAGE AVAILED FOR NTMC WORK |  |  | SCSD
92 |  | 765kV DURG PS -WARDHA_1 Total | [10 empty] | 0 | 0 | 0 | 0.84722 | [5 empty] | 100%
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-21 | 18:05 | 2015-05-21 | 18:15 |  |  |  | 0 | 0 | 0.0069444 | 0 |  |  |  | LINE TRIPPED DUE TO OVER VOLTAGE AT DURG PS END |  |  | GOVC
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-21 | 18:15 | 2015-05-22 | 16:23 |  |  |  | 0 | 0 | 0 | 0.92222 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-22 | 18:03 | 2015-05-22 | 18:13 |  |  |  | 0 | 0 | 0.0069444 | 0 |  |  |  | LINE TRIPPED DUE TO OVER VOLTAGE AT DURG PS END |  |  | GOVC
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-22 | 18:13 | 2015-05-26 | 1:58 |  |  |  | 0 | 0 | 0 | 1900-01-02 07:45 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-27 | 17:03 | 2015-05-27 | 17:13 |  |  |  | 0.0069444 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON R PH TO E FAULT,FC- 7.6 KA,FL- 53.3 KM FROM WARDHA END. |  |  | LEFT
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-27 | 17:13 | 2015-05-28 | 15:08 |  |  |  | 0 | 0 | 0 | 0.91319 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-30 | 13:13 | 2015-05-30 | 20:16 |  |  |  | 0 | 0 | 0 | 0.29375 |  |  |  | OUTAGE AVAILED FOR NTAMC WORKS. |  |  | SCSD
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-05-31 | 9:27 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 0.60625 |  |  |  | OUTAGE AVAILED FOR NTMC WORK |  |  | SCSD
93 |  | 765kV DURG PS -WARDHA_2 Total | [10 empty] | 0.0069444 | 0 | 0.013889 | 1900-01-05 01:24 | [5 empty] | 99.98%
94 | WR1L112 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2015-05-28 | 16:00 | 2015-05-28 | 16:10 |  |  |  | 0.0069444 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON R-PH TO EARTH FAULTF/L- 42 KM FROM SOLAPUR END 234 KM FROM PUNE END. |  |  | LEFT
94 | WR1L112 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2015-05-28 | 16:10 | 2015-05-29 | 8:01 |  |  |  | 0 | 0 | 0 | 0.66042 |  |  |  | LLINE KEPT OUT AFTER OUTAGE AS PER WRLDC INSTRUCTION OF WRLDC. THERE IS NO PERMANENT FAULT IN LINE AS LINE WAS SUCCESSFULLY CHARGED IN EARLY MORNING ON 29/05/15. |  |  | LVRD
94 |  | 765kV PUNE(GIS)-SOLAPUR Total | [10 empty] | 0.0069444 | 0 | 0 | 0.66042 | [5 empty] | 99.98%
95 | WR1L113 | 400Kv PARLI-PUNE(GIS)_1 | 272.202 | WRTS-I
95 |  | 400Kv PARLI-PUNE(GIS)_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
96 | WR1L114 | 400Kv PARLI-PUNE(GIS)_2 | 272.202 | WRTS-I
96 |  | 400Kv PARLI-PUNE(GIS)_2 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
97 | WR1L115 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 65 | WRTS-I |  | 2015-05-28 | 15:49 | 2015-05-28 | 19:26 |  |  |  | 0.15069 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR TIGHTINING OF JUMPERS IN LINE |  |  | OMST
97 |  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 Total | [10 empty] | 0.15069 | 0 | 0 | 0 | [5 empty] | 99.51%
98 | WR1L116 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 65 | WRTS-I |  | 2015-05-31 | 13:55 | 2015-05-31 | 17:35 |  |  |  | 0.15278 | 0 | 0 | 0 |  |  |  | LINE H/T FOR RECTIFICATION OF MELTED JUMPER OF BOTTEM PHASE. |  |  | OMST
98 |  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 Total | [10 empty] | 0.15278 | 0 | 0 | 0 | [5 empty] | 99.51%
99 | WR1L117 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2015-04-23 | 21:41 | 2015-05-02 | 10:33 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:33 |  |  |  | LINE KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
99 | WR1L117 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2015-05-03 | 17:24 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-27 06:36 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
99 |  | 765kV WARDHA - AURANGABAD(PG) III Total | [10 empty] | 0 | 0 | 0 | 1900-01-28 17:09 | [5 empty] | 100%
100 | WR1L118 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I
100 |  | 765kV WARDHA - AURANGABAD(PG) IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
101 | WR1L119 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | 11.2 | WRTS-I
101 |  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
102 | WR1L120 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | 11.2 | WRTS-I
102 |  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
103 | WR1L121 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I |  |  |  | 2015-05-29 | 21:14 | [10 empty] | LINE FIRST TIME CHARGED.
103 | WR1L121 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I |  | 2015-05-31 | 18:08 | 2015-05-31 | 18:18 |  |  |  | 0 | 0 | 0.0069444 | 0 |  |  |  | LINE TRIPPED DUE TO OVER VOLTAGE |  |  | GOVC
103 | WR1L121 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I |  | 2015-05-31 | 18:08 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 0.24444 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
103 |  | 765kV DURG PS- CHAMPA_1 Total | [10 empty] | 0 | 0 | 0.0069444 | 0.24444 | [5 empty] | 100%
104 | WR1L122 | 765kV CHAMPA- KOTRA PS | 96.33 | WRTS-I |  |  |  | 2015-05-29 | 20:38 | [10 empty] | LINE FIRST TIME CHARGED
104 |  | 765kV CHAMPA- KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
105 | WR1T1 | ICT1_400/220kv_RAIPUR | 315 | WRTS-I
105 |  | ICT1_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
106 | WR1T2 | ICT2_400/220kv_RAIPUR | 315 | WRTS-I |  | 2015-05-06 | 11:10 | 2015-05-06 | 18:19 |  |  |  | 0 | 0 | 0 | 0.29792 |  |  |  | H/T FOR NTAMC WORKS AT RAIPUR. |  |  | SCSD
106 |  | ICT2_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0.29792 | [5 empty] | 100%
107 | WR1T3 | ICT1_400/220kv_MAPUSA | 315 | WRTS-I |  | 2015-05-16 | 16:01 | 2015-05-16 | 22:57 |  |  |  | 0 | 0 | 0.28889 | 0 |  |  |  | TRIPPED DUE TO R PAHSE ISOLATOR DAMAGED ON 400 KV SIDE DUE TO HEAVY WIND & RAIN NATURAL CALAMITY. |  |  | LNCC
107 |  | ICT1_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0.28889 | 0 | [5 empty] | 100%
108 | WR1T4 | ICT2_400/220kv_MAPUSA | 315 | WRTS-I
108 |  | ICT2_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
109 | WR1T5 | ICT1_400/220kv_BAHATAPARA | 315 | WRTS-I |  | 2015-05-25 | 10:40 | 2015-05-25 | 18:21 |  |  |  | 0.32014 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS |  |  | OSPT
109 |  | ICT1_400/220kv_BAHATAPARA Total | [10 empty] | 0.32014 | 0 | 0 | 0 | [5 empty] | 98.97%
110 | WR1T6 | ICT1_400/220kv_RAIGARH | 315 | WRTS-I
110 |  | ICT1_400/220kv_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
111 | WR1T7 | ICT2_400/220kv_RAIGARH | 315 | WRTS-I
111 |  | ICT2_400/220kv_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
112 | WR1T8 | ICT1_765/400kv_SEONI | 1500 | WRTS-I
112 |  | ICT1_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
113 | WR1T9 | ICT2_765/400kv_SEONI | 1500 | WRTS-I
113 |  | ICT2_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
114 | WR1T10 | ICT3_765/400kv_SEONI | 1500 | WRTS-I
114 |  | ICT3_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
115 | WR1T11 | ICT1_400/220kv_SEONI | 315 | WRTS-I | ICT | 2015-04-30 | 21:20 | 2015-05-28 | 22:16 |  |  | 27.9278 | 1900-01-26 22:16 | 0 | 0 | 0 | 120 | N | -92.0722 | ICT TRIPPED DUE TO FAILURE OF HV SIDE B PHASE BUSHING. |  |  | SEFT
115 |  | ICT1_400/220kv_SEONI Total | [10 empty] | 1900-01-26 22:16 | 0 | 0 | 0 | [5 empty] | 100%
116 | WR1T12 | ICT1_765/400kv_WARDHA | 1500 | WRTS-I
116 |  | ICT1_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
117 | WR1T13 | ICT2_765/400kv_WARDHA | 1500 | WRTS-I
117 |  | ICT2_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
118 | WR1T14 | ICT3_765/400kv_WARDHA | 1500 | WRTS-I
118 |  | ICT3_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
119 | WR1T15 | ICT1_765/400kv_BILASPUR | 1500 | WRTS-I
119 |  | ICT1_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
120 | WR1T16 | ICT2_765/400kv_BILASPUR | 1500 | WRTS-I
120 |  | ICT2_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
121 | WR1T17 | ICT2_400/220kv_BAHATAPARA | 315 | WRTS-I |  | 2015-05-22 | 10:03 | 2015-05-22 | 18:45 |  |  |  | 0 | 0 | 0 | 0.3625 |  |  |  | H/T FOR NTAMC WORKS |  |  | SCSD
121 |  | ICT2_400/220kv_BAHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0.3625 | [5 empty] | 100%
122 | WR1T18 | ICT2_400/220kv_SEONI | 315 | WRTS-I
122 |  | ICT2_400/220kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
123 | WR1T19 | ICT3_400/220kv_RAIPUR | 315 | WRTS-I |  | 2015-05-08 | 9:03 | 2015-05-08 | 20:22 |  |  |  | 0 | 0 | 0 | 0.47153 |  |  |  | H/T FOR NTAMC WORKS AT RAIPUR. |  |  | SCSD
123 |  | ICT3_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0.47153 | [5 empty] | 100%
124 | WR1T20 | ICT1_400/220kv_WARDHA | 315 | WRTS-I
124 |  | ICT1_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
125 | WR1T21 | ICT2_400/220kv_WARDHA | 315 | WRTS-I |  | 2015-05-04 | 20:45 | 2015-05-04 | 21:25 |  |  |  | 0 | 0.027778 | 0 | 0 |  |  |  | OUTAGE AVAILED BY MSETCL FOR ISOLATION OF 400 KV WARDHA - WARORA # 2 MAIN BAY FOR ATTENDING OIL PRESSURE L/O ALONG WITH 400 KV BUS # 2, CONNECTED WITH 400 KV ICT # 2 AT WARDHA. |  |  | OMSU
125 |  | ICT2_400/220kv_WARDHA Total | [10 empty] | 0 | 0.027778 | 0 | 0 | [5 empty] | 100%
126 | WR1T22 | ICT3_400/220kv_WARDHA | 500 | WRTS-I
126 |  | ICT3_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
127 | WR1T23 | ICT1_400/220kv_SOLAPUR | 315 | WRTS-I
127 |  | ICT1_400/220kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
128 | WR1T24 | ICT2_400/220kv_SOLAPUR | 315 | WRTS-I
128 |  | ICT2_400/220kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
129 | WR1T25 | ICT1_400/220kv_PUNE | 315 | WRTS-I |  | 2015-05-14 | 0:19 | 2015-05-14 | 21:55 |  |  |  | 0 | 0 | 0 | 0.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
129 | WR1T25 | ICT1_400/220kv_PUNE | 315 | WRTS-I |  | 2015-05-15 | 0:19 | 2015-05-18 | 10:57 |  |  |  | 0 | 0 | 0 | 1900-01-02 10:38 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
129 |  | ICT1_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 1900-01-03 08:14 | [5 empty] | 100%
130 | WR1T26 | ICT2_400/220kv_PUNE | 315 | WRTS-I |  | 2015-05-14 | 16:50 | 2015-05-14 | 21:55 |  |  |  | 0 | 0 | 0 | 0.21181 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
130 | WR1T26 | ICT2_400/220kv_PUNE | 315 | WRTS-I |  | 2015-05-18 | 10:58 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-12 13:02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
130 |  | ICT2_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 1900-01-12 18:07 | [5 empty] | 100%
131 | WR1T27 | ICT3_400/220kv_PUNE | 315 | WRTS-I |  | 2015-03-05 | 14:56 | 2015-05-14 | 16:49 |  |  |  | 0 | 0 | 0 | 415:11 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
131 |  | ICT3_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
132 | WR1T28 | ICT3_765/400kv_BILASPUR | 1500 | WRTS-I
132 |  | ICT3_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
133 | WR1T29 | ICT1_765/400kv_KOTRA PS | 1500 | WRTS-I
133 |  | ICT1_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
134 | WR1T30 | ICT2_765/400kv_KOTRA PS | 1500 | WRTS-I |  | 2015-05-25 | 10:20 | 2015-05-25 | 19:48 |  |  |  | 0.39444 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS |  |  | OSPT
134 |  | ICT2_765/400kv_KOTRA PS Total | [10 empty] | 0.39444 | 0 | 0 | 0 | [5 empty] | 98.73%
135 | WR1T31 | ICT4_765/400kv_KOTRA PS | 1500 | WRTS-I
135 |  | ICT4_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
136 | WR1T32 | ICT3_400/220kv_MAPUSA | 315 | WRTS-I
136 |  | ICT3_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
137 | WR1T33 | ICT1_765/400kv_TAMNAR PS | 1500 | WRTS-I
137 |  | ICT1_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
138 | WR1T34 | ICT2_765/400kv_TAMNAR PS | 1500 | WRTS-I
138 |  | ICT2_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
139 | WR1T35 | ICT1_765/400kv_DURG PS | 1500 | WRTS-I
139 |  | ICT1_765/400kv_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
140 | WR1T36 | ICT1_765/400kv_SOLAPUR | 1500 | WRTS-I
140 |  | ICT1_765/400kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
141 | WR1T37 | ICT2_765/400kv_SOLAPUR | 1500 | WRTS-I
141 |  | ICT2_765/400kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
142 | WR1T38 | ICT1_400/200kv_AURANGABAD | 315 | WRTS-I
142 |  | ICT1_400/200kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
143 | WR1T39 | ICT2_400/200kv_AURANGABAD | 315 | WRTS-I
143 |  | ICT2_400/200kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
144 | WR1T40 | ICT2_765/400kv_AURANGABAD | 1500 | WRTS-I |  | 2015-05-13 | 17:10 | 2015-05-13 | 17:45 |  |  |  | 0.024306 | 0 | 0 | 0 |  |  |  | ICT TRIPPED DUE TO B PHASE BUCHHOLZ RELAY OPERATION |  |  | SICT
144 | WR1T40 | ICT2_765/400kv_AURANGABAD | 1500 | WRTS-I |  | 2015-05-17 | 17:33 | 2015-05-17 | 18:12 |  |  |  | 0.52708 | 0 | 0 | 0 |  |  |  | ICT TRIPPED ON B PHASE BUCHHOLZ RELAY MALOPERATION. |  |  | SRMT
144 |  | ICT2_765/400kv_AURANGABAD Total | [10 empty] | 0.55139 | 0 | 0 | 0 | [5 empty] | 98.22%
145 | WR1T41 | ICT3_765/400kv_TAMNAR PS | 1500 | WRTS-I
145 |  | ICT3_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
146 | WR1T42 | ICT3_765/400kv_KOTRA PS | 1500 | WRTS-I
146 |  | ICT3_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
147 | WR1T43 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I |  | 2015-05-13 | 10:05 | 2015-05-13 | 18:32 |  |  |  | 0.35208 | 0 | 0 | 0 |  |  |  | ICT TRIPPED DUE TO R PHASE BUCHHOLZ RELAY OPERATION. |  |  | SICT
147 | WR1T43 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I |  | 2015-05-13 | 18:32 | 2015-05-13 | 20:58 |  |  |  | 0.10139 | 0 | 0 | 0 |  |  |  | H/T DUE TO HEAVY SPARKING ON SPARE ISOLATOR. |  |  | OSFT
147 | WR1T43 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I |  | 2015-05-17 | 13:42 | 2015-05-17 | 17:34 |  |  |  | 0.16111 | 0 | 0 | 0 |  |  |  | H/T FOR REPLACING ISOLATOR ARMS OF SPARE UNIT. |  |  | OMST
147 |  | ICT1_765/400kv_AURANGABAD Total | [10 empty] | 0.61458 | 0 | 0 | 0 | [5 empty] | 98.02%
148 | WR1T44 | ICT2_765/400kv_D'JAIGARH | 1500 | WRTS-I
148 |  | ICT2_765/400kv_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
149 | WR1T45 | ICT1_765/400kv_D'JAIGARH | 1500 | WRTS-I
149 |  | ICT1_765/400kv_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
150 | WR1T46 | ICT1_400/200kv_BHADRAWATI | 315 | WRTS-I
150 |  | ICT1_400/200kv_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
151 | WR1T47 | ICT1_765/400kv_PUNE(GIS) | 1500 | WRTS-I |  | 2015-04-26 | 9:37 | 2015-05-01 | 12:44 |  |  |  | 0 | 0 | 0 | 0.53056 |  |  |  | H/T FOR SWITCHING IMPULSE TESTING. |  |  | SCSD
151 |  | ICT1_765/400kv_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 0.53056 | [5 empty] | 100%
152 | WR1T48 | ICT2_765/400kv_PUNE(GIS) | 1500 | WRTS-I
152 |  | ICT2_765/400kv_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
153 | WR1R1 | BUS REACTOR_400kV_63MVAR_RAIGARH | 63 | WRTS-I
153 |  | BUS REACTOR_400kV_63MVAR_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
154 | WR1R2 | BUS REACTOR_765kV_240MVAR_SEONI | 240 | WRTS-I
154 |  | BUS REACTOR_765kV_240MVAR_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
155 | WR1R3 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 50 | WRTS-I
155 |  | SWITCHABLE LR_400kV_KORBA 3_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
156 | WR1R4 | BUS REACTOR_400kV_50MVAR_WARDHA | 50 | WRTS-I
156 |  | BUS REACTOR_400kV_50MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-02 | 08:46 | 2015-05-02 | 16:14 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-04 | 7:29 | 2015-05-04 | 18:01 |  |  |  | 0 | 0 | 0 | 0.43889 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-05 | 9:53 | 2015-05-05 | 12:12 |  |  |  | 0 | 0 | 0 | 0.096528 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-08 | 6:57 | 2015-05-08 | 16:24 |  |  |  | 0 | 0 | 0 | 0.39375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-09 | 11:58 | 2015-05-09 | 16:58 |  |  |  | 0 | 0 | 0 | 0.20833 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-13 | 09:31 | 2015-05-13 | 16:39 |  |  |  | 0 | 0 | 0 | 0.29722 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-18 | 9:40 | 2015-05-18 | 16:39 |  |  |  | 0 | 0 | 0 | 0.29097 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-19 | 8:23 | 2015-05-19 | 17:18 |  |  |  | 0 | 0 | 0 | 0.37153 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-20 | 10:19 | 2015-05-20 | 16:46 |  |  |  | 0 | 0 | 0 | 0.26875 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-21 | 7:21 | 2015-05-21 | 16:20 |  |  |  | 0 | 0 | 0 | 0.37431 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-23 | 9:39 | 2015-05-23 | 16:57 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-25 | 9:37 | 2015-05-25 | 18:11 |  |  |  | 0 | 0 | 0 | 0.35694 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-25 | 14:35 | 2015-05-25 | 18:44 |  |  |  | 0 | 0 | 0 | 0.17292 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-26 | 10:35 | 2015-05-26 | 17:20 |  |  |  | 0 | 0 | 0 | 0.28125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-27 | 09:52 | 2015-05-27 | 18:43 |  |  |  | 0 | 0 | 0 | 0.36875 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-05-28 | 8:02 | 2015-05-29 | 18:20 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:18 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
157 |  | BUS REACTOR_400kV_63MVAR_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 1900-01-04 23:09 | [5 empty] | 100%
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-04 | 7:32 | 2015-05-04 | 18:10 |  |  |  | 0 | 0 | 0 | 0.44306 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-05 | 7:22 | 2015-05-08 | 16:36 |  |  |  | 0 | 0 | 0 | 1900-01-02 09:14 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-11 | 10:21 | 2015-05-11 | 20:51 |  |  |  | 0 | 0 | 0 | 0.4375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-13 | 07:05 | 2015-05-13 | 17:20 |  |  |  | 0 | 0 | 0 | 0.42708 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-16 | 10:04 | 2015-05-16 | 16:48 |  |  |  | 0 | 0 | 0 | 0.28056 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-18 | 11:48 | 2015-05-18 | 16:27 |  |  |  | 0 | 0 | 0 | 0.19375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-19 | 8:25 | 2015-05-19 | 17:00 |  |  |  | 0 | 0 | 0 | 0.35764 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-20 | 10:20 | 2015-05-20 | 16:20 |  |  |  | 0 | 0 | 0 | 0.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-21 | 06:24 | 2015-05-21 | 16:26 |  |  |  | 0 | 0 | 0 | 0.41806 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-22 | 9:04 | 2015-05-22 | 16:53 |  |  |  | 0 | 0 | 0 | 0.32569 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-23 | 9:57 | 2015-05-23 | 17:19 |  |  |  | 0 | 0 | 0 | 0.30694 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-26 | 10:33 | 2015-05-27 | 18:47 |  |  |  | 0 | 0 | 0 | 1899-12-31 08:14 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-05-28 | 06:37 | 2015-05-28 | 21:10 |  |  |  | 0 | 0 | 0 | 0.60625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 |  | BUS REACTOR_400kV_63MVAR_PARLI Total | [10 empty] | 0 | 0 | 0 | 1900-01-07 18:35 | [5 empty] | 100%
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-04-29 | 11:49 | 2015-05-01 | 16:32 |  |  |  | 0 | 0 | 0 | 0.68889 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-05-05 | 10:04 | 2015-05-09 | 18:32 |  |  |  | 0 | 0 | 0 | 1900-01-03 08:28 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-05-09 | 23:17 | 2015-05-09 | 23:34 |  |  |  | 0.011806 | 0 | 0 | 0 |  |  |  | B/R TRIPPED DUE TO BUCCHOLZ RELAY OPERATION. |  |  | SRET
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-05-09 | 23:34 | 2015-05-10 | 18:30 |  |  |  | 0 | 0 | 0 | 0.78889 |  |  |  | REACTOR WAS READY FOR CHARGING FOR KEPT OUT ON VOLATGE REGULATION DUE TO RAIN. |  |  | SVRD
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-05-13 | 11:12 | 2015-05-16 | 16:50 |  |  |  | 0 | 0 | 0 | 1900-01-02 05:38 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-05-18 | 11:23 | 2015-05-18 | 17:43 |  |  |  | 0 | 0 | 0 | 0.26389 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-05-19 | 11:31 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-11 12:29 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 |  | BUS REACTOR_400kV_50MVAR_PUNE Total | [10 empty] | 0.011806 | 0 | 0 | 1900-01-20 20:23 | [5 empty] | 99.96%
160 | WR1R8 | BUS REACTOR_765kV_240MVAR_WARDHA | 240 | WRTS-I
160 |  | BUS REACTOR_765kV_240MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
161 | WR1R9 | BUS REACTOR_765kV_240MVAR_BILASPUR | 240 | WRTS-I |  | 2015-05-21 | 10:14 | 2015-05-23 | 19:12 |  |  |  | 0 | 0 | 0 | 1900-01-01 08:58 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
161 |  | BUS REACTOR_765kV_240MVAR_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 1900-01-01 08:58 | [5 empty] | 100%
162 | WR1R10 | SWITCHABLE LR_765kV_BINA_SEONI | 240 | WRTS-I
162 |  | SWITCHABLE LR_765kV_BINA_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
163 | WR1R11 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 240 | WRTS-I
163 |  | SWITCHABLE LR_765kV_SEONI 1_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
164 | WR1R12 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 240 | WRTS-I
164 |  | SWITCHABLE LR_765kV_SEONI 2_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
165 | WR1R13 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 240 | WRTS-I
165 |  | SWITCHABLE LR_765kV_D'GARH_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
166 | WR1R14 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 240 | WRTS-I
166 |  | BUS REACTOR_765kV_240MVAR_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
167 | WR1R15 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 80 | WRTS-I
167 |  | BUS REACTOR_400kV_80MVAR_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
168 | WR1R16 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 240 | WRTS-I
168 |  | SWITCHABLE LR_765kV_DURG 1_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
169 | WR1R17 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 50 | WRTS-I
169 |  | BUS REACTOR_400kV_50MVAR_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
170 | WR1R18 | BUS REACTOR_400kV_80MVAR_RAIPUR | 80 | WRTS-I |  | 2015-05-11 | 9:35 | 2015-05-11 | 18:17 |  |  |  | 0 | 0 | 0 | 0.3625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
170 |  | BUS REACTOR_400kV_80MVAR_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0.3625 | [5 empty] | 100%
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-02 | 09:04 | 2015-05-02 | 16:07 |  |  |  | 0 | 0 | 0 | 0.29375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-04 | 9:41 | 2015-05-04 | 16:12 |  |  |  | 0 | 0 | 0 | 0.27153 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-05 | 9:41 | 2015-05-05 | 12:16 |  |  |  | 0 | 0 | 0 | 0.10764 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-07 | 10:18 | 2015-05-07 | 17:07 |  |  |  | 0 | 0 | 0 | 0.28403 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-12 | 15:25 | 2015-05-12 | 18:07 |  |  |  | 0 | 0 | 0 | 0.1125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-13 | 11:01 | 2015-05-13 | 16:38 |  |  |  | 0 | 0 | 0 | 0.23403 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-17 | 9:42 | 2015-05-17 | 16:02 |  |  |  | 0 | 0 | 0 | 0.26389 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-20 | 09:31 | 2015-05-20 | 16:17 |  |  |  | 0 | 0 | 0 | 0.28194 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-21 | 8:57 | 2015-05-21 | 16:08 |  |  |  | 0 | 0 | 0 | 0.29931 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-22 | 9:50 | 2015-05-22 | 16:51 |  |  |  | 0 | 0 | 0 | 0.29236 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-27 | 09:51 | 2015-05-27 | 17:57 |  |  |  | 0 | 0 | 0 | 0.3375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-05-28 | 8:57 | 2015-05-28 | 17:21 |  |  |  | 0 | 0 | 0 | 0.35 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
171 |  | BUS REACTOR_400kV_50MVAR_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 1900-01-02 03:05 | [5 empty] | 100%
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-02 | 09:08 | 2015-05-02 | 16:11 |  |  |  | 0 | 0 | 0 | 0.29375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-04 | 9:39 | 2015-05-04 | 16:15 |  |  |  | 0 | 0 | 0 | 0.275 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-05 | 9:41 | 2015-05-05 | 12:20 |  |  |  | 0 | 0 | 0 | 0.11042 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-06 | 10:28 | 2015-05-06 | 17:15 |  |  |  | 0 | 0 | 0 | 0.28264 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-07 | 8:57 | 2015-05-08 | 16:36 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:39 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-11 | 9:53 | 2015-05-11 | 16:38 |  |  |  | 0 | 0 | 0 | 0.28125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-13 | 11:00 | 2015-05-13 | 17:06 |  |  |  | 0 | 0 | 0 | 0.25417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-15 | 10:03 | 2015-05-15 | 16:15 |  |  |  | 0 | 0 | 0 | 0.25833 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-18 | 9:36 | 2015-05-18 | 16:41 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-19 | 9:32 | 2015-05-19 | 13:10 |  |  |  | 0 | 0 | 0 | 0.15139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-20 | 08:53 | 2015-05-20 | 16:17 |  |  |  | 0 | 0 | 0 | 0.30833 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-21 | 9:20 | 2015-05-21 | 16:05 |  |  |  | 0 | 0 | 0 | 0.28125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-22 | 9:46 | 2015-05-22 | 16:34 |  |  |  | 0 | 0 | 0 | 0.28333 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-23 | 9:24 | 2015-05-23 | 16:30 |  |  |  | 0 | 0 | 0 | 0.29583 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-25 | 9:58 | 2015-05-25 | 16:15 |  |  |  | 0 | 0 | 0 | 0.26181 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-26 | 09:35 | 2015-05-26 | 17:08 |  |  |  | 0 | 0 | 0 | 0.31458 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR CSD COMMISSIONING WORKS. |  |  | SCSD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-27 | 08:51 | 2015-05-27 | 17:56 |  |  |  | 0 | 0 | 0 | 0.37847 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-28 | 8:35 | 2015-05-28 | 16:12 |  |  |  | 0 | 0 | 0 | 0.31736 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-05-29 | 8:48 | 2015-05-29 | 16:06 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 |  | BUS REACTOR_400kV_80MVAR_KOLHAPUR Total | [10 empty] | 0 | 0 | 0 | 1900-01-05 06:23 | [5 empty] | 100%
173 | WR1R21 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 240 | WRTS-I
173 |  | SWITCHABLE LR_765kV_DURG 2_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
174 | WR1R22 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 240 | WRTS-I
174 |  | BUS REACTOR_765kV_240MVAR_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
175 | WR1R23 | BUS REACTOR_765kV_240MVAR_DURG PS | 240 | WRTS-I
175 |  | BUS REACTOR_765kV_240MVAR_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-02 | 10:32 | 2015-05-02 | 15:14 |  |  |  | 0 | 0 | 0 | 0.19583 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-05 | 9:50 | 2015-05-05 | 13:09 |  |  |  | 0 | 0 | 0 | 0.13819 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-20 | 09:31 | 2015-05-20 | 15:27 |  |  |  | 0 | 0 | 0 | 0.24722 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-21 | 9:50 | 2015-05-21 | 16:13 |  |  |  | 0 | 0 | 0 | 0.26597 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-22 | 12:04 | 2015-05-22 | 13:33 |  |  |  | 0 | 0 | 0 | 0.061806 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-25 | 14:33 | 2015-05-25 | 16:44 |  |  |  | 0 | 0 | 0 | 0.090972 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-27 | 10:32 | 2015-05-27 | 16:59 |  |  |  | 0 | 0 | 0 | 0.26875 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-05-28 | 8:56 | 2015-05-28 | 16:23 |  |  |  | 0 | 0 | 0 | 0.31042 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
176 |  | BUS REACTOR_765kV_240MVAR_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 13:54 | [5 empty] | 100%
177 | WR1R25 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | 240 | WRTS-I |  | 2015-05-15 | 10:19 | 2015-05-15 | 17:06 |  |  |  | 0 | 0 | 0 | 0.28264 |  |  |  | FOR CSD COMMISSIONING WORKS |  |  | SCSD
177 | WR1R25 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | 240 | WRTS-I |  | 2015-05-24 | 20:48 | 2015-05-24 | 21:10 |  |  |  | 0.015278 | 0 | 0 | 0 |  |  |  | REACTOR TRIPPED ON DIFFERENTIAL PROTECTION OPERATION AT SOLAPUR END |  |  | SRET
177 |  | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR Total | [10 empty] | 0.015278 | 0 | 0 | 0.28264 | [5 empty] | 99.95%
178 | WR1R26 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | 240 | WRTS-I |  | 2015-05-07 | 10:06 | 2015-05-08 | 17:43 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:37 |  |  |  | H/T FOR CSD COMMISSIONING WORKS AT SOLAPUR. |  |  | SCSD
178 |  | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 07:37 | [5 empty] | 100%
179 | WR1R27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I |  | 2015-04-27 | 22:02 | 2015-05-05 | 0:34 |  |  |  | 0 | 0 | 0 | 1900-01-03 00:34 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
179 | WR1R27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I |  | 2015-05-04 | 23:51 | 2015-05-09 | 18:50 |  |  |  | 0 | 0 | 0 | 1900-01-03 18:59 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
179 | WR1R27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I |  | 2015-05-21 | 14:44 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-09 09:16 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
179 |  | SWITCHABLE LR_765kV_A'BAD 1_WARDHA Total | [10 empty] | 0 | 0 | 0 | 1900-01-18 04:49 | [5 empty] | 100%
180 | WR1R28 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 330 | WRTS-I
180 |  | SWITCHABLE LR_765kV_A'BAD 2_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
181 | WR1R29 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 240 | WRTS-I |  | 2015-05-13 | 09:37 | 2015-05-13 | 17:20 |  |  |  | 0 | 0 | 0 | 0.32153 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
181 |  | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0.32153 | [5 empty] | 100%
182 | WR1R30 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 240 | WRTS-I
182 |  | SWITCHABLE LR_765kV_WARDHA 2_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
183 | WR1R31 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I |  | 2015-05-16 | 10:26 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-14 13:34 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
183 |  | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 1900-01-14 13:34 | [5 empty] | 100%
184 | WR1R32 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I
184 |  | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-04-30 | 08:32 | 2015-05-01 | 17:14 |  |  |  | 0 | 0 | 0 | 0.71806 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-03 | 21:09 | 2015-05-04 | 18:03 |  |  |  | 0 | 0 | 0 | 0.87083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-04 | 21:23 | 2015-05-06 | 17:24 |  |  |  | 0 | 0 | 0 | 1899-12-31 20:01 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-07 | 8:19 | 2015-05-07 | 17:48 |  |  |  | 0 | 0 | 0 | 0.39514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-09 | 12:03 | 2015-05-09 | 16:28 |  |  |  | 0 | 0 | 0 | 0.18403 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-10 | 9:02 | 2015-05-10 | 17:56 |  |  |  | 0 | 0 | 0 | 0.37083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-11 | 10:18 | 2015-05-11 | 16:36 |  |  |  | 0 | 0 | 0 | 0.2625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-12 | 09:21 | 2015-05-12 | 13:15 |  |  |  | 0 | 0 | 0 | 0.1625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-13 | 06:24 | 2015-05-15 | 17:36 |  |  |  | 0 | 0 | 0 | 1900-01-01 11:12 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-16 | 9:40 | 2015-05-16 | 16:53 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-18 | 6:28 | 2015-05-18 | 17:09 |  |  |  | 0 | 0 | 0 | 0.44514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-19 | 8:18 | 2015-05-19 | 15:38 |  |  |  | 0 | 0 | 0 | 0.30556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-19 | 22:06 | 2015-05-20 | 16:51 |  |  |  | 0 | 0 | 0 | 0.78125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-21 | 06:24 | 2015-05-21 | 16:13 |  |  |  | 0 | 0 | 0 | 0.40903 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-23 | 9:56 | 2015-05-23 | 18:13 |  |  |  | 0 | 0 | 0 | 0.34514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-26 | 09:05 | 2015-05-26 | 19:16 |  |  |  | 0 | 0 | 0 | 0.42431 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-28 | 06:27 | 2015-05-28 | 16:49 |  |  |  | 0 | 0 | 0 | 0.43194 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-05-31 | 9:40 | 2015-05-31 | 16:44 |  |  |  | 0 | 0 | 0 | 0.29444 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
185 |  | BUS REACTOR_765kV_240MVAR_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1900-01-10 00:03 | [5 empty] | 100%
186 | WR1R34 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I |  | 2015-05-04 | 9:43 | 2015-05-04 | 18:04 |  |  |  | 0 | 0 | 0 | 0.34792 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R34 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I |  | 2015-05-06 | 14:58 | 2015-05-07 | 13:35 |  |  |  | 0.94236 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR AMP & TAN DELTA MEASUREMENT. |  |  | OSPT
186 | WR1R34 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I |  | 2015-05-19 | 15:50 | 2015-05-25 | 22:11 |  |  |  | 0 | 0 | 0 | 1900-01-05 06:21 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
186 |  | BUS REACTOR_400kV_125MVAR_AURANGABAD Total | [10 empty] | 0.94236 | 0 | 0 | 1900-01-05 14:42 | [5 empty] | 96.96%
187 | WR1R35 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 240 | WRTS-I
187 |  | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
188 | WR1R36 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 125 | WRTS-I |  | 2015-05-20 | 10:23 | 2015-05-20 | 18:51 |  |  |  | 0.35278 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS |  |  | OSPT
188 |  | BUS REACTOR_400kV_125MVAR_BHATAPARA Total | [10 empty] | 0.35278 | 0 | 0 | 0 | [5 empty] | 98.86%
189 | WR1R37 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 240 | WRTS-I
189 |  | SWITCHABLE LR_765kV_WARDHA 1_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
190 | WR1R38 | BUS REACTOR_400kV_125MVAR_RAIGARH | 125 | WRTS-I
190 |  | BUS REACTOR_400kV_125MVAR_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-01 | 19:20 | 2015-05-02 | 17:50 |  |  |  | 0 | 0 | 0 | 0.9375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-01 | 19:20 | 2015-05-02 | 17:50 |  |  |  | 0 | 0 | 0 | 0.9375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-03 | 22:36 | 2015-05-04 | 23:46 |  |  |  | 0 | 0 | 0 | 1899-12-31 01:10 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-05 | 14:41 | 2015-05-05 | 17:30 |  |  |  | 0 | 0 | 0 | 0.11736 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-06 | 8:06 | 2015-05-06 | 16:58 |  |  |  | 0 | 0 | 0 | 0.36944 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-06 | 19:08 | 2015-05-07 | 17:54 |  |  |  | 0 | 0 | 0 | 0.94861 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-08 | 1:19 | 2015-05-08 | 18:57 |  |  |  | 0 | 0 | 0 | 0.73472 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-09 | 7:52 | 2015-05-09 | 19:36 |  |  |  | 0 | 0 | 0 | 0.48889 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-12 | 08:29 | 2015-05-12 | 18:38 |  |  |  | 0 | 0 | 0 | 0.42292 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-13 | 11:08 | 2015-05-13 | 16:20 |  |  |  | 0 | 0 | 0 | 0.21667 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-14 | 10:48 | 2015-05-14 | 17:18 |  |  |  | 0 | 0 | 0 | 0.27083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-15 | 11:48 | 2015-05-17 | 15:17 |  |  |  | 0 | 0 | 0 | 1900-01-01 03:29 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-18 | 7:14 | 2015-05-18 | 17:38 |  |  |  | 0 | 0 | 0 | 0.43333 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-18 | 22:36 | 2015-05-19 | 17:52 |  |  |  | 0 | 0 | 0 | 0.80278 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-20 | 09:07 | 2015-05-20 | 18:25 |  |  |  | 0 | 0 | 0 | 0.3875 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-21 | 9:03 | 2015-05-21 | 14:12 |  |  |  | 0 | 0 | 0 | 0.21458 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-22 | 9:01 | 2015-05-22 | 17:53 |  |  |  | 0 | 0 | 0 | 0.36944 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-25 | 7:17 | 2015-05-26 | 02:34 |  |  |  | 0 | 0 | 0 | 0.80347 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-27 | 09:06 | 2015-05-27 | 17:16 |  |  |  | 0 | 0 | 0 | 0.34028 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-28 | 7:53 | 2015-05-28 | 17:24 |  |  |  | 0 | 0 | 0 | 0.39653 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-05-30 | 11:46 | 2015-05-30 | 20:49 |  |  |  | 0 | 0 | 0 | 0.37708 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
191 |  | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1900-01-11 18:19 | [5 empty] | 100%
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-02 | 08:11 | 2015-05-02 | 16:55 |  |  |  | 0 | 0 | 0 | 0.36389 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-03 | 23:17 | 2015-05-04 | 18:12 |  |  |  | 0 | 0 | 0 | 0.78819 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-06 | 8:47 | 2015-05-08 | 15:58 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:11 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-08 | 23:02 | 2015-05-09 | 17:13 |  |  |  | 0 | 0 | 0 | 0.75764 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-10 | 23:33 | 2015-05-13 | 17:32 |  |  |  | 0 | 0 | 0 | 1900-01-01 17:59 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-14 | 9:20 | 2015-05-15 | 18:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:07 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-14 | 9:20 | 2015-05-15 | 18:27 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:07 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-16 | 6:30 | 2015-05-17 | 17:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 10:59 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-18 | 9:23 | 2015-05-18 | 18:03 |  |  |  | 0 | 0 | 0 | 0.36111 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-19 | 9:27 | 2015-05-19 | 17:52 |  |  |  | 0 | 0 | 0 | 0.35069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-20 | 09:46 | 2015-05-21 | 16:55 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:09 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-22 | 10:32 | 2015-05-22 | 14:05 |  |  |  | 0 | 0 | 0 | 0.14792 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-23 | 9:27 | 2015-05-23 | 17:05 |  |  |  | 0 | 0 | 0 | 0.31806 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-25 | 8:52 | 2015-05-29 | 18:09 |  |  |  | 0 | 0 | 0 | 1900-01-03 09:17 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-05-30 | 11:53 | 2015-05-31 | 18:20 |  |  |  | 0 | 0 | 0 | 1899-12-31 06:27 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 |  | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1900-01-18 07:22 | [5 empty] | 100%
193 | WR1R41 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 240 | WRTS-I
193 |  | SWITCHABLE LR_765kV_WARDHA 1_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
194 | WR1R42 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I
194 |  | SWITCHABLE LR_765kV_WARDHA 2_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
195 | WR1R43 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 80 | WRTS-I
195 |  | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
196 | WR1R44 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 80 | WRTS-I |  | 2015-04-21 | 11:29 | 2015-05-01 | 16:27 |  |  |  | 0 | 0 | 0 | 0.68542 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
196 | WR1R44 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 80 | WRTS-I |  | 2015-05-27 | 09:08 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-03 14:52 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
196 |  | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1900-01-04 07:19 | [5 empty] | 100%
197 | WR1R45 | BUS REACTOR_400kV_125MVAR_RAIPUR | 125 | WRTS-I
197 |  | BUS REACTOR_400kV_125MVAR_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
198 | WR1R46 | BUS REACTOR_765kV_330MVAR_WARDHA | 330 | WRTS-I |  | 2015-04-29 | 20:43 | 2015-05-01 | 17:16 |  |  |  | 0 | 0 | 0 | 0.71944 |  |  |  | BUS REACTOR KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
198 | WR1R46 | BUS REACTOR_765kV_330MVAR_WARDHA | 330 | WRTS-I |  | 2015-05-13 | 11:47 | 2015-05-13 | 16:26 |  |  |  | 0 | 0 | 0 | 0.19375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
198 |  | BUS REACTOR_765kV_330MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0.91319 | [5 empty] | 100%
199 | WR1R47 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 80 | WRTS-I |  | 2015-05-06 | 9:44 | 2015-05-16 | 14:57 |  |  |  | 0 | 0 | 0 | 1900-01-09 05:13 |  |  |  | H/T FOR CSD COMMISSIONING & FIRE FIGHTING WORKS AT SOLAPUR. |  |  | SCSD
199 |  | SWITCHABLE LR_400kV_KARAD_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 1900-01-09 05:13 | [5 empty] | 100%
200 | WR1R48 | BUS REACTOR_400kV_125MVAR_SEONI | 125 | WRTS-I |  | 2015-05-21 | 9:30 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-09 14:30 |  |  |  | H/T FOR FIRE FIGHTING WORKS |  |  | SCSD
200 |  | BUS REACTOR_400kV_125MVAR_SEONI Total | [10 empty] | 0 | 0 | 0 | 1900-01-09 14:30 | [5 empty] | 100%
201 | WR1R49 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 50 | WRTS-I |  | 2015-05-14 | 11:32 | 2015-05-15 | 18:34 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
201 |  | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 07:02 | [5 empty] | 100%
202 | WR1R50 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 50 | WRTS-I
202 |  | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
203 | WR1R51 | SWITCHABLE LR_400kV_A'BAD 1_PUNE | 50 | WRTS-I
203 |  | SWITCHABLE LR_400kV_A'BAD 1_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
204 | WR1R52 | SWITCHABLE LR_400kV_A'BAD 2_PUNE | 50 | WRTS-I
204 |  | SWITCHABLE LR_400kV_A'BAD 2_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-04 | 7:33 | 2015-05-04 | 18:25 |  |  |  | 0 | 0 | 0 | 0.45278 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-05 | 7:23 | 2015-05-06 | 18:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:05 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-08 | 6:56 | 2015-05-09 | 18:44 |  |  |  | 0 | 0 | 0 | 1899-12-31 11:48 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-11 | 9:55 | 2015-05-11 | 20:48 |  |  |  | 0 | 0 | 0 | 0.45347 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-12 | 08:53 | 2015-05-13 | 01:07 |  |  |  | 0 | 0 | 0 | 0.67639 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-13 | 07:05 | 2015-05-13 | 16:40 |  |  |  | 0 | 0 | 0 | 0.39931 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-15 | 12:07 | 2015-05-15 | 18:13 |  |  |  | 0 | 0 | 0 | 0.25417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-16 | 9:37 | 2015-05-16 | 16:55 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-18 | 11:48 | 2015-05-18 | 16:31 |  |  |  | 0 | 0 | 0 | 0.19653 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-19 | 8:26 | 2015-05-19 | 17:04 |  |  |  | 0 | 0 | 0 | 0.35972 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-20 | 10:22 | 2015-05-20 | 16:48 |  |  |  | 0 | 0 | 0 | 0.26806 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-21 | 8:52 | 2015-05-21 | 17:18 |  |  |  | 0 | 0 | 0 | 0.35139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-22 | 9:14 | 2015-05-23 | 17:04 |  |  |  | 0 | 0 | 0 | 1899-12-31 07:50 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-25 | 11:00 | 2015-05-25 | 18:52 |  |  |  | 0 | 0 | 0 | 0.32778 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-26 | 10:34 | 2015-05-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-04 13:26 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-26 | 10:34 | 2015-05-28 | 18:10 |  |  |  | 0 | 0 | 0 | 1900-01-01 07:36 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-05-29 | 9:26 | 2015-05-30 | 1:13 |  |  |  | 0 | 0 | 0 | 0.65764 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
205 |  | BUS REACTOR_400kV_125MVAR_PARLI Total | [10 empty] | 0 | 0 | 0 | 1900-01-15 20:35 | [5 empty] | 100%
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-11 | 10:17 | 2015-05-11 | 17:48 |  |  |  | 0 | 0 | 0 | 0.31319 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-18 | 11:54 | 2015-05-18 | 17:42 |  |  |  | 0 | 0 | 0 | 0.24167 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-19 | 11:22 | 2015-05-19 | 18:13 |  |  |  | 0 | 0 | 0 | 0.28542 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-20 | 09:50 | 2015-05-20 | 16:45 |  |  |  | 0 | 0 | 0 | 0.28819 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-21 | 9:30 | 2015-05-21 | 17:01 |  |  |  | 0 | 0 | 0 | 0.31319 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-22 | 10:00 | 2015-05-22 | 13:38 |  |  |  | 0 | 0 | 0 | 0.15139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-23 | 9:59 | 2015-05-23 | 17:12 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-25 | 10:43 | 2015-05-25 | 19:26 |  |  |  | 0 | 0 | 0 | 0.36319 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-26 | 10:47 | 2015-05-26 | 17:25 |  |  |  | 0 | 0 | 0 | 0.27639 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-27 | 09:05 | 2015-05-27 | 22:12 |  |  |  | 0 | 0 | 0 | 0.54653 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-28 | 7:56 | 2015-05-30 | 1:29 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-05-31 | 12:28 | 2015-05-31 | 24:00 |  |  |  | 0.48056 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE AVAILED FOR ATTENDING LEAKAGE THROUGH MOG. |  |  | OSFT
206 |  | BUS REACTOR_765kV_240MVAR_PUNE(GIS) Total | [10 empty] | 0.48056 | 0 | 0 | 1900-01-03 19:28 | [5 empty] | 98.45%
207 | WR1R55 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 240 | WRTS-I
207 |  | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-02 | 10:02 | 2015-05-02 | 16:12 |  |  |  | 0 | 0 | 0 | 0.25694 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-07 | 9:09 | 2015-05-07 | 17:54 |  |  |  | 0 | 0 | 0 | 0.36458 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-09 | 11:00 | 2015-05-09 | 17:30 |  |  |  | 0 | 0 | 0 | 0.27083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-10 | 11:01 | 2015-05-10 | 17:29 |  |  |  | 0 | 0 | 0 | 0.26944 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-13 | 11:26 | 2015-05-13 | 17:41 |  |  |  | 0 | 0 | 0 | 0.26042 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-15 | 10:07 | 2015-05-15 | 17:32 |  |  |  | 0 | 0 | 0 | 0.30903 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-19 | 10:04 | 2015-05-19 | 17:41 |  |  |  | 0 | 0 | 0 | 0.31736 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-20 | 08:56 | 2015-05-20 | 17:15 |  |  |  | 0 | 0 | 0 | 0.34653 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-21 | 06:20 | 2015-05-21 | 17:10 |  |  |  | 0 | 0 | 0 | 0.45139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-25 | 10:01 | 2015-05-25 | 18:20 |  |  |  | 0 | 0 | 0 | 0.34653 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-26 | 09:59 | 2015-05-26 | 18:36 |  |  |  | 0 | 0 | 0 | 0.35903 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-27 | 09:00 | 2015-05-27 | 17:43 |  |  |  | 0 | 0 | 0 | 0.36319 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-05-28 | 11:16 | 2015-05-28 | 18:15 |  |  |  | 0 | 0 | 0 | 0.29097 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
208 |  | BUS REACTOR_400kV_80MVAR_DHULE Total | [10 empty] | 0 | 0 | 0 | 1900-01-03 04:57 | [5 empty] | 100%
209 | WR1R57 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | 330 | WRTS-I |  | 2015-05-03 | 17:46 | 2015-05-03 | 17:46 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | LINE REACTOR CONVERT AS A BUS REACTOR AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
209 |  | SWITCHABLE LR_765kV_A'BAD 3_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
210 | WR1R58 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | 330 | WRTS-I
210 |  | SWITCHABLE LR_765kV_A'BAD 4_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
211 | WR1H1 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I
211 |  | HVDC_POLE1_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
212 | WR1H2 | HVDC_POLE2_BHADRAWATI | 500 | WRTS-I
212 |  | HVDC_POLE2_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
100%
Formulas:
ISTS Licensee = SUBTOTAL(9,N6:[ISTS Licensee, row above])
ISTS Licensee = SUBTOTAL(9,[ISTS Licensee, row above]:[ISTS Licensee, row above])
OTHERS = SUBTOTAL(9,O6:[OTHERS, row above])
OTHERS = SUBTOTAL(9,[OTHERS, row above]:[OTHERS, row above])
Deemed Available = SUBTOTAL(9,Q6:[Deemed Available, row above])
Deemed Available = SUBTOTAL(9,[Deemed Available, row above]:[Deemed Available, row above])

## Element list
|  | NEW PROPOSED NAME | CODE BY WREPC | TYPE | CODE BY PGCIL | LENGTH |  | DOCO | Type of conductor | Configuration | SN
1 | 1 | 220kV KORBA(EAST)-BUDDHIPADAR III | 63 | LINE | WR1L2 | 184 | WR1-IR1 | 1999-09-01 | AAAC Zebra | Single | 1
2 | 2 | 400kV RAIPUR-RAIGARH I | 74 | LINE | WR1L43 | 217.02 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 2
3 | 3 | 400kV RAIPUR-KWPCL II | 75 | LINE | WR1L44 | 203.02 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 3
4 | 4 | 400kV KWPCL-RAIGARH II | 76 | LINE | WR1L45 | 14 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 4
5 | 5 | 400kV RAIGARH-IBEUL I | 485 | LINE | WR1L110 | 94.43 | WR1-IR2 | 2014-11-13 | ACSR Moose | Twin | 5
6 | 6 | 400kV IBEUL-JHARSUGUDA I | 486 | LINE | WR1L111 | 20.03 | WR1-IR2 | 2014-11-13 | ACSR Moose | Twin | 6
7 | 7 | 400kV JHARSUGUDA-ROURKELA I | 78 | LINE | WR1L49 | 142.45 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 7
8 | 8 | 400kV RAIGARH-ROURKELA II | 433 | LINE | WR1L98 | 212.46 | WR1-IR2 | 2014-07-03 | ACSR Moose | Twin | 8
9 | 9 | 400KV RANCHI-SIPAT I | 124 | LINE | WR1L50 | 405.77 | WR1-IR3 | 2009-01-01 | ACSR Moose | Twin | 9
10 | 10 | 400KV RANCHI-SIPAT II | 125 | LINE | WR1L51 | 405.77 | WR1-IR3 | 2009-01-01 | ACSR Moose | Twin | 10
11 | 11 | 400kV RAIPUR-KSK III | 430 | LINE | WR1L52 | 134.74 | WR1-IR4 | 2014-07-01 | ACSR Moose | Twin | 11
12 | 12 | 400kV KSK-RKKML III | 471 | LINE | WR1L105 | 82.248 | WR1-IR4 | 2014-10-11 | ACSR Moose | Twin | 12
13 | 13 | 400kV RKKML-RAIGARH III | 472 | LINE | WR1L106 | 3.896 | WR1-IR4 | 2014-10-11 | ACSR Moose | Twin | 13
14 | 14 | 400KV RAIPUR-KSK IV | 440 | LINE | WR1L103 | 161.82 | WR1-IR4 | 2014-07-25 | ACSR Moose | Twin | 14
15 | 15 | 400kV KSK-RAIGARH IV | 441 | LINE | WR1L97 | 113.389 | WR1-IR4 | 2014-07-25 | ACSR Moose | Twin | 15
16 | 16 | 400kV RAIGARH-JHARSUGUDA III | 81 | LINE | WR1L56 | 110.98 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 16
17 | 17 | 400kV JHARSUGUDA-ROURKELA III | 82 | LINE | WR1L57 | 143.06 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 17
18 | 18 | 400kV RAIGARH-STERLITE IV | 83 | LINE | WR1L58 | 105 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 18
19 | 19 | 400kV STERLITE-ROURKELA IV | 84 | LINE | WR1L59 | 104.28 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 19
20 | 20 | 765kV D'JAIGARH-BILASPUR | 403 | LINE | WR1L60 | 90 | WR1-IR5 | 2014-04-01 | Bersimis | Quad | 20
21 | 21 | 765kV D'JAIGARH-RANCHI | 404 | LINE | WR1L61 | 303 | WR1-IR5 | 2014-04-01 | Bersimis | Quad | 21
22 | 22 | 765kV D'JAIGARH- JHARSUGUDA I | 444 | LINE | WR1L101 | 149.789 | WR1-IR6 | 2014-07-31 | Bersimis | Quad | 22
23 | 23 | 765kV D'JAIGARH- JHARSUGUDA II | 445 | LINE | WR1L102 | 149.789 | WR1-IR6 | 2014-07-31 | Bersimis | Quad | 23
24 | 24 | 400kV KORBA-KORBA(WEST) | 1 | LINE | WR1L3 | 14 | CG(O&M) | 1983-01-25 | ACSR Moose | Twin | 24
25 | 25 | 400kV KORBA-BHILAI I | 2 | LINE | WR1L4 | 197 | CG(O&M) | 1984-01-01 | ACSR Moose | Twin | 25
26 | 26 | 400kV KORBA-BHILAI II | 3 | LINE | WR1L5 | 192 | CG(O&M) | 1984-01-01 | ACSR Moose | Twin | 26
27 | 27 | 400kV BHILAI-KORADI | 4 | LINE | WR1L6 | 272 | MH(O&M) | 1984-05-01 | ACSR Moose | Twin | 27
28 | 28 | 400kV KORADI-SATPURA | 6 | LINE | WR1L7 | 149 | MH(O&M) | 1987-04-18 | ACSR Moose | Twin | 28
29 | 29 | 400kV RAIPUR-BHILAI I | 14 | LINE | WR1L8 | 13 | CG(O&M) | 1989-03-28 | ACSR Moose | Twin | 29
30 | 30 | 400kV BHILAI-BHADRAVATI I | 19 | LINE | WR1L9 | 322 | WR1-LINE | 1990-01-22 | ACSR Moose | Twin | 30
31 | 31 | 400kV RAIPUR-BHADRAVATI I | 13 | LINE | WR1L10 | 333 | WR1-LINE | 1989-03-28 | ACSR Moose | Twin | 31
32 | 32 | 400kV RAIPUR-BHADRAVATI II | 86 | LINE | WR1L11 | 345.55 | WR1-LINE | 2005-06-01 | ACSR Moose | Twin | 32
33 | 33 | 400kV RAIPUR-BHADRAVATI III | 87 | LINE | WR1L12 | 345.55 | WR1-LINE | 2005-06-01 | ACSR Moose | Twin | 33
34 | 34 | 400kV BHADRAVATI-CHANDRAPUR I | 11 | LINE | WR1L13 | 20 | MH(O&M) | 1989-03-28 | ACSR Moose | Twin | 34
35 | 35 | 400kV BHADRAVATI-CHANDRAPUR II | 12 | LINE | WR1L14 | 20 | MH(O&M) | 1989-03-28 | ACSR Moose | Twin | 35
36 | 36 | 400kV BHADRAVATI-CHANDRAPUR III | 92 | LINE | WR1L15 | 22.42 | MH(O&M) | 2006-05-01 | ACSR Moose | Twin | 36
37 | 37 | 400kV BHADRAVATI-CHANDRAPUR IV | 93 | LINE | WR1L16 | 22.42 | MH(O&M) | 2006-05-01 | ACSR Moose | Twin | 37
38 | 38 | 400kV KOLHAPUR-MAPUSA I | 73 | LINE | WR1L17 | 150 | MH(O&M) | 2003-01-01 | ACSR Moose | Twin | 38
39 | 39 | 400kV KOLHAPUR-MAPUSA II | 72 | LINE | WR1L18 | 150 | MH(O&M) | 2002-12-01 | ACSR Moose | Twin | 39
40 | 40 | 400kV MAHAN-VINDHYACHAL | 8 | LINE | WR1L25 | 19 | CG(O&M) | 1988-07-24 | ACSR Moose | Twin | 40
41 | 41 | 400kV KORBA-MAHAN | 9 | LINE | WR1L26 | 196 | CG(O&M) | 1988-07-24 | ACSR Moose | Twin | 41
42 | 42 | 400kV VINDHYACHAL-KORBA II | 99 | LINE | WR1L27 | 288.994 | CG(O&M) | 2007-06-01 | ACSR Moose | Twin | 42
43 | 43 | 400kV SATPURA-SEONI | 102 | LINE | WR1L28 | 1.5 | MH(O&M) | 2007-11-01 | ACSR Moose | Twin | 43
44 | 44 | 400kV BHILAI-SEONI | 103 | LINE | WR1L29 | 1.5 | MH(O&M) | 2007-11-01 | ACSR Moose | Twin | 44
45 | 45 | 400kV BHILAI-BHATAPARA | 65 | LINE | WR1L30 | 90.453 | CG(O&M) | 2000-01-01 | ACSR Moose | Twin | 45
46 | 46 | 400kV BHATAPARA-KORBA | 64 | LINE | WR1L31 | 123.73 | CG(O&M) | 2000-01-01 | ACSR Moose | Twin | 46
47 | 47 | 400kV RAIPUR-SIPAT I | 122 | LINE | WR1L34 | 149.12 | CG(O&M) | 2008-08-01 | ACSR Moose | Twin | 47
48 | 48 | 765kV TAMNAR PS-KOTRA PS I | 392 | LINE | WR1L35 | 47.97 | CG(O&M) | 2013-11-01 | Zebra | Hexa | 48
49 | 49 | 765kV TAMNAR PS-KOTRA PS II | 393 | LINE | WR1L36 | 47.97 | CG(O&M) | 2013-11-01 | Zebra | Hexa | 49
50 | 50 | 765kV KOTRA PS-DURG PS I | 398 | LINE | WR1L37 | 239.84 | CG(O&M) | 2014-02-01 | Zebra | Hexa | 50
51 | 51 | 765kV KOTRA PS-DURG PS II | 399 | LINE | WR1L38 | 239.84 | CG(O&M) | 2014-02-01 | Zebra | Hexa | 51
52 | 52 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 418 | LINE | WR1L39 | 52.56 | MH(O&M) | 2014-04-29 | ACSR Moose | Quad | 52
53 | 53 | 400kV BHADRAVATI-DHARIWAL TPP II | 416 | LINE | WR1L40 | 18.14 | MH(O&M) | 2014-04-21 | ACSR Moose | Twin | 53
54 | 54 | 400kV DHARIWAL TPP-PARLI II | 417 | LINE | WR1L41 | 391 | MH(O&M) | 2014-04-21 | ACSR Moose | Twin | 54
55 | 55 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 419 | LINE | WR1L42 | 52.56 | MH(O&M) | 2014-04-30 | ACSR Moose | Quad | 55
56 | 56 | 400KV RAIPUR-SIPAT II | 123 | LINE | WR1L62 | 149.12 | CG(O&M) | 2008-08-01 | ACSR Moose | Twin | 56
57 | 57 | 400kV RAIPUR-SIPAT III | 22 | LINE | WR1L63 | 162.04 | CG(O&M) | 1990-02-08 | ACSR Moose | Twin | 57
58 | 58 | 765kV BILASPUR-SIPAT I | 195 | LINE | WR1L64 | 21.51 | CG(O&M) | 2013-04-01 | Bersimis | Quad | 58
59 | 59 | 765kV SEONI-BILASPUR I | 196 | LINE | WR1L65 | 337.05 | WR1-LINE | 2013-04-01 | Bersimis | Quad | 59
60 | 60 | 765kV BILASPUR-SIPAT II | 197 | LINE | WR1L66 | 22.22 | CG(O&M) | 2013-04-01 | Bersimis | Quad | 60
61 | 61 | 765kV SEONI-BILASPUR II | 198 | LINE | WR1L67 | 338.33 | WR1-LINE | 2013-04-01 | Bersimis | Quad | 61
62 | 62 | 765kV SEONI-WARDHA I | 128 | LINE | WR1L68 | 267.89 | MH(O&M) | 2009-04-01 | Bersimis | Quad | 62
63 | 63 | 765kV SEONI-WARDHA II | 165 | LINE | WR1L69 | 260.76 | MH(O&M) | 2012-03-01 | Bersimis | Quad | 63
64 | 64 | 400kV WARDHA-AKOLA I | 126 | LINE | WR1L70 | 161.87 | MH(O&M) | 2009-04-01 | ACSR Moose | Twin | 64
65 | 65 | 400kV WARDHA-AKOLA II | 127 | LINE | WR1L71 | 161.87 | MH(O&M) | 2009-04-01 | ACSR Moose | Twin | 65
66 | 66 | 400kV AURANGABAD (PG) -AKOLA I | 133 | LINE | WR1L72 | 241.23 | MH(O&M) | 2009-12-01 | ACSR Moose | Twin | 66
67 | 67 | 400kV AURANGABAD (PG) -AKOLA II | 134 | LINE | WR1L73 | 289.97 | MH(O&M) | 2009-12-01 | ACSR Moose | Twin | 67
68 | 68 | 400kV BHADRAVATI-PARLI I | 150 | LINE | WR1L74 | 378.67 | MH(O&M) | 2011-06-01 | ACSR Moose | Twin | 68
69 | 69 | 400kV PARLI(PG)-PARLI(MSETCL) I | 152 | LINE | WR1L76 | 4.96 | MH(O&M) | 2011-06-01 | ACSR Moose | Twin | 69
70 | 70 | 400kV PARLI(PG)-PARLI(MSETCL) II | 153 | LINE | WR1L77 | 4.96 | MH(O&M) | 2011-06-01 | ACSR Moose | Twin | 70
71 | 71 | 400kV KORBA-RAIPUR III | 154 | LINE | WR1L78 | 211.86 | CG(O&M) | 2011-07-01 | ACSR Moose | Twin | 71
72 | 72 | 400kV KORBA-RAIPUR IV | 155 | LINE | WR1L79 | 212.83 | CG(O&M) | 2011-07-01 | ACSR Moose | Twin | 72
73 | 73 | 400kV WARDHA-PARLI I | 156 | LINE | WR1L80 | 336.94 | MH(O&M) | 2011-08-01 | ACSR Moose | Quad | 73
74 | 74 | 400kV WARDHA-PARLI II | 157 | LINE | WR1L81 | 336.94 | MH(O&M) | 2011-08-01 | ACSR Moose | Quad | 74
75 | 75 | 400kV KORBA-BALCO | 163 | LINE | WR1L82 | 7.45 | CG(O&M) | 2012-03-01 | ACSR Moose | Twin | 75
76 | 76 | 400kV BALCO-BIRSINGHPUR | 164 | LINE | WR1L83 | 219.19 | CG(O&M) | 2012-03-01 | ACSR Moose | Twin | 76
77 | 77 | 400kV WARDHA-MAUDA II | 175 | LINE | WR1L84 | 123.84 | MH(O&M) | 2012-06-01 | ACSR Moose | Quad | 77
78 | 78 | 400kV KORBA-VANDANA | 168 | LINE | WR1L85 | 14.77 | CG(O&M) | 2012-04-01 | ACSR Moose | Twin | 78
79 | 79 | 400KV VANDANA-BIRSINGHPUR | 169 | LINE | WR1L86 | 211.87 | CG(O&M) | 2012-04-01 | ACSR Moose | Twin | 79
80 | 80 | 400KV RAIPUR-WARDHA I | 179 | LINE | WR1L87 | 370.57 | WR1-LINE | 2013-01-01 | ACSR Moose | Quad | 80
81 | 81 | 400KV RAIPUR-WARDHA II | 180 | LINE | WR1L88 | 370.57 | WR1-LINE | 2013-01-01 | ACSR Moose | Quad | 81
82 | 82 | 400KV WARDHA-IEPL | 171 | LINE | WR1L89 | 52.62 | MH(O&M) | 2012-04-01 | ACSR Moose | Quad | 82
83 | 83 | 400KV IEPL-MAUDA | 170 | LINE | WR1L90 | 70.83 | MH(O&M) | 2012-04-01 | ACSR Moose | Quad | 83
84 | 84 | 400kV RAIPUR-DURG I | 190 | LINE | WR1L91 | 21.5 | CG(O&M) | 2013-04-01 | ACSR Moose | Twin | 84
85 | 85 | 400kV RAIPUR-DURG II | 191 | LINE | WR1L92 | 21.5 | CG(O&M) | 2013-04-01 | ACSR Moose | Twin | 85
86 | 86 | 400kV RAIGARH-KOTRA PS I | 389 | LINE | WR1L93 | 6.29 | CG(O&M) | 2013-05-01 | ACSR Moose | Twin | 86
87 | 87 | 400kV RAIGARH-KOTRA PS II | 390 | LINE | WR1L94 | 6.29 | CG(O&M) | 2013-05-01 | ACSR Moose | Twin | 87
88 | 88 | 765KV DURG PS - D'JAIGARH | 424 | LINE | WR1L95 | 357.62 | CG(O&M) | 2014-05-24 | Bersimis | Quad | 88
89 | 89 | 765kV WARDHA - AURANGABAD(PG) I | 435 | LINE | WR1L99 | 347.577 | MH(O&M) | 2014-07-08 | Bersimis | Quad | 89
90 | 90 | 765kV WARDHA - AURANGABAD(PG) II | 436 | LINE | WR1L100 | 347.577 | MH(O&M) | 2014-07-08 | Bersimis | Quad | 90
91 | 91 | 400kV KORBA-SIPAT | 458 | LINE | WR1L104 | 68.653 | CG(O&M) | 2014-09-03 | ACSR Moose | Twin | 91
92 | 92 | 765kV DURG PS -WARDHA_1 | 480 | LINE | WR1L108 | 369.107 | WR1-LINE | 2014-11-17 | zebra | Hexa | 92
93 | 93 | 765kV DURG PS -WARDHA_2 | 481 | LINE | WR1L109 | 369.107 | WR1-LINE | 2014-11-17 | Zebra | Hexa | 93
94 | 94 | 765kV PUNE(GIS)-SOLAPUR | 512 | LINE | WR1L112 | 269.842 | MH(O&M) | 2015-03-02 | Bersimis | Quad | 94
95 | 95 | 400Kv PARLI-PUNE(GIS)_1 | 513 | LINE | WR1L113 | 272.202 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 95
96 | 96 | 400Kv PARLI-PUNE(GIS)_2 | 514 | LINE | WR1L114 | 272.202 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 96
97 | 97 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 515 | LINE | WR1L115 | 65 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 97
98 | 98 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 516 | LINE | WR1L116 | 65 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 98
99 | 99 | 765kV WARDHA - AURANGABAD(PG) III |  | LINE | WR1L117 | 355 | MH(O&M) | 2015-04-01 | zebra | Hexa | 99
100 | 100 | 765kV WARDHA - AURANGABAD(PG) IV |  | LINE | WR1L118 | 355 | MH(O&M) | 2015-04-01 | zebra | Hexa | 100
101 | 101 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 |  | LINE | WR1L119 | 11.2 | MH(O&M) | 2015-04-03 | ACSR Moose | Twin | 101
102 | 102 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 |  | LINE | WR1L120 | 11.2 | MH(O&M) | 2015-04-03 | ACSR Moose | Twin | 102
103 | 103 | 765kV DURG PS- CHAMPA_1 |  | LINE | WR1L121 | 149.15 | CG(O&M) | 2015-05-30 | zebra | Hexa | 103
104 | 104 | 765kV CHAMPA- KOTRA PS |  | LINE | WR1L122 | 96.33 | CG(O&M) | 2015-05-31 | Bersimis | Quad | 104
105 | 1 | ICT1_400/220kv_RAIPUR | 233 | ICT | WR1T1 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 105
106 | 2 | ICT2_400/220kv_RAIPUR | 234 | ICT | WR1T2 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 106
107 | 3 | ICT1_400/220kv_MAPUSA | 235 | ICT | WR1T3 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 107
108 | 4 | ICT2_400/220kv_MAPUSA | 236 | ICT | WR1T4 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 108
109 | 5 | ICT1_400/220kv_BAHATAPARA | 239 | ICT | WR1T5 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 109
110 | 6 | ICT1_400/220kv_RAIGARH | 240 | ICT | WR1T6 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 110
111 | 7 | ICT2_400/220kv_RAIGARH | 241 | ICT | WR1T7 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 111
112 | 8 | ICT1_765/400kv_SEONI | 242 | ICT | WR1T8 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 112
113 | 9 | ICT2_765/400kv_SEONI | 243 | ICT | WR1T9 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 113
114 | 10 | ICT3_765/400kv_SEONI | 244 | ICT | WR1T10 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 114
115 | 11 | ICT1_400/220kv_SEONI | 245 | ICT | WR1T11 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 115
116 | 12 | ICT1_765/400kv_WARDHA | 246 | ICT | WR1T12 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 116
117 | 13 | ICT2_765/400kv_WARDHA | 247 | ICT | WR1T13 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 117
118 | 14 | ICT3_765/400kv_WARDHA | 248 | ICT | WR1T14 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 118
119 | 15 | ICT1_765/400kv_BILASPUR | 249 | ICT | WR1T15 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 119
120 | 16 | ICT2_765/400kv_BILASPUR | 250 | ICT | WR1T16 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 120
121 | 17 | ICT2_400/220kv_BAHATAPARA | 251 | ICT | WR1T17 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 121
122 | 18 | ICT2_400/220kv_SEONI | 252 | ICT | WR1T18 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 122
123 | 19 | ICT3_400/220kv_RAIPUR | 253 | ICT | WR1T19 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 123
124 | 20 | ICT1_400/220kv_WARDHA | 254 | ICT | WR1T20 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 124
125 | 21 | ICT2_400/220kv_WARDHA | 255 | ICT | WR1T21 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 125
126 | 22 | ICT3_400/220kv_WARDHA | 256 | ICT | WR1T22 | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | 126
127 | 23 | ICT1_400/220kv_SOLAPUR | 257 | ICT | WR1T23 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 127
128 | 24 | ICT2_400/220kv_SOLAPUR | 258 | ICT | WR1T24 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 128
129 | 25 | ICT1_400/220kv_PUNE | 259 | ICT | WR1T25 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 129
130 | 26 | ICT2_400/220kv_PUNE | 260 | ICT | WR1T26 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 130
131 | 27 | ICT3_400/220kv_PUNE | 261 | ICT | WR1T27 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 131
132 | 28 | ICT3_765/400kv_BILASPUR | 262 | ICT | WR1T28 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 132
133 | 29 | ICT1_765/400kv_KOTRA PS | 263 | ICT | WR1T29 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 133
134 | 30 | ICT2_765/400kv_KOTRA PS | 264 | ICT | WR1T30 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 134
135 | 31 | ICT4_765/400kv_KOTRA PS | 265 | ICT | WR1T31 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 135
136 | 32 | ICT3_400/220kv_MAPUSA | 266 | ICT | WR1T32 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 136
137 | 33 | ICT1_765/400kv_TAMNAR PS | 267 | ICT | WR1T33 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 137
138 | 34 | ICT2_765/400kv_TAMNAR PS | 268 | ICT | WR1T34 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 138
139 | 35 | ICT1_765/400kv_DURG PS | 269 | ICT | WR1T35 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 139
140 | 36 | ICT1_765/400kv_SOLAPUR | 270 | ICT | WR1T36 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 140
141 | 37 | ICT2_765/400kv_SOLAPUR | 271 | ICT | WR1T37 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 141
142 | 38 | ICT1_400/200kv_AURANGABAD | 272 | ICT | WR1T38 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 142
143 | 39 | ICT2_400/200kv_AURANGABAD | 273 | ICT | WR1T39 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 143
144 | 40 | ICT2_765/400kv_AURANGABAD | 274 | ICT | WR1T40 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 144
145 | 41 | ICT3_765/400kv_TAMNAR PS | 275 | ICT | WR1T41 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 145
146 | 42 | ICT3_765/400kv_KOTRA PS | 276 | ICT | WR1T42 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 146
147 | 43 | ICT1_765/400kv_AURANGABAD | 429 | ICT | WR1T43 | 1500 | MH(O&M) | 2014-07-01 | 1500 | 1500 | 147
148 | 44 | ICT2_765/400kv_D'JAIGARH | 426 | ICT | WR1T44 | 1500 | CG(O&M) | 2014-06-19 | 1500 | 1500 | 148
149 | 45 | ICT1_765/400kv_D'JAIGARH | 437 | ICT | WR1T45 | 1500 | CG(O&M) | 2014-07-09 | 1500 | 1500 | 149
150 | 46 | ICT1_400/200kv_BHADRAWATI | 517 | ICT | WR1T46 | 315 | MH(O&M) | 2015-03-19 | 315 | 315 | 150
151 | 47 | ICT1_765/400kv_PUNE(GIS) | 518 | ICT | WR1T47 | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | 151
152 | 48 | ICT2_765/400kv_PUNE(GIS) | 519 | ICT | WR1T48 | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | 152
153 | 1 | BUS REACTOR_400kV_63MVAR_RAIGARH | 282 | BR | WR1R1 | 63 | CG(O&M) | 2013-04-01 | 63 | 63 | 153
154 | 2 | BUS REACTOR_765kV_240MVAR_SEONI | 288 | BR | WR1R2 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 154
155 | 3 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 279 | BR | WR1R3 | 50 | CG(O&M) | 2013-04-01 | 50 | 50 | 155
156 | 4 | BUS REACTOR_400kV_50MVAR_WARDHA | 280 | BR | WR1R4 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 156
157 | 5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 283 | BR | WR1R5 | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | 157
158 | 6 | BUS REACTOR_400kV_63MVAR_PARLI | 284 | BR | WR1R6 | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | 158
159 | 7 | BUS REACTOR_400kV_50MVAR_PUNE | 281 | BR | WR1R7 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 159
160 | 8 | BUS REACTOR_765kV_240MVAR_WARDHA | 289 | BR | WR1R8 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 160
161 | 9 | BUS REACTOR_765kV_240MVAR_BILASPUR | 290 | BR | WR1R9 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 161
162 | 10 | SWITCHABLE LR_765kV_BINA_SEONI | 291 | BR | WR1R10 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 162
163 | 11 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 292 | BR | WR1R11 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 163
164 | 12 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 293 | BR | WR1R12 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 164
165 | 13 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 294 | BR | WR1R13 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 165
166 | 14 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 295 | BR | WR1R14 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 166
167 | 15 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 287 | BR | WR1R15 | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | 167
168 | 16 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 296 | BR | WR1R16 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 168
169 | 17 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 277 | BR | WR1R17 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 169
170 | 18 | BUS REACTOR_400kV_80MVAR_RAIPUR | 285 | BR | WR1R18 | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | 170
171 | 19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 278 | BR | WR1R19 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 171
172 | 20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 286 | BR | WR1R20 | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | 172
173 | 21 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 297 | BR | WR1R21 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 173
174 | 22 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 298 | BR | WR1R22 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 174
175 | 23 | BUS REACTOR_765kV_240MVAR_DURG PS | 299 | BR | WR1R23 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 175
176 | 24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 300 | BR | WR1R24 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 176
177 | 25 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | 301 | BR | WR1R25 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 177
178 | 26 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | 302 | BR | WR1R26 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 178
179 | 27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 305 | BR | WR1R27 | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | 179
180 | 28 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 306 | BR | WR1R28 | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | 180
181 | 29 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 303 | BR | WR1R29 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 181
182 | 30 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 407 | BR | WR1R30 | 240 | MH(O&M) | 2014-04-01 | 240 | 240 | 182
183 | 31 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 408 | BR | WR1R31 | 330 | CG(O&M) | 2014-04-01 | 240 | 240 | 183
184 | 32 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 415 | BR | WR1R32 | 330 | CG(O&M) | 2014-04-18 | 240 | 240 | 184
185 | 33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 304 | BR | WR1R33 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 185
186 | 34 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 420 | BR | WR1R34 | 125 | MH(O&M) | 2014-04-30 | 125 | 125 | 186
187 | 35 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 425 | BR | WR1R35 | 240 | CG(O&M) | 2014-05-26 | 240 | 240 | 187
188 | 36 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 442 | BR | WR1R36 | 125 | CG(O&M) | 2014-07-26 | 125 | 125 | 188
189 | 37 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 423 | BR | WR1R37 | 240 | MH(O&M) | 2014-05-02 | 240 | 240 | 189
190 | 38 | BUS REACTOR_400kV_125MVAR_RAIGARH | 446 | BR | WR1R38 | 125 | CG(O&M) | 2014-08-01 | 125 | 125 | 190
191 | 39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 448 | BR | WR1R39 | 240 | MH(O&M) | 2014-08-02 | 240 | 240 | 191
192 | 40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 450 | BR | WR1R40 | 240 | MH(O&M) | 2014-08-07 | 240 | 240 | 192
193 | 41 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 456 | BR | WR1R41 | 240 | CG(O&M) | 2014-08-21 | 240 | 240 | 193
194 | 42 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 457 | BR | WR1R42 | 240 | CG(O&M) | 2014-08-29 | 240 | 240 | 194
195 | 43 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 462 | BR | WR1R43 | 80 | MH(O&M) | 2014-10-01 | 80 | 80 | 195
196 | 44 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 464 | BR | WR1R44 | 80 | MH(O&M) | 2014-10-02 | 80 | 80 | 196
197 | 45 | BUS REACTOR_400kV_125MVAR_RAIPUR | 465 | BR | WR1R45 | 125 | CG(O&M) | 2014-10-02 | 125 | 125 | 197
198 | 46 | BUS REACTOR_765kV_330MVAR_WARDHA | 475 | BR | WR1R46 | 330 | MH(O&M) | 2014-11-03 | 330 | 330 | 198
199 | 47 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 484 | BR | WR1R47 | 80 | MH(O&M) | 2014-11-26 | 80 | 80 | 199
200 | 48 | BUS REACTOR_400kV_125MVAR_SEONI | 489 | BR | WR1R48 | 125 | MH(O&M) | 2014-12-13 | 125 | 125 | 200
201 | 49 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 490 | BR | WR1R49 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 201
202 | 50 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 491 | BR | WR1R50 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 202
203 | 51 | SWITCHABLE LR_400kV_A'BAD 1_PUNE | 492 | BR | WR1R51 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 203
204 | 52 | SWITCHABLE LR_400kV_A'BAD 2_PUNE | 493 | BR | WR1R52 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 204
205 | 53 | BUS REACTOR_400kV_125MVAR_PARLI | 505 | BR | WR1R53 | 125 | MH(O&M) | 2015-01-10 | 125 | 125 | 205
206 | 54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 520 | BR | WR1R54 | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | 206
207 | 55 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 521 | BR | WR1R55 | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | 207
208 | 56 | BUS REACTOR_400kV_80MVAR_DHULE | 365 | BR | WR1R56 | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | 208
209 | 57 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA |  | BR | WR1R57 | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | 209
210 | 58 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA |  | BR | WR1R58 | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | 210
211 | 1 | HVDC_POLE1_BHADRAWATI | 307 | HVDC | WR1H1 | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | 211
212 | 2 | HVDC_POLE2_BHADRAWATI | 308 | HVDC | WR1H2 | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | 212
Note on I105: DOCO earlier but splitted into two line 30.05.15 & 31.05.15

## Sheet2
Total Element Nos. | To be included | Element having tripping
1 | 1 | 1
2 | 2 | 2
3 |  | 8
4 |  | 9
5 |  | 10
6 |  | 11
7 |  | 12
8 | 8 | 13
9 | 9 | 14
10 | 10 | 21
11 | 11 | 24
12 | 12 | 26
13 | 13 | 27
14 | 14 | 31
15 |  | 32
16 |  | 33
17 |  | 38
18 |  | 39
19 |  | 41
20 |  | 46
21 | 21 | 47
22 |  | 53
23 |  | 54
24 | 24 | 56
25 |  | 58
26 | 26 | 68
27 | 27 | 75
28 |  | 76
29 |  | 77
30 |  | 81
31 | 31 | 82
32 | 32 | 83
33 | 33 | 86
34 |  | 87
35 |  | 88
36 |  | 89
37 |  | 90
38 | 38 | 91
39 | 39 | 92
40 |  | 93
41 | 41 | 94
42 |  | 97
43 |  | 98
44 |  | 99
45 |  | 103
46 | 46 | 104
47 | 47 | 106
48 |  | 107
49 |  | 109
50 |  | 115
51 |  | 121
52 |  | 123
53 | 53 | 125
54 | 54 | 129
55 |  | 130
56 | 56 | 131
57 |  | 134
58 | 58 | 144
59 |  | 147
60 |  | 151
61 |  | 157
62 |  | 158
63 |  | 159
64 |  | 161
65 |  | 170
66 |  | 171
67 |  | 172
68 | 68 | 176
69 |  | 177
70 |  | 178
71 |  | 179
72 |  | 181
73 |  | 183
74 |  | 185
75 | 75 | 186
76 | 76 | 188
77 | 77 | 191
78 |  | 192
79 |  | 196
80 |  | 198
81 | 81 | 199
82 | 82 | 200
83 | 83 | 201
84 |  | 205
85 |  | 206
86 | 86 | 208
87 | 87 | 209
88 | 88
89 | 89
90 | 90
91 | 91
92 | 92
93 | 93
94 | 94
95
96
97 | 97
98 | 98
99 | 99
100
101
102
103 | 103
104 | 104
105
106 | 106
107 | 107
108
109 | 109
110
111
112
113
114
115 | 115
116
117
118
119
120
121 | 121
122
123 | 123
124
125 | 125
126
127
128
129 | 129
130 | 130
131 | 131
132
133
134 | 134
135
136
137
138
139
140
141
142
143
144 | 144
145
146
147 | 147
148
149
150
151 | 151
152
153
154
155
156
157 | 157
158 | 158
159 | 159
160
161 | 161
162
163
164
165
166
167
168
169
170 | 170
171 | 171
172 | 172
173
174
175
176 | 176
177 | 177
178 | 178
179 | 179
180
181 | 181
182
183 | 183
184
185 | 185
186 | 186
187
188 | 188
189
190
191 | 191
192 | 192
193
194
195
196 | 196
197
198 | 198
199 | 199
200 | 200
201 | 201
202
203
204
205 | 205
206 | 206
207
208 | 208
209 | 209
210
211
212
3
4
5
6
7
15
16
17
18
19
20
22
23
25
28
29
30
34
35
36
37
40
42
43
44
45
48
49
50
51
52
55
57
59
60
61
62
63
64
65
66
67
69
70
71
72
73
74
78
79
80
84
85
95
96
100
101
102
105
108
110
111
112
113
114
116
117
118
119
120
122
124
126
127
128
132
133
135
136
137
138
139
140
141
142
143
145
146
148
149
150
152
153
154
155
156
160
162
163
164
165
166
167
168
169
173
174
175
180
182
184
187
189
190
193
194
195
197
202
203
204
207
210
211
212

## tripping
L
ELEMENT WISE TRIPPING DETAILS FOR POWERGRID WRTS-I FOR THE MONTH OF MAY-15 | [16 empty] | O | Y
[17 empty] | S | N
|  | POWERGRID WRTS-I | MONTH: | 2015-05-31 |  |  |  |  | ATTRIBUTED TO ( IN HRS:MIN) | [7 empty] | D
SN | EVENT NO. | NAME OF LINE/ICT | OWNERSHIP | Tripping No. | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | LICENCEE | OTHERS | SYSTEM CONSTR. | DEEMED AVAILABLE | OUTAGE CATEGORY | UNIT OUT DUE TO TRIPPING OF LINE | CATEGORY | REASON | Tripping Code | Restoration Code
1 | 703033 | ICT3_400/220kv_PUNE | WRTS-I | 0 | 2015-03-05 | 14:56 | 2015-05-14 | 16:49 | 0 | 0 | 0 | 415:11 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 03/567 | 5/1515
2 | 703220 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | WRTS-I | 0 | 2015-04-21 | 11:29 | 2015-05-01 | 16:27 | 0 | 0 | 0 | 0.68542 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 4/2237
3 | 704165 | 765kV WARDHA - AURANGABAD(PG) III | WRTS-I | 0 | 2015-04-23 | 21:41 | 2015-05-02 | 10:33 | 0 | 0 | 0 | 1899-12-31 10:33 | D | N | LVRD | LINE KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 05/120,NL-05/25
4 | 704210 | 400kV RAIPUR-KSK III | WRTS-I | 0 | 2015-04-25 | 17:33 | 2015-05-06 | 20:34 | 0 | 0 | 1900-01-04 20:34 | 0 | S | N | LAMC | LINE TRIPPED ON B PH TO E FAULT DUE TO THEFT OF LARGE BRACING MEMBERS FROM MAIN LEGS C AND D AT LOC. NO. 547 BY MISCREANT PEOPLES. THIS MAY CAUSE TOWER COLLAPSED AT LOC. NO. 547 DURING HEAVY LIGHTENING AND THUNDER STORM 69 KM FROM RAIPUR. | - | 5/657
5 | 704211 | 400kV RAIPUR-KSK IV | WRTS-I | 0 | 2015-04-25 | 17:33 | 2015-05-06 | 20:39 | 0 | 0 | 1900-01-04 20:39 | 0 | S | N | LAMC | LINE TRIPPED ON B PH TO E FAULT DUE TO THEFT OF LARGE BRACING MEMBERS FROM MAIN LEGS C AND D AT LOC. NO. 547 BY MISCREANT PEOPLES. THIS MAY CAUSE TOWER COLLAPSED AT LOC. NO. 547 DURING HEAVY LIGHTENING AND THUNDER STORM 69 KM FROM RAIPUR. | - | 5/658
6 | 704073 | ICT1_765/400kv_PUNE(GIS) | WRTS-I | 0 | 2015-04-26 | 9:37 | 2015-05-01 | 12:44 | 0 | 0 | 0 | 0.53056 | D | N | SCSD | H/T FOR SWITCHING IMPULSE TESTING. | 4/2800 NL-4/831 | 5/30, NL-5/8
7 | 704074 | 765kV WARDHA - AURANGABAD(PG) I | WRTS-I | 0 | 2015-04-26 | 11:36 | 2015-05-05 | 0:34 | 0 | 0 | 0 | 1900-01-03 00:34 | D | N | LPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 4/2813 NL-4/836 | 05/440 NL-05/102
8 | 704079 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | WRTS-I | 0 | 2015-04-27 | 22:02 | 2015-05-05 | 0:34 | 0 | 0 | 0 | 1900-01-03 00:34 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 4/2996 NL-4/881 | 05/440 NL-05/102
9 | 704087 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-04-29 | 11:49 | 2015-05-01 | 16:32 | 0 | 0 | 0 | 0.68889 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 04/3174 | 5/58
10 | 704089 | BUS REACTOR_765kV_330MVAR_WARDHA | WRTS-I | 0 | 2015-04-29 | 20:43 | 2015-05-01 | 17:16 | 0 | 0 | 0 | 0.71944 | D | N | SVRD | BUS REACTOR KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | --- | 5/60, NL-5/13
11 | 704091 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-04-30 | 08:32 | 2015-05-01 | 17:14 | 0 | 0 | 0 | 0.71806 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 04/3262,NL-04/960 | 5/65, NL-5/14
12 | 704094 | ICT1_400/220kv_SEONI | WRTS-I | 1 | 2015-04-30 | 21:20 | 2015-05-28 | 22:16 | 1900-01-26 22:16 | 0 | 0 | 0 | L | N | SEFT | ICT TRIPPED DUE TO FAILURE OF HV SIDE B PHASE BUSHING. |  | 05/3147
13 | 705001 | 400kV RAIPUR-BHADRAVATI I | WRTS-I | 0 | 2015-05-01 | 9:00 | 2015-05-01 | 17:23 | 0 | 0 | 0 | 0.34931 | D | N | SCSD | LINE H/T FOR NTAMC & CSD WORKS AT RAIPUR SS | 5/16 | 5/66
14 | 705002 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-01 | 16:26 | 2015-05-02 | 07:00 | 0 | 0 | 0 | 0.60694 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/56 | 05/110
15 | 705003 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-01 | 19:20 | 2015-05-02 | 17:50 | 0 | 0 | 0 | 0.9375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/79, NL-5/17 | 05/182,NL-05/41
16 | 705004 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-01 | 16:26 | 2015-05-02 | 07:00 | 0 | 0 | 0 | 0.60694 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/56 | 05/110
17 | 705005 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-01 | 19:20 | 2015-05-02 | 17:50 | 0 | 0 | 0 | 0.9375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/79, NL-5/17 | 05/182,NL-05/41
18 | 705006 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-02 | 08:11 | 2015-05-02 | 16:55 | 0 | 0 | 0 | 0.36389 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/115, NL-05/22 | 05/170, NL-05/38
19 | 705007 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-02 | 08:46 | 2015-05-02 | 16:14 | 0 | 0 | 0 | 0.31111 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/118 | 05/166
20 | 705008 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-02 | 09:04 | 2015-05-02 | 16:07 | 0 | 0 | 0 | 0.29375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/124 | 05/163
21 | 705009 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-02 | 09:08 | 2015-05-02 | 16:11 | 0 | 0 | 0 | 0.29375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/121 | 05/164
22 | 705010 | 400kV RAIGARH-ROURKELA II | WRTS-I | 0 | 2015-05-02 | 9:26 | 2015-05-02 | 19:39 | 0.42569 | 0 | 0 | 0 | L | N | OSPT | OUTAGE AVAILED BY ER-II (ROURKELA) | 05/123,NL-05/26,ER-05/35 | 05/200,NL-05/44,ER-05/60
23 | 705011 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-02 | 10:02 | 2015-05-02 | 16:12 | 0 | 0 | 0 | 0.25694 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/131 | 05/165
24 | 705012 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-02 | 10:32 | 2015-05-02 | 15:14 | 0 | 0 | 0 | 0.19583 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/136, NL-05/30 | 05/155, NL-05/35
25 | 705013 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-02 | 17:42 | 2015-05-03 | 7:37 | 0 | 0 | 0 | 0.57986 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/179 | 5/229
26 | 705014 | 400KV RANCHI-SIPAT I | WRTS-I | 0 | 2015-05-03 | 10:03 | 2015-05-03 | 15:23 | 0 | 0 | 0.22222 | 0 | S | N | LMAC | H/T FOR REPLACEMENT OF DAMAGED INSULATORS BY ER | - | -
27 | 705015 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-03 | 16:44 | 2015-05-04 | 7:10 | 0 | 0 | 0 | 0.60139 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/271 | 5/339
28 | 705016 | 765kV WARDHA - AURANGABAD(PG) III | WRTS-I | 0 | 2015-05-03 | 17:24 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-27 06:36 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/276 NL-5/62
29 | 705017 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | WRTS-I | 0 | 2015-05-03 | 17:46 | 2015-05-03 | 17:46 | 0 | 0 | 0 | 0 | D | N | SVRD | LINE REACTOR CONVERT AS A BUS REACTOR AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/276 NL-5/62
30 | 705018 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-03 | 21:09 | 2015-05-04 | 18:03 | 0 | 0 | 0 | 0.87083 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/292 NL-5/67 | 5/388 NL-05/88
31 | 705019 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-03 | 22:36 | 2015-05-04 | 23:46 | 0 | 0 | 0 | 1899-12-31 01:10 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/301 NL-5/68 | 05/439 NL-05/101
32 | 705020 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-03 | 23:17 | 2015-05-04 | 18:12 | 0 | 0 | 0 | 0.78819 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/306 NL-5/70 | 5/395 NL-05/90
33 | 705021 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-04 | 7:29 | 2015-05-04 | 18:01 | 0 | 0 | 0 | 0.43889 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/343 | 5/389
34 | 705022 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-04 | 7:32 | 2015-05-04 | 18:10 | 0 | 0 | 0 | 0.44306 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/344 | 5/392
35 | 705023 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-04 | 7:33 | 2015-05-04 | 18:25 | 0 | 0 | 0 | 0.45278 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/345 | 5/393
36 | 705024 | 400kV RAIPUR-BHADRAVATI II | WRTS-I | 0 | 2015-05-04 | 9:10 | 2015-05-04 | 19:23 | 0 | 0 | 0 | 0.42569 | D | N | SCSD | LINE H/T FOR CSD & NTAMC WORKS AT RAIPUR END | 5/356 | 5/398
37 | 705025 | 400KV RANCHI-SIPAT II | WRTS-I | 0 | 2015-05-04 | 9:22 | 2015-05-04 | 13:15 | 0 | 0 | 0.16181 | 0 | S | N | LMAC | H/T FOR REPLACEMENT OF DAMAGED INSULATORS BY ER | 5/357 ER-5/104 NL-05/77 | 5/371 ER-5/115 NL-05/83
38 | 705026 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-04 | 9:39 | 2015-05-04 | 16:15 | 0 | 0 | 0 | 0.275 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/359 | 5/380
39 | 705027 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-04 | 9:41 | 2015-05-04 | 16:12 | 0 | 0 | 0 | 0.27153 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/360 | 5/379
40 | 705028 | BUS REACTOR_400kV_125MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-04 | 9:43 | 2015-05-04 | 18:04 | 0 | 0 | 0 | 0.34792 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/361 | 5/387
41 | 705029 | 400kV KORBA-BHILAI II | WRTS-I | 0 | 2015-05-04 | 10:56 | 2015-05-07 | 9:51 | 0 | 0 | 0 | 1900-01-01 22:55 | D | N | LCSD | FOR CROSSING WORKS OF 765KV DHARAMJAYGARH-JABALPUR LINE BY JTCL | 5/363 | 5/681
42 | 705030 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-04 | 18:14 | 2015-05-05 | 6:13 | 0 | 0 | 0 | 0.49931 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/391 | 5/451
43 | 705031 | 400kV DHARIWAL TPP-PARLI II | WRTS-I | 0 | 2015-05-04 | 18:42 | 2015-05-04 | 20:10 | 0 | 0.061111 | 0 | 0 | O | N | OMSU | LINE TRIPPED ON B PH TO E FAULT AND DT RECIVED AT PARLI END F.L. R OF 191 KM FROM PARLI. LINE TRIPPED DUE TO FALLING OF OPGW PILOT WIRE DURING ONLINE STRINGING OF OPGW WIRE. THIS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. FOR REPLACEMENT OF GI EARTHWIRE BY OPGW . | … | 5/402
44 | 705032 | 400KV WARDHA-IEPL | WRTS-I | 0 | 2015-05-04 | 20:23 | 2015-05-04 | 22:39 | 0 | 0.094444 | 0 | 0 | O | N | SEFU | LINE A/R SUCCESSFUL ON B PH TO E FAULT AT WARDHA BUT A/R FAIL TO OPERATE AT IEPL END. | … | 05/419
45 | 705033 | ICT2_400/220kv_WARDHA | WRTS-I | 0 | 2015-05-04 | 20:45 | 2015-05-04 | 21:25 | 0 | 0.027778 | 0 | 0 | O | N | OMSU | OUTAGE AVAILED BY MSETCL FOR ISOLATION OF 400 KV WARDHA - WARORA # 2 MAIN BAY FOR ATTENDING OIL PRESSURE L/O ALONG WITH 400 KV BUS # 2, CONNECTED WITH 400 KV ICT # 2 AT WARDHA. | … | 5/412
46 | 705034 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | WRTS-I | 0 | 2015-05-04 | 23:51 | 2015-05-09 | 18:50 | 0 | 0 | 0 | 1900-01-03 18:59 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/433,NL-05/99 | 05/967,NL-05/238
47 | 705035 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-04 | 21:23 | 2015-05-06 | 17:24 | 0 | 0 | 0 | 1899-12-31 20:01 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/410 | 5/630 5/141
48 | 705036 | 400KV IEPL-MAUDA | WRTS-I | 0 | 2015-05-04 | 22:01 | 2015-05-04 | 22:52 | 0 | 0.035417 | 0 | 0 | O | N | OMSU | LINE TRIPPED DUE TO UNDER VOLTAGE AT MAUDA END | … | 5/423
49 | 705037 | 400kV WARDHA-MAUDA II | WRTS-I | 1 | 2015-05-04 | 22:00 | 2015-05-04 | 23:03 | 0.04375 | 0 | 0 | 0 | L | N | LEFT | LINE TRIPPED ON B PH TO E FAULT AT F/L= 12 KM FROM WARDHA. | .. | 05/424
50 | 705038 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-05 | 7:22 | 2015-05-08 | 16:36 | 0 | 0 | 0 | 1900-01-02 09:14 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/469 | 5/847
51 | 705039 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-05 | 7:23 | 2015-05-06 | 18:28 | 0 | 0 | 0 | 1899-12-31 11:05 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/470 | 5/643
52 | 705040 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-05 | 9:50 | 2015-05-05 | 13:09 | 0 | 0 | 0 | 0.13819 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/478 5/107 | 5/492 5/102
53 | 705041 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-05 | 9:53 | 2015-05-05 | 12:12 | 0 | 0 | 0 | 0.096528 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/479 | 5/497
54 | 705042 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-05-05 | 10:04 | 2015-05-09 | 18:32 | 0 | 0 | 0 | 1900-01-03 08:28 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/108 | 5/966
55 | 705043 | 765kV WARDHA - AURANGABAD(PG) I | WRTS-I | 0 | 2015-05-05 | 10:30 | 2015-05-05 | 10:40 | 0 | 0 | 0.0069444 | 0 | S | N | GOVC | LINE TRIPPED ON OVER VOLTAGE AT AURANGABAD | - | -
56 | 705044 | 765kV WARDHA - AURANGABAD(PG) I | WRTS-I | 0 | 2015-05-05 | 10:40 | 2015-05-21 | 15:10 | 0 | 0 | 0 | 1900-01-15 04:30 | D | N | LVRD | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | - | 05/2268,NL-05/663
57 | 705045 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-05 | 9:41 | 2015-05-05 | 12:16 | 0 | 0 | 0 | 0.10764 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/477 | 5/499
58 | 705046 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-05 | 9:41 | 2015-05-05 | 12:20 | 0 | 0 | 0 | 0.11042 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/477 | 5/498
59 | 705047 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-05 | 14:41 | 2015-05-05 | 17:30 | 0 | 0 | 0 | 0.11736 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/507 5/114 | 5/519 5/116
60 | 705048 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-05 | 18:28 | 2015-05-06 | 7:05 | 0 | 0 | 0 | 0.52569 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/524 | 5/565
61 | 705049 | 400kV RAIGARH-ROURKELA II | WRTS-I | 0 | 2015-05-06 | 5:12 | 2015-05-06 | 11:24 | 0.25833 | 0 | 0 | 0 | L | N | OSPT | OUTAGE AVAILED BY ER-II (ROURKELA) | WR/5/559 ER/5/155 NL/5/124 | 5/595 5/169 5/135
62 | 705050 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-06 | 8:06 | 2015-05-06 | 16:58 | 0 | 0 | 0 | 0.36944 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/569 5/128 | 5/623 5/139
63 | 705051 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-06 | 8:47 | 2015-05-08 | 15:58 | 0 | 0 | 0 | 1900-01-01 07:11 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/574 5/132 | 5/840, NL-5/200
64 | 705052 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | WRTS-I | 0 | 2015-05-06 | 9:44 | 2015-05-16 | 14:57 | 0 | 0 | 0 | 1900-01-09 05:13 | D | N | SCSD | H/T FOR CSD COMMISSIONING & FIRE FIGHTING WORKS AT SOLAPUR. | 5/583 | 5/1710
65 | 705053 | ICT2_400/220kv_RAIPUR | WRTS-I | 0 | 2015-05-06 | 11:10 | 2015-05-06 | 18:19 | 0 | 0 | 0 | 0.29792 | D | N | SCSD | H/T FOR NTAMC WORKS AT RAIPUR. | 5/587 | 5/640
66 | 705054 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-06 | 10:28 | 2015-05-06 | 17:15 | 0 | 0 | 0 | 0.28264 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/592 | 5/628
67 | 705055 | BUS REACTOR_400kV_125MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-06 | 14:58 | 2015-05-07 | 13:35 | 0.94236 | 0 | 0 | 0 | L | N | OSPT | OUTAGE AVAILED FOR AMP & TAN DELTA MEASUREMENT. | 5/612 | 5/718
68 | 705056 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-06 | 17:57 | 2015-05-07 | 5:55 | 0 | 0 | 0 | 0.49861 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/639 | 5/671
69 | 705057 | 765kV WARDHA - AURANGABAD(PG) II | WRTS-I | 2 | 2015-05-06 | 18:45 | 2015-05-06 | 19:18 | 0.022917 | 0 | 0 | 0 | L | N | LEFT | LINE TRIPPED ON B-PH TO E FAULT. F/L= 67KM FROM WARDHA & 248KM FROM A'BAD |  | 5/651 5/146
70 | 705058 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-06 | 19:08 | 2015-05-07 | 17:54 | 0 | 0 | 0 | 0.94861 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/649 5/145 | 5/752, NL-5/167
71 | 705059 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-07 | 8:19 | 2015-05-07 | 17:48 | 0 | 0 | 0 | 0.39514 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/681, NL-5/153 | 5/750, NL-5/166
72 | 705060 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-07 | 8:57 | 2015-05-08 | 16:36 | 0 | 0 | 0 | 1899-12-31 07:39 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/687
73 | 705061 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | WRTS-I | 0 | 2015-05-07 | 10:06 | 2015-05-08 | 17:43 | 0 | 0 | 0 | 1899-12-31 07:37 | D | N | SCSD | H/T FOR CSD COMMISSIONING WORKS AT SOLAPUR. | 5/694, NL-5/159
74 | 705062 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-07 | 10:18 | 2015-05-07 | 17:07 | 0 | 0 | 0 | 0.28403 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/697 | 5/747
75 | 705063 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-07 | 17:10 | 2015-05-08 | 6:57 | 0 | 0 | 0 | 0.57431 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/748 | 5/793
76 | 705064 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-07 | 9:09 | 2015-05-07 | 17:54 | 0 | 0 | 0 | 0.36458 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/686 | 5/754
77 | 705065 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-08 | 1:19 | 2015-05-08 | 18:57 | 0 | 0 | 0 | 0.73472 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/784, NL-5/186 | 5/863, NL-5/210
78 | 705066 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-08 | 6:56 | 2015-05-09 | 18:44 | 0 | 0 | 0 | 1899-12-31 11:48 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/795 | 5/968
79 | 705067 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-08 | 6:57 | 2015-05-08 | 16:24 | 0 | 0 | 0 | 0.39375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/796 | 5/846
80 | 705068 | ICT3_400/220kv_RAIPUR | WRTS-I | 0 | 2015-05-08 | 9:03 | 2015-05-08 | 20:22 | 0 | 0 | 0 | 0.47153 | D | N | SCSD | H/T FOR NTAMC WORKS AT RAIPUR. | 5/802 | 5/864
81 | 705069 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-08 | 17:49 | 2015-05-09 | 7:04 | 0 | 0 | 0 | 0.55208 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/853 | 5/875
82 | 705070 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-08 | 23:02 | 2015-05-09 | 17:13 | 0 | 0 | 0 | 0.75764 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/876, NL-5/214 | 5/954, NL-5/231
83 | 705071 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-09 | 7:52 | 2015-05-09 | 19:36 | 0 | 0 | 0 | 0.48889 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/900, NL-5/219
84 | 705072 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-09 | 11:00 | 2015-05-09 | 17:30 | 0 | 0 | 0 | 0.27083 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/918 | 5/959
85 | 705073 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-09 | 11:58 | 2015-05-09 | 16:58 | 0 | 0 | 0 | 0.20833 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/924 | 5/951
86 | 705074 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-09 | 12:03 | 2015-05-09 | 16:28 | 0 | 0 | 0 | 0.18403 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/925 5/225 | 5/946 5/228
87 | 705075 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-09 | 17:34 | 2015-05-10 | 9:18 | 0 | 0 | 0 | 0.65556 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/960 | 5/1017
88 | 705076 | 400kV BHADRAVATI-PARLI I | WRTS-I | 0 | 2015-05-09 | 17:47 | 2015-05-09 | 19:39 | 0 | 0.077778 | 0 | 0 | O | N | OMSU | LINE TRIPPED ON B-PH TO EARTH FAULT F/L=139.05 KM FROM BHADRAWATI. DURING ON LINE OPGW WORK.THIS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. FOR REPLACEMENT OF GI EARTHWIRE BY OPGW.LINE CHARGING ATTEMPTED BUT TRIPPED ON OVERVOLATGE AT BHADRAWATI END HENCE KEPT OUT ON VOLTAGE REGULATION THEN CHARGED FROM PARLI END. | 5/969 | 5/979
89 | 705077 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-09 | 17:34 | 2015-05-10 | 9:18 | 0 | 0 | 0 | 0.65556 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/960 | 5/1017
90 | 705078 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 1 | 2015-05-09 | 23:17 | 2015-05-09 | 23:34 | 0.011806 | 0 | 0 | 0 | L | N | SRET | B/R TRIPPED DUE TO BUCCHOLZ RELAY OPERATION. | … | 05/1063
91 | 705079 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-05-09 | 23:34 | 2015-05-10 | 18:30 | 0 | 0 | 0 | 0.78889 | D | N | SVRD | REACTOR WAS READY FOR CHARGING FOR KEPT OUT ON VOLATGE REGULATION DUE TO RAIN. | … | 05/1063
92 | 705080 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-10 | 9:02 | 2015-05-10 | 17:56 | 0 | 0 | 0 | 0.37083 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1014 NL-5/257 | 5/1056 NL-5/261
93 | 705081 | 400kV RAIPUR-BHADRAVATI III | WRTS-I | 0 | 2015-05-10 | 10:35 | 2015-05-10 | 11:22 | 0 | 0 | 0 | 0.032639 | D | N | LVRD | FOR TAKING LR IN SERVICE AT RAIPUR. | 5/1026 | 5/1031
94 | 705082 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-10 | 11:01 | 2015-05-10 | 17:29 | 0 | 0 | 0 | 0.26944 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1029 | 5/1053
95 | 705083 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-10 | 23:33 | 2015-05-13 | 17:32 | 0 | 0 | 0 | 1900-01-01 17:59 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1080 NL-5/270 | 05/1401, NL-05/375
96 | 705084 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-10 | 16:40 | 2015-05-11 | 9:46 | 0 | 0 | 0 | 0.7125 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1050 | 5/1100
97 | 705085 | 400kV RAIGARH-KOTRA PS I | WRTS-I | 0 | 2015-05-11 | 9:14 | 2015-05-11 | 18:55 | 0.40347 | 0 | 0 | 0 | L | N | OSPT | H/T FOR LINE AMP WORKS. | 5/1099 | 5/1159
98 | 705086 | BUS REACTOR_400kV_80MVAR_RAIPUR | WRTS-I | 0 | 2015-05-11 | 9:35 | 2015-05-11 | 18:17 | 0 | 0 | 0 | 0.3625 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1106 | 5/1156
99 | 705087 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-11 | 10:18 | 2015-05-11 | 16:36 | 0 | 0 | 0 | 0.2625 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1109 NL-5/278 | 5/1147 NL-5/294
100 | 705088 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-11 | 9:55 | 2015-05-11 | 20:48 | 0 | 0 | 0 | 0.45347 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1111 | 5/1171
101 | 705089 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-11 | 9:53 | 2015-05-11 | 16:38 | 0 | 0 | 0 | 0.28125 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1113 | 5/1148
102 | 705090 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-11 | 10:17 | 2015-05-11 | 17:48 | 0 | 0 | 0 | 0.31319 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1117 NL-5/283 | 5/1152 NL-5/295
103 | 705091 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-11 | 10:21 | 2015-05-11 | 20:51 | 0 | 0 | 0 | 0.4375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1118 | 5/1171
104 | 705092 | 400kV BHADRAVATI-PARLI I | WRTS-I | 0 | 2015-05-11 | 12:24 | 2015-05-11 | 20:17 | 0 | 0.32847 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY & FOR RECTIFICATION WORKS OF BROKEN EARTH WIRE AT LOC NO 411 | 5/1126 | 5/1165
105 | 705093 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-11 | 17:19 | 2015-05-12 | 08:27 | 0 | 0 | 0 | 0.63056 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1150 | 05/1209
106 | 705094 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-12 | 08:29 | 2015-05-12 | 18:38 | 0 | 0 | 0 | 0.42292 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1210, NL-05/309 | 05/1272, NL-05/335
107 | 705095 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-12 | 08:53 | 2015-05-13 | 01:07 | 0 | 0 | 0 | 0.67639 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1216 | 05/1312
108 | 705096 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-12 | 09:21 | 2015-05-12 | 13:15 | 0 | 0 | 0 | 0.1625 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1222, NL-05/313 | 05/1242, NL-05/319
109 | 705097 | 765kV D'JAIGARH-RANCHI | WRTS-I | 0 | 2015-05-12 | 13:53 | 2015-05-13 | 20:37 | 0 | 0 | 0 | 1899-12-31 06:44 | D | N | SCSD | OUTAGE AVAILED FOR ERECTION OF AUXILARY BUS FOR SPARE REACTOR AT DHARAMJAYGARH END. | 05/1244, NL-05/321, ER-05/413 | 05/1428, NL-05/382, ER-05/477
110 | 705098 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 2 | 2015-05-12 | 14:53 | 2015-05-12 | 15:10 | 0.011806 | 0 | 0 | 0 | L | N | LPPT | LINE TRIPPED ON R-B PH TO E FAULT,F/L-39.85 KM FROM MAPUSA END HEAVY RAINS & LIGHTNING OCCURRED IN THAT AREA.. | …. | ….
111 | 705099 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-12 | 15:10 | 2015-05-12 | 21:47 | 0 | 0.27569 | 0 | 0 | O | N | OMSU | LINE WAS READY FOR CHARGING FROM POWERGRID END,BUT LINE CHARGING WAS DELAYED AT MSETCL END. | …. | 05/1299
112 | 705100 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-12 | 15:25 | 2015-05-12 | 18:07 | 0 | 0 | 0 | 0.1125 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1254 | 05/1270
113 | 705101 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-13 | 03:39 | 2015-05-13 | 07:08 | 0 | 0 | 0 | 0.14514 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1314 | 05/1325
114 | 705102 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-13 | 06:24 | 2015-05-15 | 17:36 | 0 | 0 | 0 | 1900-01-01 11:12 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1320, NL-05/345 | 05/1619, NL-05/429
115 | 705103 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-13 | 07:05 | 2015-05-13 | 17:20 | 0 | 0 | 0 | 0.42708 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1327 | 05/1403
116 | 705104 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-13 | 07:05 | 2015-05-13 | 16:40 | 0 | 0 | 0 | 0.39931 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1328 | 05/1392
117 | 705105 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-13 | 09:31 | 2015-05-13 | 16:39 | 0 | 0 | 0 | 0.29722 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1343 | 05/1391
118 | 705106 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | WRTS-I | 0 | 2015-05-13 | 09:37 | 2015-05-13 | 17:20 | 0 | 0 | 0 | 0.32153 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1342, NL-05/351 | 05/1396, NL-05/372
119 | 705107 | 400KV RAIPUR-SIPAT II | WRTS-I | 0 | 2015-05-13 | 09:43 | 2015-05-13 | 22:33 | 0 | 0 | 0 | 0.53472 | D | N | SCSD | LINE H/T FOR NTAMC WORKS AT RAIPUR. | 05/1341 | 05/1435
120 | 705108 | ICT1_765/400kv_AURANGABAD | WRTS-I | 2 | 2015-05-13 | 10:05 | 2015-05-13 | 18:32 | 0.35208 | 0 | 0 | 0 | L | N | SICT | ICT TRIPPED DUE TO R PHASE BUCHHOLZ RELAY OPERATION. | …. | 05/1414,NL-05/378
121 | 705109 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-13 | 11:00 | 2015-05-13 | 17:06 | 0 | 0 | 0 | 0.25417 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1360 | 05/1397
122 | 705110 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-13 | 11:01 | 2015-05-13 | 16:38 | 0 | 0 | 0 | 0.23403 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1357 | 05/1390
123 | 705111 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-13 | 11:08 | 2015-05-13 | 16:20 | 0 | 0 | 0 | 0.21667 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1361,NL-05/359 | 05/1386,NL-05/369
124 | 705112 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-05-13 | 11:12 | 2015-05-16 | 16:50 | 0 | 0 | 0 | 1900-01-02 05:38 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1358 | 5/1722
125 | 705113 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-13 | 11:26 | 2015-05-13 | 17:41 | 0 | 0 | 0 | 0.26042 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1359 | 05/1398
126 | 705114 | BUS REACTOR_765kV_330MVAR_WARDHA | WRTS-I | 0 | 2015-05-13 | 11:47 | 2015-05-13 | 16:26 | 0 | 0 | 0 | 0.19375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1362,NL-05/360 | 05/1387,NL-05/370
127 | 705115 | ICT2_765/400kv_AURANGABAD | WRTS-I | 2 | 2015-05-13 | 17:10 | 2015-05-13 | 17:45 | 0.024306 | 0 | 0 | 0 | L | N | SICT | ICT TRIPPED DUE TO B PHASE BUCHHOLZ RELAY OPERATION | …. | 05/1406,NL-05/376
128 | 705116 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-13 | 17:42 | 2015-05-14 | 8:14 | 0 | 0 | 0 | 0.60556 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1409 | 5/1463
129 | 705117 | ICT1_765/400kv_AURANGABAD | WRTS-I | 0 | 2015-05-13 | 18:32 | 2015-05-13 | 20:58 | 0.10139 | 0 | 0 | 0 | L | N | OSFT | H/T DUE TO HEAVY SPARKING ON SPARE ISOLATOR. | …. | 05/1431,NL-05/383
130 | 705118 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-14 | 9:20 | 2015-05-15 | 18:27 | 0 | 0 | 0 | 1899-12-31 09:07 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1474, NL-05/387 | 05/1630, NL-05/431
131 | 705119 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-14 | 10:48 | 2015-05-14 | 17:18 | 0 | 0 | 0 | 0.27083 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1487, NL-05/391 | 05/1519, NL-05/400
132 | 705120 | ICT2_400/220kv_PUNE | WRTS-I | 0 | 2015-05-14 | 16:50 | 2015-05-14 | 21:55 | 0 | 0 | 0 | 0.21181 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 5/1516 | 5/1541
133 | 705121 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-14 | 17:11 | 2015-05-15 | 6:53 | 0 | 0 | 0 | 0.57083 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1518 | 5/1557
134 | 705122 | ICT1_400/220kv_PUNE | WRTS-I | 0 | 2015-05-14 | 0:19 | 2015-05-14 | 21:55 | 0 | 0 | 0 | 0.9 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 5/1548 | 5/1541
135 | 705123 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-14 | 9:20 | 2015-05-15 | 18:27 | 0 | 0 | 0 | 1899-12-31 09:07 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1474, NL-05/387 | 05/1630, NL-05/431
136 | 705124 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | WRTS-I | 0 | 2015-05-14 | 11:32 | 2015-05-15 | 18:34 | 0 | 0 | 0 | 1899-12-31 07:02 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1489 | 5/1634
137 | 705125 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-14 | 17:11 | 2015-05-15 | 6:53 | 0 | 0 | 0 | 0.57083 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1518 | 5/1557
138 | 705126 | ICT1_400/220kv_PUNE | WRTS-I | 0 | 2015-05-15 | 0:19 | 2015-05-18 | 10:57 | 0 | 0 | 0 | 1900-01-02 10:38 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 5/1548 | 5/1865
139 | 705127 | 400kV RAIPUR-SIPAT I | WRTS-I | 0 | 2015-05-15 | 9:07 | 2015-05-15 | 19:38 | 0 | 0 | 0 | 0.43819 | D | N | SCSD | FOR NTAMC WORKS AT RAIPUR END | 5/1570 | 5/1640
140 | 705128 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-15 | 10:07 | 2015-05-15 | 17:32 | 0 | 0 | 0 | 0.30903 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1579 | 5/1622
141 | 705129 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-15 | 10:03 | 2015-05-15 | 16:15 | 0 | 0 | 0 | 0.25833 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1580 | 5/1616
142 | 705130 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | WRTS-I | 0 | 2015-05-15 | 10:19 | 2015-05-15 | 17:06 | 0 | 0 | 0 | 0.28264 | D | N | SCSD | FOR CSD COMMISSIONING WORKS | 05/1583, NL-05/417 | 05/1618, NL-05/428
143 | 705131 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-15 | 11:48 | 2015-05-17 | 15:17 | 0 | 0 | 0 | 1900-01-01 03:29 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/1594, NL-05/420 | 5/1799 NL-5/478
144 | 705132 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-15 | 12:07 | 2015-05-15 | 18:13 | 0 | 0 | 0 | 0.25417 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1597 | 5/1631
145 | 705133 | 400KV RAIPUR-WARDHA II | WRTS-I | 0 | 2015-05-15 | 13:49 | 2015-05-15 | 13:49 | 0 | 0 | 0 | 0 | L | N | LART | LINE A/R FROM BOTH END SUCESSFULLY ON B-PH TO EARTH FAULT. F/L=79.2KM FROM WARDHA. | --- | ---
146 | 705134 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-15 | 16:19 | 2015-05-16 | 6:34 | 0 | 0 | 0 | 0.59375 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1615 | 5/1673
147 | 705135 | 220kV KORBA(EAST)-BUDDHIPADAR III | WRTS-I | 1 | 2015-05-15 | 22:00 | 2015-05-15 | 22:10 | 0.0069444 | 0 | 0 | 0 | L | N | LEFT | LINE TRIPPED DUE TO EARTH FAULT. F.D 140 KM FROM KORBA,& 56 KM FROM BUDIPADAR
148 | 705136 | 220kV KORBA(EAST)-BUDDHIPADAR III | WRTS-I | 0 | 2015-05-15 | 22:10 | 2015-05-16 | 22:17 | 0 | 0 | 0 | 1899-12-31 00:07 | D | N | LVRD | KEPT UN CHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 5/1748 5/460 5/611
149 | 705137 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-16 | 6:30 | 2015-05-17 | 17:29 | 0 | 0 | 0 | 1899-12-31 10:59 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1671 5/438 | 5/1812 NL-5/482
150 | 705138 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-16 | 9:37 | 2015-05-16 | 16:55 | 0 | 0 | 0 | 0.30417 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1687 | 5/1721
151 | 705139 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-16 | 9:40 | 2015-05-16 | 16:53 | 0 | 0 | 0 | 0.30069 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1690 5/443 | 5/1724 5/454
152 | 705140 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-16 | 10:04 | 2015-05-16 | 16:48 | 0 | 0 | 0 | 0.28056 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1691 | 5/1720
153 | 705141 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | WRTS-I | 0 | 2015-05-16 | 10:26 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-14 13:34 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1692 5/445 | -
154 | 705142 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-16 | 16:54 | 2015-05-16 | 17:59 | 0 | 0 | 0 | 0.045139 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1718 | 5/1730
155 | 705143 | 765KV DURG PS - D'JAIGARH | WRTS-I | 0 | 2015-05-16 | 10:10 | 2015-05-22 | 21:28 | 0 | 0 | 0 | 1900-01-05 11:18 | D | N | LCSD | KEPT OUT AS WRLDC INSTRUCTIONS FOR LINE CROSSING WORKS OF 765KV CHAMPA LINE | 5/1685 5/442 | 05/2434,NL-05/684
156 | 705144 | ICT1_400/220kv_MAPUSA | WRTS-I | 0 | 2015-05-16 | 16:01 | 2015-05-16 | 22:57 | 0 | 0 | 0.28889 | 0 | S | N | LNCC | TRIPPED DUE TO R PAHSE ISOLATOR DAMAGED ON 400 KV SIDE DUE TO HEAVY WIND & RAIN NATURAL CALAMITY. | - | 5/1752
157 | 705145 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-16 | 18:02 | 2015-05-17 | 16:01 | 0 | 0 | 0.91597 | 0 | S | N | SNCC | LINE HAND TRIPPED DUE TO Y PHASE WAVETRAP BPI FAILURE AT MAPUSA DUE TO HEAVY RAIN & THUNDER NATURAL CALAMITY | - | 5/1802
158 | 705146 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-17 | 9:42 | 2015-05-17 | 16:02 | 0 | 0 | 0 | 0.26389 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1778 | 5/1803
159 | 705147 | ICT1_765/400kv_AURANGABAD | WRTS-I | 0 | 2015-05-17 | 13:42 | 2015-05-17 | 17:34 | 0.16111 | 0 | 0 | 0 | L | N | OMST | H/T FOR REPLACING ISOLATOR ARMS OF SPARE UNIT. | 5/1793 NL-5/474 | 5/1811 NL-5/481
160 | 705148 | 400kV BALCO-BIRSINGHPUR | WRTS-I | 0 | 2015-05-17 | 16:01 | 2015-05-17 | 17:17 | 0 | 0.052778 | 0 | 0 | O | N | SEFU | LINE TRIPPED DUE TO A/R UNSUCCESSFUL AT BOTH ENDS ON R PH TO E FAULT,FL- 137 KM FROM BIRSINGHPUR END. | ,…… | 5/1806
161 | 705149 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-17 | 16:09 | 2015-05-18 | 09:16 | 0 | 0 | 0 | 0.71319 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1804 | 5/1856
162 | 705150 | ICT2_765/400kv_AURANGABAD | WRTS-I | 3 | 2015-05-17 | 17:33 | 2015-05-17 | 18:12 | 0.52708 | 0 | 0 | 0 | L | N | SRMT | ICT TRIPPED ON B PHASE BUCHHOLZ RELAY MALOPERATION. | ….. | 5/1815 NL-5/484
163 | 705151 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-18 | 6:28 | 2015-05-18 | 17:09 | 0 | 0 | 0 | 0.44514 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1843 NL-5/491 | 5/1902 NL-5/513
164 | 705152 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-18 | 7:14 | 2015-05-18 | 17:38 | 0 | 0 | 0 | 0.43333 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1846 NL-5/493 | 5/1905 NL-5/514
165 | 705153 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-18 | 9:23 | 2015-05-18 | 18:03 | 0 | 0 | 0 | 0.36111 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 5/1857 NL-5/498 | 5/1912 NL-5/518
166 | 705154 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-18 | 9:36 | 2015-05-18 | 16:41 | 0 | 0 | 0 | 0.29514 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1861 | 5/1899
167 | 705155 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-18 | 9:40 | 2015-05-18 | 16:39 | 0 | 0 | 0 | 0.29097 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 5/1862 | 5/1893
168 | 705156 | ICT2_400/220kv_PUNE | WRTS-I | 0 | 2015-05-18 | 10:58 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-12 13:02 | D | N | SPRD | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | 5/1867
169 | 705157 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-05-18 | 11:23 | 2015-05-18 | 17:43 | 0 | 0 | 0 | 0.26389 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1872 | 5/1904
170 | 705158 | 400kV RAIGARH-KOTRA PS II | WRTS-I | 0 | 2015-05-18 | 11:20 | 2015-05-18 | 19:00 | 0.31944 | 0 | 0 | 0 | L | N | OSPT | H/T FOR AMP WORKS AT KOTRA | 5/1873 | 5/1915
171 | 705159 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-18 | 11:48 | 2015-05-18 | 16:27 | 0 | 0 | 0 | 0.19375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1876 | 5/1891
172 | 705160 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-18 | 11:48 | 2015-05-18 | 16:31 | 0 | 0 | 0 | 0.19653 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1877 | 5/1892
173 | 705161 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-18 | 11:54 | 2015-05-18 | 17:42 | 0 | 0 | 0 | 0.24167 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1878 NL-5/503 | 5/1906 NL-5/515
174 | 705162 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-18 | 22:36 | 2015-05-19 | 17:52 | 0 | 0 | 0 | 0.80278 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1936 NL-5/527 | 5/2025 5/553
175 | 705163 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-19 | 8:18 | 2015-05-19 | 15:38 | 0 | 0 | 0 | 0.30556 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1966 5/530 | 5/2002 5/544
176 | 705164 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-19 | 8:25 | 2015-05-19 | 17:00 | 0 | 0 | 0 | 0.35764 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1967
177 | 705165 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-19 | 8:26 | 2015-05-19 | 17:04 | 0 | 0 | 0 | 0.35972 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1968 | 5/2014
178 | 705166 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-19 | 8:23 | 2015-05-19 | 17:18 | 0 | 0 | 0 | 0.37153 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1969 | 5/2018
179 | 705167 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-19 | 9:27 | 2015-05-19 | 17:52 | 0 | 0 | 0 | 0.35069 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1974 5/533 | 5/2026 5/554
180 | 705168 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-19 | 9:32 | 2015-05-19 | 13:10 | 0 | 0 | 0 | 0.15139 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1976 | 5/1992
181 | 705169 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-19 | 10:04 | 2015-05-19 | 17:41 | 0 | 0 | 0 | 0.31736 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1980 | 5/2022
182 | 705170 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-19 | 11:22 | 2015-05-19 | 18:13 | 0 | 0 | 0 | 0.28542 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1985 5/539 | 5/2030 5/555
183 | 705171 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-05-19 | 11:31 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-11 12:29 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/1986
184 | 705172 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-19 | 16:42 | 2015-05-20 | 08:38 | 0 | 0 | 0 | 0.66389 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2010 | 05/2100
185 | 705173 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-19 | 22:06 | 2015-05-20 | 16:51 | 0 | 0 | 0 | 0.78125 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2062 5/579 | 05/2161,NL-05/617
186 | 705174 | 400KV RAIPUR-WARDHA II | WRTS-I | 0 | 2015-05-20 | 08:40 | 2015-05-20 | 12:00 | 0 | 0 | 0.13889 | 0 | S | N | LMAC | LINE TRIPPED DUE TO FIRE ON COTTON NEAR TO LINE ON R PHASE TO E FAULT,FC-9.8 KA,FL-22.5 KM FROM WARDHA AND FL-339KM FROM RAIPUR END. | --- | 05/2142
187 | 705175 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-20 | 08:53 | 2015-05-20 | 16:17 | 0 | 0 | 0 | 0.30833 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2108 | 05/2156
188 | 705176 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-20 | 08:56 | 2015-05-20 | 17:15 | 0 | 0 | 0 | 0.34653 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2109 | 05/2168
189 | 705177 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-20 | 09:07 | 2015-05-20 | 18:25 | 0 | 0 | 0 | 0.3875 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2111,NL-05/588 | 05/2174,NL-05/620
190 | 705178 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-20 | 09:31 | 2015-05-20 | 15:27 | 0 | 0 | 0 | 0.24722 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2118,NL-05/593 | 05/2149,NL-05/613
191 | 705179 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-20 | 09:31 | 2015-05-20 | 16:17 | 0 | 0 | 0 | 0.28194 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2119 | 05/2153
192 | 705180 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-20 | 09:46 | 2015-05-21 | 16:55 | 0 | 0 | 0 | 1899-12-31 07:09 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2121,NL-05/595 | 05/2287,NL-05/671
193 | 705181 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-20 | 09:50 | 2015-05-20 | 16:45 | 0 | 0 | 0 | 0.28819 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2123,NL-05/597 | 05/2160,NL-05/616
194 | 705182 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-20 | 10:19 | 2015-05-20 | 16:46 | 0 | 0 | 0 | 0.26875 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2128 | 05/2165
195 | 705183 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-20 | 10:20 | 2015-05-20 | 16:20 | 0 | 0 | 0 | 0.25 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2119 | 05/2155
196 | 705184 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-20 | 10:22 | 2015-05-20 | 16:48 | 0 | 0 | 0 | 0.26806 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2130 | 05/2162
197 | 705185 | BUS REACTOR_400kV_125MVAR_BHATAPARA | WRTS-I | 0 | 2015-05-20 | 10:23 | 2015-05-20 | 18:51 | 0.35278 | 0 | 0 | 0 | L | N | OSPT | H/T FOR AMP WORKS | 05/2126 | 05/2179
198 | 705186 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-20 | 17:57 | 2015-05-20 | 20:11 | 0 | 0 | 0 | 0.093056 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2171 | 05/2185
199 | 705187 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-21 | 06:20 | 2015-05-21 | 17:10 | 0 | 0 | 0 | 0.45139 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2205 | 05/2289
200 | 705188 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-21 | 06:24 | 2015-05-21 | 16:13 | 0 | 0 | 0 | 0.40903 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2206,NL-05/634 | 05/2277,NL-05/668
201 | 705189 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-21 | 06:24 | 2015-05-21 | 16:26 | 0 | 0 | 0 | 0.41806 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2207 | 05/2279
202 | 705190 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-21 | 7:21 | 2015-05-21 | 16:20 | 0 | 0 | 0 | 0.37431 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2218 | 5/2278
203 | 705191 | BUS REACTOR_400kV_125MVAR_SEONI | WRTS-I | 0 | 2015-05-21 | 9:30 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-09 14:30 | D | N | SCSD | H/T FOR FIRE FIGHTING WORKS | 05/2222
204 | 705192 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-21 | 8:52 | 2015-05-21 | 17:18 | 0 | 0 | 0 | 0.35139 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2226 | 5/2290
205 | 705193 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-21 | 8:57 | 2015-05-21 | 16:08 | 0 | 0 | 0 | 0.29931 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2227 | 5/2275
206 | 705194 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-21 | 9:03 | 2015-05-21 | 14:12 | 0 | 0 | 0 | 0.21458 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2228,NL-05/637 | 05/2264,NL-05/660
207 | 705195 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-21 | 9:30 | 2015-05-21 | 17:01 | 0 | 0 | 0 | 0.31319 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2233,NL-05/638 | 05/2286,NL-05/670
208 | 705196 | 400kV KSK-RKKML III | WRTS-I | 0 | 2015-05-21 | 9:52 | 2015-05-21 | 17:35 | 0 | 0 | 0 | 0.32153 | D | N | OSPD | H/T FOR RELAY REPLACEMENT WORKS AT RKKML END | 5/2239 | 5/2281
209 | 705197 | 400kV RKKML-RAIGARH III | WRTS-I | 0 | 2015-05-21 | 9:50 | 2015-05-21 | 17:22 | 0 | 0 | 0 | 0.31389 | D | N | OSPD | H/T FOR RELAY REPLACEMENT WORKS AT RKKML END | 5/2238 | 5/2282
210 | 705198 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-21 | 9:50 | 2015-05-21 | 16:13 | 0 | 0 | 0 | 0.26597 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2243,NL-05/643 | 05/2276,NL-05/667
211 | 705199 | BUS REACTOR_765kV_240MVAR_BILASPUR | WRTS-I | 0 | 2015-05-21 | 10:14 | 2015-05-23 | 19:12 | 0 | 0 | 0 | 1900-01-01 08:58 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2244,NL-05/644 | 5/2534 5/715
212 | 705200 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | WRTS-I | 0 | 2015-05-21 | 14:44 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-09 09:16 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2267,NL-05/662
213 | 705201 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-21 | 9:20 | 2015-05-21 | 16:05 | 0 | 0 | 0 | 0.28125 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2234 | 5/2274
214 | 705202 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-21 | 18:05 | 2015-05-21 | 18:15 | 0 | 0 | 0.0069444 | 0 | S | N | GOVC | LINE TRIPPED DUE TO OVER VOLTAGE AT DURG PS END
215 | 705203 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-21 | 18:15 | 2015-05-22 | 16:23 | 0 | 0 | 0 | 0.92222 | D | N | LVRD | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 05/2409,NL-05/680
216 | 705204 | 220kV KORBA(EAST)-BUDDHIPADAR III | WRTS-I | 0 | 2015-05-21 | 18:12 | 2015-05-21 | 20:20 | 0 | 0.088889 | 0 | 0 | O | N | OMSU | LINE TRIPPED DUE TO PROBLEM AT BUDIPADAR S/S |  | 05/2317, NL-05/654, 5/822
217 | 705205 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-22 | 9:01 | 2015-05-22 | 17:53 | 0 | 0 | 0 | 0.36944 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2345,NL-05/661 | 05/2396,NL-05/677
218 | 705206 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-22 | 9:04 | 2015-05-22 | 16:53 | 0 | 0 | 0 | 0.32569 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2346 | 5/2403
219 | 705207 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-22 | 9:14 | 2015-05-23 | 17:04 | 0 | 0 | 0 | 1899-12-31 07:50 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2347 | 5/2514
220 | 705208 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-22 | 9:46 | 2015-05-22 | 16:34 | 0 | 0 | 0 | 0.28333 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2357 | 5/2399
221 | 705209 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-22 | 9:50 | 2015-05-22 | 16:51 | 0 | 0 | 0 | 0.29236 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2358 | 5/2402
222 | 705210 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-22 | 10:00 | 2015-05-22 | 13:38 | 0 | 0 | 0 | 0.15139 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2359,NL-05/663 | 05/2387,NL-05/672
223 | 705211 | ICT2_400/220kv_BAHATAPARA | WRTS-I | 0 | 2015-05-22 | 10:03 | 2015-05-22 | 18:45 | 0 | 0 | 0 | 0.3625 | D | N | SCSD | H/T FOR NTAMC WORKS | 5/2361 | 5/2417
224 | 705212 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-22 | 10:32 | 2015-05-22 | 14:05 | 0 | 0 | 0 | 0.14792 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2369,NL-05/665 | 05/2386,NL-05/671
225 | 705213 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-22 | 12:04 | 2015-05-22 | 13:33 | 0 | 0 | 0 | 0.061806 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2400,NL-05/677 | 05/2388,NL-05/673
226 | 705214 | 765kV WARDHA - AURANGABAD(PG) II | WRTS-I | 0 | 2015-05-22 | 16:44 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-08 07:16 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2379,NL-05/670
227 | 705215 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-22 | 17:38 | 2015-05-23 | 7:30 | 0 | 0 | 0 | 0.57778 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2406 | 5/2450
228 | 705216 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-22 | 18:03 | 2015-05-22 | 18:13 | 0 | 0 | 0.0069444 | 0 | S | N | GOVC | LINE TRIPPED DUE TO OVER VOLTAGE AT DURG PS END
229 | 705217 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-22 | 18:13 | 2015-05-26 | 1:58 | 0 | 0 | 0 | 1900-01-02 07:45 | D | N | LVRD | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2429,NL-05/681 | 5/2761 NL-5/779
230 | 705218 | 400kV BHADRAVATI-PARLI I | WRTS-I | 0 | 2015-05-23 | 9:25 | 2015-05-23 | 17:56 | 0 | 0.35486 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 5/2460 | 5/2520
231 | 705219 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-23 | 9:27 | 2015-05-23 | 17:05 | 0 | 0 | 0 | 0.31806 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2466 5/692 | 5/2516 5/707
232 | 705220 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-23 | 9:57 | 2015-05-23 | 17:19 | 0 | 0 | 0 | 0.30694 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2474 | 5/2519
233 | 705221 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-23 | 9:24 | 2015-05-23 | 16:30 | 0 | 0 | 0 | 0.29583 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2465 | 5/2513
234 | 705222 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-23 | 9:39 | 2015-05-23 | 16:57 | 0 | 0 | 0 | 0.30417 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2469 | 5/2515
235 | 705223 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-23 | 9:59 | 2015-05-23 | 17:12 | 0 | 0 | 0 | 0.30069 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2473 5/694 | 5/2516 5/707
236 | 705224 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-23 | 9:56 | 2015-05-23 | 18:13 | 0 | 0 | 0 | 0.34514 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2475 5/695 | 5/2526 5/712
237 | 705225 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-24 | 16:03 | 2015-05-24 | 23:16 | 0 | 0 | 0 | 0.30069 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2600 | 5/2638
238 | 705226 | 400kV DHARIWAL TPP-PARLI II | WRTS-I | 0 | 2015-05-24 | 10:17 | 2015-05-24 | 17:57 | 0 | 0.31944 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 5/2575 | 5/2605
239 | 705227 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | WRTS-I | 1 | 2015-05-24 | 20:48 | 2015-05-24 | 21:10 | 0.015278 | 0 | 0 | 0 | L | N | SRET | REACTOR TRIPPED ON DIFFERENTIAL PROTECTION OPERATION AT SOLAPUR END | … | 5/2629 NL-5/745
240 | 705228 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-25 | 7:17 | 2015-05-26 | 02:34 | 0 | 0 | 0 | 0.80347 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2658 NL-5/753 | 5/2770 NL-5/784
241 | 705229 | 400kV BHADRAVATI-DHARIWAL TPP II | WRTS-I | 0 | 2015-05-25 | 8:18 | 2015-05-25 | 19:48 | 0 | 0.47917 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 5/2661 | 5/2746
242 | 705230 | 400kV DHARIWAL TPP-PARLI II | WRTS-I | 0 | 2015-05-25 | 8:20 | 2015-05-25 | 19:58 | 0 | 0.48472 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 5/2662 | 5/2747
243 | 705231 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-25 | 8:52 | 2015-05-29 | 18:09 | 0 | 0 | 0 | 1900-01-03 09:17 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2668 NL- 5/755 | 05/3253,NL-05/904
244 | 705232 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-25 | 9:37 | 2015-05-25 | 18:11 | 0 | 0 | 0 | 0.35694 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2672 | 5/2729
245 | 705233 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-25 | 10:01 | 2015-05-25 | 18:20 | 0 | 0 | 0 | 0.34653 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2678 | 5/2732
246 | 705234 | ICT2_765/400kv_KOTRA PS | WRTS-I | 0 | 2015-05-25 | 10:20 | 2015-05-25 | 19:48 | 0.39444 | 0 | 0 | 0 | L | N | OSPT | H/T FOR AMP WORKS | 5/2680 NL- 5/762 | 5/2744 NL- 5/774
247 | 705235 | ICT1_400/220kv_BAHATAPARA | WRTS-I | 0 | 2015-05-25 | 10:40 | 2015-05-25 | 18:21 | 0.32014 | 0 | 0 | 0 | L | N | OSPT | H/T FOR AMP WORKS | 5/2682 | 5/2730
248 | 705236 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-25 | 10:43 | 2015-05-25 | 19:26 | 0 | 0 | 0 | 0.36319 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2683 NL- 5/761 | 5/2733 NL-5/770
249 | 705237 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-25 | 11:00 | 2015-05-25 | 18:52 | 0 | 0 | 0 | 0.32778 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2684 | 5/2738
250 | 705238 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-25 | 14:33 | 2015-05-25 | 16:44 | 0 | 0 | 0 | 0.090972 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2703 NL- 5/764 | 5/2715 NL- 5/767
251 | 705239 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-25 | 14:35 | 2015-05-25 | 18:44 | 0 | 0 | 0 | 0.17292 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2704 | 5/2734
252 | 705240 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-25 | 9:58 | 2015-05-25 | 16:15 | 0 | 0 | 0 | 0.26181 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2679 | 5/2714
253 | 705241 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-25 | 17:20 | 2015-05-26 | 08:20 | 0 | 0 | 0 | 0.625 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2718 | 05/2780
254 | 705242 | BUS REACTOR_400kV_125MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-19 | 15:50 | 2015-05-25 | 22:11 | 0 | 0 | 0 | 1900-01-05 06:21 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2004 | 5/2756
255 | 705243 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-26 | 09:05 | 2015-05-26 | 19:16 | 0 | 0 | 0 | 0.42431 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2787,NL-05/789 | 05/2851,NL-05/807
256 | 705244 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-26 | 09:35 | 2015-05-26 | 17:08 | 0 | 0 | 0 | 0.31458 | D | N | SCSD | OCC APPROVED OUTAGE AVAILED FOR CSD COMMISSIONING WORKS. | 05/2790 | 05/2839
257 | 705245 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-26 | 09:59 | 2015-05-26 | 18:36 | 0 | 0 | 0 | 0.35903 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2796 | 05/2850
258 | 705246 | 400kV BHADRAVATI-PARLI I | WRTS-I | 0 | 2015-05-26 | 10:23 | 2015-05-26 | 20:27 | 0 | 0.41944 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 05/2798 | 05/2864
259 | 705247 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-26 | 10:33 | 2015-05-27 | 18:47 | 0 | 0 | 0 | 1899-12-31 08:14 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2803 | 05/2988
260 | 705248 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-26 | 10:34 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-04 13:26 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2804 | ---
261 | 705249 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-26 | 10:35 | 2015-05-26 | 17:20 | 0 | 0 | 0 | 0.28125 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2805 | 05/2840
262 | 705250 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-26 | 10:47 | 2015-05-26 | 17:25 | 0 | 0 | 0 | 0.27639 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2802,NL-05/792 | 05/2842,NL-05/802
263 | 705251 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-26 | 17:16 | 2015-05-27 | 08:29 | 0 | 0 | 0 | 0.63403 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2841 | 05/2899
264 | 705252 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-27 | 08:51 | 2015-05-27 | 17:56 | 0 | 0 | 0 | 0.37847 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2904 | 05/2975
265 | 705253 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-27 | 09:00 | 2015-05-27 | 17:43 | 0 | 0 | 0 | 0.36319 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2906 | 05/2976
266 | 705254 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-27 | 09:05 | 2015-05-27 | 22:12 | 0 | 0 | 0 | 0.54653 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2909,NL-05/820 | 05/3012,NL-05/852
267 | 705255 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-27 | 09:06 | 2015-05-27 | 17:16 | 0 | 0 | 0 | 0.34028 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2907,NL-05/819 | 05/2972,NL-05/839
268 | 705256 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | WRTS-I | 0 | 2015-05-27 | 09:08 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-03 14:52 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2908 | ---
269 | 705257 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-27 | 09:51 | 2015-05-27 | 17:57 | 0 | 0 | 0 | 0.3375 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2916 | 05/2978
270 | 705258 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-27 | 09:52 | 2015-05-27 | 18:43 | 0 | 0 | 0 | 0.36875 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2915 | 05/2979
271 | 705259 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-27 | 10:32 | 2015-05-27 | 16:59 | 0 | 0 | 0 | 0.26875 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2924,NL-05/826 | 05/2970,NL-05/838
272 | 705260 | 400KV RANCHI-SIPAT I | WRTS-I | 0 | 2015-05-27 | 13:45 | 2015-05-27 | 19:51 | 0 | 0 | 0 | 0.25417 | D | N | OSFD | EMERGENCY OUTAGE AVAILED BY NTPC SIPAT FOR L/R OTI REPLACEMENT WORK. | 05/2946, NL-05/832, ER-05/1044 | 05/2995, NL-05/847, ER-05/1055
273 | 705261 | 765kV DURG PS -WARDHA_2 | WRTS-I | 2 | 2015-05-27 | 17:03 | 2015-05-27 | 17:13 | 0.0069444 | 0 | 0 | 0 | L | N | LEFT | LINE TRIPPED ON R PH TO E FAULT,FC- 7.6 KA,FL- 53.3 KM FROM WARDHA END. | --- | ---
274 | 705262 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-27 | 17:13 | 2015-05-28 | 15:08 | 0 | 0 | 0 | 0.91319 | D | N | LVRD | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | --- | 05/3089,NL-05/868
275 | 705263 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-27 | 18:13 | 2015-05-28 | 06:31 | 0 | 0 | 0 | 0.5125 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/2982 | 05/3031
276 | 705264 | 400kV KORBA-MAHAN | WRTS-I | 0 | 2015-05-27 | 23:17 | 2015-05-27 | 23:32 | 0 | 0.010417 | 0 | 0 | O | N | SEFU | LINE TRIPPED DUE TO FAULT IN R PHASE BUSHING OF L/R AT KORBA END, AS ON R PH TO E FAULT,Z2 FAULT,FC- 1.704 KA,FL- 207.3 KM FROM MAHAN END. | --- | ---
277 | 705265 | 400kV KORBA-MAHAN | WRTS-I | 0 | 2015-05-27 | 23:17 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 1900-01-03 00:43 | D | N | GOMD | LINE UNABLE TO RESTORED AFTER OUTAGE DUE TO FAILURE OF REACTOR BUSHING AT KORBA NTPC END. | --- | ---
278 | 705266 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-28 | 06:27 | 2015-05-28 | 16:49 | 0 | 0 | 0 | 0.43194 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3032,NL-05/855 | 05/3104,NL-05/871
279 | 705267 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-05-28 | 06:37 | 2015-05-28 | 21:10 | 0 | 0 | 0 | 0.60625 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3033 | 5/3145
280 | 705268 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-28 | 7:53 | 2015-05-28 | 17:24 | 0 | 0 | 0 | 0.39653 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3039,NL-05/858 | 05/3113,NL-05/872
281 | 705269 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-28 | 7:56 | 2015-05-30 | 1:29 | 0 | 0 | 0 | 1899-12-31 17:33 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3040,NL-05/859 | 05/3290,NL-05/917
282 | 705270 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-28 | 8:02 | 2015-05-29 | 18:20 | 0 | 0 | 0 | 1899-12-31 10:18 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3042 | 5/3255
283 | 705271 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-28 | 8:35 | 2015-05-28 | 16:12 | 0 | 0 | 0 | 0.31736 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3045 | 5/3102
284 | 705272 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-05-28 | 8:56 | 2015-05-28 | 16:23 | 0 | 0 | 0 | 0.31042 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3051,NL-05/862 | 05/3103,NL-05/870
285 | 705273 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-05-28 | 8:57 | 2015-05-28 | 17:21 | 0 | 0 | 0 | 0.35 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3052 | 5/3112
286 | 705274 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-05-28 | 11:16 | 2015-05-28 | 18:15 | 0 | 0 | 0 | 0.29097 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3072 | 5/3130
287 | 705275 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | WRTS-I | 0 | 2015-05-28 | 15:49 | 2015-05-28 | 19:26 | 0.15069 | 0 | 0 | 0 | L | N | OMST | OUTAGE AVAILED FOR TIGHTINING OF JUMPERS IN LINE | 5/3089 | 5/3138
288 | 705276 | 765kV PUNE(GIS)-SOLAPUR | WRTS-I | 1 | 2015-05-28 | 16:00 | 2015-05-28 | 16:10 | 0.0069444 | 0 | 0 | 0 | L | N | LEFT | LINE TRIPPED ON R-PH TO EARTH FAULTF/L- 42 KM FROM SOLAPUR END 234 KM FROM PUNE END.
289 | 705277 | 765kV PUNE(GIS)-SOLAPUR | WRTS-I | 0 | 2015-05-28 | 16:10 | 2015-05-29 | 8:01 | 0 | 0 | 0 | 0.66042 | D | N | LVRD | LLINE KEPT OUT AFTER OUTAGE AS PER WRLDC INSTRUCTION OF WRLDC. THERE IS NO PERMANENT FAULT IN LINE AS LINE WAS SUCCESSFULLY CHARGED IN EARLY MORNING ON 29/05/15. |  | 05/3193,NL-05/890
290 | 705278 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-28 | 17:29 | 2015-05-29 | 6:49 | 0 | 0 | 0 | 0.55556 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION
291 | 705279 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-26 | 10:34 | 2015-05-28 | 18:10 | 0 | 0 | 0 | 1900-01-01 07:36 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/2804 | 5/3128
292 | 705280 | 765kV DURG PS- CHAMPA_1 | WRTS-I | 0 |  |  | 2015-05-29 | 21:14 | [7 empty] | LINE FIRST TIME CHARGED. |  | 05/3117, NL-05/875
293 | 705281 | 400kV BHADRAVATI-DHARIWAL TPP II | WRTS-I | 0 | 2015-05-29 | 8:08 | 2015-05-29 | 20:08 | 0 | 0.5 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 5/3189 | 5/3271
294 | 705282 | 400kV DHARIWAL TPP-PARLI II | WRTS-I | 0 | 2015-05-29 | 8:12 | 2015-05-29 | 20:25 | 0 | 0.50903 | 0 | 0 | O | N | OMSU | OCC APPROVED OUTAGE AVAILED FOR REPLACEMENT OF PORCELAIN INSULATOR AT CRITICAL CROSSING (NH)FOR PUBLIC SAFETY | 5/3190 | 5/3272
295 | 705283 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-05-29 | 9:26 | 2015-05-30 | 1:13 | 0 | 0 | 0 | 0.65764 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3207 | 5/3291
296 | 705284 | 400kV RAIPUR-RAIGARH I | WRTS-I | 1 | 2015-05-29 | 15:13 | 2015-05-29 | 15:51 | 0.026389 | 0 | 0 | 0 | L | N | SRMT | TRIPPED DUE TO RELAY MAL OPERATION AT RAIGARH. DT RECEIVED AT RAIPUR END |  | 5/3236
297 | 705285 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-05-29 | 8:48 | 2015-05-29 | 16:06 | 0 | 0 | 0 | 0.30417 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3200 | 5/3237
298 | 705286 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-05-29 | 16:52 | 2015-05-30 | 10:49 | 0 | 0 | 0 | 0.74792 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 5/3329
299 | 705287 | 765kV CHAMPA- KOTRA PS | WRTS-I | 0 |  |  | 2015-05-29 | 20:38 | [7 empty] | LINE FIRST TIME CHARGED |  | 05/3273, NL-05/911
300 | 705288 | 765kV DURG PS -WARDHA_1 | WRTS-I | 0 | 2015-05-30 | 11:25 | 2015-05-30 | 19:43 | 0 | 0 | 0 | 0.34583 | D | N | SCSD | OUTAGE AVAILED FOR NTAMC WORKS. | 5/3335 5/934 | 5/3381 5/949
301 | 705289 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-05-30 | 11:46 | 2015-05-30 | 20:49 | 0 | 0 | 0 | 0.37708 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3346 05/937 | 5/3388 5/953
302 | 705290 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-05-30 | 11:53 | 2015-05-31 | 18:20 | 0 | 0 | 0 | 1899-12-31 06:27 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3337 5/938
303 | 705291 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-30 | 13:13 | 2015-05-30 | 20:16 | 0 | 0 | 0 | 0.29375 | D | N | SCSD | OUTAGE AVAILED FOR NTAMC WORKS. | 5/3343 5/940 | 5/3382 5/950
304 | 705292 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-30 | 17:55 | 2015-05-31 | 9:48 | 0 | 0 | 0 | 0.66181 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 5/3369 | 5/3433
305 | 705293 | 400kV KORBA-KORBA(WEST) | WRTS-I | 0 | 2015-05-29 | 9:30 | 2015-05-30 | 22:44 | 0 | 0 | 0 | 1899-12-31 13:14 | D | N | OSFD | TO ATTEND HOTSPOT BY KORBA(W) |  | 5/3394
306 | 705294 | 765kV DURG PS -WARDHA_1 | WRTS-I | 0 | 2015-05-31 | 9:16 | 2015-05-31 | 21:18 | 0 | 0 | 0 | 0.50139 | D | N | SCSD | OUTAGE AVAILED FOR NTMC WORK | WR 5/3437 NL 5/959 | WR 5/3492 NL 5/984
307 | 705295 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-05-31 | 9:27 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 0.60625 | D | N | SCSD | OUTAGE AVAILED FOR NTMC WORK | WR 5/3430 NL 5/960 | ---
308 | 705296 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-05-31 | 9:40 | 2015-05-31 | 16:44 | 0 | 0 | 0 | 0.29444 | D | N | SVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WR 5/3431 NL 5/961 | WR 5/3454 NL 5/968
309 | 705297 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-05-31 | 12:28 | 2015-05-31 | 24:00 | 0.48056 | 0 | 0 | 0 | L | N | OSFT | EMERGENCY OUTAGE AVAILED FOR ATTENDING LEAKAGE THROUGH MOG. | WR 5/3442 NL 5/964 | ---
310 | 705298 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | WRTS-I | 0 | 2015-05-31 | 13:55 | 2015-05-31 | 17:35 | 0.15278 | 0 | 0 | 0 | L | N | OMST | LINE H/T FOR RECTIFICATION OF MELTED JUMPER OF BOTTEM PHASE. | 05/3444 | 05/3458
311 | 705299 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-05-31 | 16:10 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 0.32639 | D | N | LVRD | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | 05/3452 | ---
312 | 705300 | 765kV DURG PS- CHAMPA_1 | WRTS-I | 0 | 2015-05-31 | 18:08 | 2015-05-31 | 18:18 | 0 | 0 | 0.0069444 | 0 | S | N | GOVC | LINE TRIPPED DUE TO OVER VOLTAGE | .. | ..
313 | 705301 | 765kV DURG PS- CHAMPA_1 | WRTS-I | 0 | 2015-05-31 | 18:08 | 2015-05-31 | 24:00 | 0 | 0 | 0 | 0.24444 | D | N | LVRD | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | .. | ..
314 | 705302 | 400kV BHILAI-KORADI | WRTS-I | 1 | 2015-05-31 | 19:09 | 2015-05-31 | 24:00 | 0.20208 | 0 | 0 | 0 | L | N | LHWT | LINE TRIPPED ON B-PHASE TO E-FAULT. FL = 210 KM FROM KORADI. LINE TEST CHARGED AT 20:11 BUT LINE TRIPPED ON SOTF. LINE EARTH WIRE CAME OUT FROM CLAMP. FAULT IS UNDER CG(O&M) | … | …..
315 | 705303 | 400KV KORBA-SIPAT | WRTS-I | 0 | 2015-05-31 | 20:17 | 2015-05-31 | 21:44 | 0 | 0.060417 | 0 | 0 | O | N | OMSU | LINE TRIPPED. NO INDICATION FOUND IN RELAY. | --- | 3494
316 | 705304 | 400KV KORBA-BALCO | WRTS-I | 0 | 2015-05-31 | 20:30 | 2015-05-31 | 21:15 | 0 | 0.03125 | 0 | 0 | O | N | OMSU | LINE TRIPPED. NO INDICATION FOUND IN RELAY. | --- | 3489
317 | 705305 | 765kV BILASPUR-SIPAT I | WRTS-I | 1 | 2015-05-31 | 20:17 | 2015-05-31 | 24:00 | 0.15486 | 0 | 0 | 0 | L | N | LPPT | LINE TRIPPED ON - PHASE TO PHASE FAULT- FAULT CURRENT -10K.A. FL = 30KM FROM BILASPUR END. FAULT IS UNDER CG(O&M) | --- | 5/3510 NL-987
318 | 705306 | 400kV BHATAPARA-KORBA | WRTS-I | 0 | 2015-05-31 | 20:42 | 2015-05-31 | 22:41 | 0 | 0.082639 | 0 | 0 | O | N | SEFU | LINE A/R SUCCESSFUL AT BHATAPARA END BUT TRIPPED AT KORBA END. | --- | 3500
TOTAL |  | GRAND TOTAL IN HRS:MIN | [6 empty] | 1900-02-01 19:18 | 1900-01-03 07:03 | 1900-01-12 11:21 | 1900-11-09 06:46
TOTAL |  | GRAND TOTAL IN HRS | [6 empty] | 811.3 | 103.05 | 323.35 | 7542.77
Ouatge hrs due to more than 2 tripping
|  | ICT2_765/400kv_AURANGABAD | [6 empty] | 12
|  | TOTAL HRS AS PER WRLDC= | [6 empty] | 799.3
|  | GRAND TOTAL HRS (includingOuatge hrs due to more than 2 tripping) = | [6 empty] | 811.3
Formulas:
ATTRIBUTED TO ( IN HRS:MIN) = SUM(J6:[ATTRIBUTED TO ( IN HRS:MIN), row above])
OTHERS = SUM(K6:[OTHERS, row above])
SYSTEM CONSTR. = SUM(L6:[SYSTEM CONSTR., row above])
DEEMED AVAILABLE = SUM(M6:[DEEMED AVAILABLE, row above])