## Aug15
|  | ELEMENT WISE AVAILABILITY FOR = | 2015-08-01
744
|  | POWERGRID WRTS-I | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
SN | Unique ID of transmission Element | NAME OF LINE/ICT |  |  |  | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available | [6 empty] | CATEGORY
1 | WR1L2 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I | [16 empty] | WRPC
|  | 220kV KORBA(EAST)-BUDDHIPADAR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
2 | WR1L43 | 400kV RAIPUR-RAIGARH I | 217.02 | WRTS-I
|  | 400kV RAIPUR-RAIGARH I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
3 | WR1L44 | 400kV RAIPUR-KWPCL II | 203.02 | WRTS-I
|  | 400kV RAIPUR-KWPCL II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
4 | WR1L45 | 400kV KWPCL-RAIGARH II | 14 | WRTS-I
|  | 400kV KWPCL-RAIGARH II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
5 | WR1L110 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I |  | 2015-08-08 | 14:30 | 2015-08-08 | 17:44 |  |  |  | 0 | 0.13472 | 0 | 0 |  |  |  | LINE TRIPPED IN R-E FAULT, ZONE-2 ,FC-0.6KA AT RAIGARH END. FAULT IS IN INDBHARAT SECTION. |  |  | OMSU
5 | WR1L110 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I |  | 2015-08-21 | 13:05 | 2015-08-21 | 17:27 |  |  |  | 0 | 0 | 0 | 0.18194 |  |  |  | LINE H/T TO ATTEND HOT SPOT IN LILO PORTION BY M/S IBEUL. FAULT IN M/S BEUL SECTION. |  |  | OSFD
5 | WR1L110 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I |  | 2015-08-26 | 21:54 | 2015-08-27 | 0:02 |  |  |  | 0.088889 | 0 | 0 | 0 |  |  |  | TRIPPED ON B- E FAULT. FC=15.2KA, FL:4.94KM FROM RAIGARH END. |  |  | LEFT
|  | 400kV RAIGARH-IBEUL I Total | [10 empty] | 0.088889 | 0.13472 | 0 | 0.18194 | [5 empty] | 99.71%
6 | WR1L111 | 400kV IBEUL-JHARSUGUDA I | 20.03 | WRTS-I
|  | 400kV IBEUL-JHARSUGUDA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
7 | WR1L49 | 400kV JHARSUGUDA-ROURKELA I | 142.45 | WRTS-I
|  | 400kV JHARSUGUDA-ROURKELA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
8 | WR1L98 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I |  | 2015-08-03 | 9:53 | 2015-08-03 | 10:56 |  |  |  | 0.04375 | 0 | 0 | 0 |  |  |  | H/T FOR REACTOR WORKS AT ROURKELA END. |  |  | OSPT
8 | WR1L98 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I |  | 2015-08-20 | 11:17 | 2015-08-20 | 11:45 |  |  |  | 0.019444 | 0 | 0 | 0 |  |  |  | H/T FOR TAKING REACTOR IN SERVICE |  |  | OMST
8 | WR1L98 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I |  | 2015-08-31 | 9:41 | 2015-08-31 | 22:44 |  |  |  | 0.54375 | 0 | 0 | 0 |  |  |  | A/R SUCCESSFUL AT RAIGARH END BUT LINE WAS TRIPPED AT ROURKELA END ON R-E FAULT. FAULY UNDER ER-2 |  |  | LEFT
|  | 400kV RAIGARH-ROURKELA II Total | [10 empty] | 0.60694 | 0 | 0 | 0 | [5 empty] | 98.04%
9 | WR1L50 | 400KV RANCHI-SIPAT I | 405.77 | WRTS-I
|  | 400KV RANCHI-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
10 | WR1L51 | 400KV RANCHI-SIPAT II | 405.77 | WRTS-I
|  | 400KV RANCHI-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
11 | WR1L52 | 400kV RAIPUR-KSK III | 134.74 | WRTS-I
|  | 400kV RAIPUR-KSK III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
12 | WR1L105 | 400kV KSK-RKKML III | 82.248 | WRTS-I
|  | 400kV KSK-RKKML III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
13 | WR1L106 | 400kV RKKML-RAIGARH III | 3.896 | WRTS-I
|  | 400kV RKKML-RAIGARH III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
14 | WR1L103 | 400KV RAIPUR-KSK IV | 161.82 | WRTS-I
|  | 400KV RAIPUR-KSK IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
15 | WR1L97 | 400kV KSK-RAIGARH IV | 113.389 | WRTS-I
|  | 400kV KSK-RAIGARH IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
16 | WR1L56 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I |  | 2015-08-03 | 06:13 | 2015-08-03 | 08:39 |  |  |  | 0.10139 | 0 | 0 | 0 |  |  |  | TRIPPED DUE TO A/R UNSUCCESSFUL ON FAULT.86B RELAY OPERATED AT RAIGARH END. |  |  | SEMT
16 | WR1L56 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I |  | 2015-08-03 | 10:01 | 2015-08-03 | 12:57 |  |  |  | 0.62222 | 0 | 0 | 0 |  |  |  | DT RECEIVED AT RAIGARH END. |  |  | OMST
16 | WR1L56 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I |  | 2015-08-24 | 9:21 | 2015-08-24 | 19:54 |  |  |  | 0 | 0 | 0 | 0.43958 |  |  |  | H/T FOR PROTECTION AUDIT APPROVED BY CEA. |  |  | OSPD
|  | 400kV RAIGARH-JHARSUGUDA III Total | [10 empty] | 0.72361 | 0 | 0 | 0.43958 | [5 empty] | 97.67%
17 | WR1L57 | 400kV JHARSUGUDA-ROURKELA III | 143.06 | WRTS-I
|  | 400kV JHARSUGUDA-ROURKELA III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
18 | WR1L58 | 400kV RAIGARH-STERLITE IV | 105 | WRTS-I
|  | 400kV RAIGARH-STERLITE IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
19 | WR1L59 | 400kV STERLITE-ROURKELA IV | 104.28 | WRTS-I
|  | 400kV STERLITE-ROURKELA IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
20 | WR1L60 | 765kV D'JAIGARH-BILASPUR | 90 | WRTS-I
|  | 765kV D'JAIGARH-BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
21 | WR1L61 | 765kV D'JAIGARH-RANCHI | 303 | WRTS-I |  | 2015-08-28 | 8:34 | 2015-08-28 | 22:21 |  |  |  | 0 | 0 | 0 | 0.57431 |  |  |  | H/T FOR PROTECTION AUDIT APPROVED BY CEA. |  |  | OSPD
21 | WR1L61 | 765kV D'JAIGARH-RANCHI | 303 | WRTS-I |  | 2015-08-31 | 11:07 | 2015-08-31 | 11:59 |  |  |  | 0.036111 | 0 | 0 | 0 |  |  |  | MAL OPRETION OF PLCC AT RANCHI AND DT RECIVED AT DHARAMJAYGARH, FAULT UNDER-ER-1 |  |  | SPLT
|  | 765kV D'JAIGARH-RANCHI Total | [10 empty] | 0.036111 | 0 | 0 | 0.57431 | [5 empty] | 99.88%
22 | WR1L101 | 765kV D'JAIGARH- JHARSUGUDA I | 149.789 | WRTS-I |  | 2015-08-23 | 8:27 | 2015-08-23 | 23:09 |  |  |  | 0 | 0 | 0 | 0.6125 |  |  |  | H/T FOR PROTECTION AUDIT APPROVED BY CEA. |  |  | OSPD
|  | 765kV D'JAIGARH- JHARSUGUDA I Total | [10 empty] | 0 | 0 | 0 | 0.6125 | [5 empty] | 100%
23 | WR1L102 | 765kV D'JAIGARH- JHARSUGUDA II | 149.789 | WRTS-I |  | 2015-08-22 | 8:14 | 2015-08-23 | 0:13 |  |  |  | 0 | 0 | 0 | 0.66597 |  |  |  | OUTAGE AVAILED BY FOR PROTECTION AUDIT APPROVED BY CEA |  |  | OSPD
23 | WR1L102 | 765kV D'JAIGARH- JHARSUGUDA II | 149.789 | WRTS-I |  | 2015-08-29 | 16:05 | 2015-08-29 | 18:06 |  |  |  | 0 | 0 | 0 | 0.084028 |  |  |  | OUTAGE AVAILED FOR FRA TEST ON 765KV JABALPUR # 4 - L/R AT DHARAMJAYGARH S/S.(JABALPUR # 4 LINE REACTOR IS ADJACENT TO THE JHARSUGUDA CKT # 2). |  |  | SCSD
|  | 765kV D'JAIGARH- JHARSUGUDA II Total | [10 empty] | 0 | 0 | 0 | 0.75 | [5 empty] | 100%
24 | WR1L3 | 400kV KORBA-KORBA(WEST) | 14 | WRTS-I |  | 2015-07-17 | 11:03 | 2015-07-26 | 18:49 |  |  |  | 0 | 0 | 0 | 1900-01-08 07:46 |  |  |  | EMERGENCY OUTAGE AVAILED BY KORBA WEST (CSPTCL) |  |  | OSFD
|  | 400kV KORBA-KORBA(WEST) Total | [10 empty] | 0 | 0 | 0 | 1900-01-08 07:46 | [5 empty] | 100%
25 | WR1L4 | 400kV KORBA-BHILAI I | 197 | WRTS-I
|  | 400kV KORBA-BHILAI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
26 | WR1L5 | 400kV KORBA-BHILAI II | 192 | WRTS-I
|  | 400kV KORBA-BHILAI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
27 | WR1L6 | 400kV BHILAI-KORADI | 272 | WRTS-I
|  | 400kV BHILAI-KORADI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
28 | WR1L7 | 400kV KORADI-SATPURA | 149 | WRTS-I
|  | 400kV KORADI-SATPURA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
29 | WR1L8 | 400kV RAIPUR-BHILAI I | 13 | WRTS-I
|  | 400kV RAIPUR-BHILAI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
30 | WR1L9 | 400kV BHILAI-BHADRAVATI I | 322 | WRTS-I
|  | 400kV BHILAI-BHADRAVATI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
31 | WR1L10 | 400kV RAIPUR-BHADRAVATI I | 333 | WRTS-I
|  | 400kV RAIPUR-BHADRAVATI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
32 | WR1L11 | 400kV RAIPUR-BHADRAVATI II | 345.55 | WRTS-I |  | 2015-08-06 | 11:25 | 2015-08-06 | 18:47 |  |  |  | 0 | 0.30694 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR REPLACEMENT OF INSULATORS FOR PUBLIC SAFETY AT NH/SH. |  |  | OMSU
|  | 400kV RAIPUR-BHADRAVATI II Total | [10 empty] | 0 | 0.30694 | 0 | 0 | [5 empty] | 100%
33 | WR1L12 | 400kV RAIPUR-BHADRAVATI III | 345.55 | WRTS-I
|  | 400kV RAIPUR-BHADRAVATI III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
34 | WR1L13 | 400kV BHADRAVATI-CHANDRAPUR I | 20 | WRTS-I
|  | 400kV BHADRAVATI-CHANDRAPUR I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
35 | WR1L14 | 400kV BHADRAVATI-CHANDRAPUR II | 20 | WRTS-I
|  | 400kV BHADRAVATI-CHANDRAPUR II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
36 | WR1L15 | 400kV BHADRAVATI-CHANDRAPUR III | 22.42 | WRTS-I |  | 2015-08-03 | 09:52 | 2015-08-03 | 15:18 |  |  |  | 0 | 0.22639 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR REPLACEMENT OF INSULATORS FOR PUBLIC SAFETY AT NH/SH. |  |  | OMSU
|  | 400kV BHADRAVATI-CHANDRAPUR III Total | [10 empty] | 0 | 0.22639 | 0 | 0 | [5 empty] | 100%
37 | WR1L16 | 400kV BHADRAVATI-CHANDRAPUR IV | 22.42 | WRTS-I |  | 2015-08-31 | 9:41 | 2015-08-31 | 14:26 |  |  |  | 0 | 0.19792 | 0 | 0 |  |  |  | FOR INSULATOR REPLACMENT ON NH, RAILWAY CROSSING FOR PUBLIC SAFTEY |  |  | OMSU
|  | 400kV BHADRAVATI-CHANDRAPUR IV Total | [10 empty] | 0 | 0.19792 | 0 | 0 | [5 empty] | 100%
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-01 | 16:38 | 2015-08-03 | 09:28 |  |  |  | 0 | 0 | 0 | 1899-12-31 16:50 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-04 | 17:04 | 2015-08-05 | 7:16 |  |  |  | 0 | 0 | 0 | 0.59167 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-06 | 16:42 | 2015-08-07 | 07:16 |  |  |  | 0 | 0 | 0 | 0.60694 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-08 | 16:46 | 2015-08-09 | 7:13 |  |  |  | 0 | 0 | 0 | 0.60208 |  |  |  | CHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-09 | 16:13 | 2015-08-10 | 7:13 |  |  |  | 0 | 0 | 0 | 0.625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-10 | 16:11 | 2015-08-11 | 7:22 |  |  |  | 0 | 0 | 0 | 0.63264 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-12 | 17:12 | 2015-08-13 | 9:23 |  |  |  | 0 | 0 | 0 | 0.67431 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-14 | 16:20 | 2015-08-15 | 6:42 |  |  |  | 0 | 0 | 0 | 0.59861 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-17 | 16:38 | 2015-08-18 | 7:10 |  |  |  | 0 | 0 | 0 | 0.60556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-19 | 16:39 | 2015-08-20 | 7:14 |  |  |  | 0 | 0 | 0 | 0.60764 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-21 | 16:39 | 2015-08-22 | 7:15 |  |  |  | 0 | 0 | 0 | 0.60833 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-23 | 6:26 | 2015-08-23 | 17:37 |  |  |  | 0 | 0 | 0 | 0.46597 |  |  |  | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE |  |  | LCSD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-24 | 17:16 | 2015-08-25 | 6:58 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-26 | 16:43 | 2015-08-27 | 7:06 |  |  |  | 0 | 0 | 0 | 0.59931 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-27 | 16:49 | 2015-08-28 | 6:43 |  |  |  | 0 | 0 | 0 | 0.57917 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-29 | 17:10 | 2015-08-30 | 7:00 |  |  |  | 0 | 0 | 0 | 0.57639 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-30 | 9:35 | 2015-08-30 | 15:46 |  |  |  | 0 | 0 | 0 | 0.25764 |  |  |  | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE |  |  | LCSD
38 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WRTS-I |  | 2015-08-31 | 16:42 | 2015-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 400kV KOLHAPUR-MAPUSA I Total | [10 empty] | 0 | 0 | 0 | 1900-01-10 04:59 | [5 empty] | 100%
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-07-31 | 16:50 | 2015-08-01 | 09:54 |  |  |  | 0 | 0 | 0 | 0.4125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-03 | 16:43 | 2015-08-04 | 7:09 |  |  |  | 0 | 0 | 0 | 0.60139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-05 | 16:13 | 2015-08-06 | 06:54 |  |  |  | 0 | 0 | 0 | 0.61181 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-07 | 16:43 | 2015-08-08 | 09:33 |  |  |  | 0 | 0 | 0 | 0.70139 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-11 | 16:11 | 2015-08-12 | 7:09 |  |  |  | 0 | 0 | 0 | 0.62361 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-13 | 16:16 | 2015-08-16 | 9:09 |  |  |  | 0 | 0 | 0 | 1900-01-01 16:53 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-16 | 16:09 | 2015-08-17 | 7:50 |  |  |  | 0 | 0 | 0 | 0.65347 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-18 | 16:48 | 2015-08-19 | 6:44 |  |  |  | 0 | 0 | 0 | 0.58056 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-20 | 16:39 | 2015-08-21 | 6:33 |  |  |  | 0 | 0 | 0 | 0.57917 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-22 | 16:43 | 2015-08-23 | 6:22 |  |  |  | 0 | 0 | 0 | 0.56875 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-23 | 6:22 | 2015-08-23 | 17:32 |  |  |  | 0 | 0 | 0 | 0.46528 |  |  |  | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE |  |  | LCSD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-23 | 17:32 | 2015-08-24 | 7:46 |  |  |  | 0 | 0 | 0 | 0.59306 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-25 | 16:16 | 2015-08-26 | 6:47 |  |  |  | 0 | 0 | 0 | 0.60486 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-30 | 8:54 | 2015-08-30 | 15:32 |  |  |  | 0 | 0 | 0 | 0.27639 |  |  |  | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE |  |  | LCSD
39 | WR1L18 | 400kV KOLHAPUR-MAPUSA II | 150 | WRTS-I |  | 2015-08-30 | 15:32 | 2015-08-31 | 07:00 |  |  |  | 0 | 0 | 0 | 0.64444 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 400kV KOLHAPUR-MAPUSA II Total | [10 empty] | 0 | 0 | 0 | 1900-01-09 14:53 | [5 empty] | 100%
40 | WR1L25 | 400kV MAHAN-VINDHYACHAL | 19 | WRTS-I
|  | 400kV MAHAN-VINDHYACHAL Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
41 | WR1L26 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2015-08-23 | 4:47 | 2015-08-23 | 4:57 |  |  |  | 0.0069444 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DUE ON R PHASE TO E FAULT,FC-3.502 KA, FL-114 KM FROM KORBA END AND FC-1.25KA,FL-99.3 KM FROM MAHAN END. |  |  | LEFT
41 | WR1L26 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2015-08-23 | 4:57 | 2015-08-23 | 8:05 |  |  |  | 0 | 0.13056 | 0 | 0 |  |  |  | LINE CHARGING DELAYED BY NTPC KORBA END. |  |  | OMSU
|  | 400kV KORBA-MAHAN Total | [10 empty] | 0.0069444 | 0.13056 | 0 | 0 | [5 empty] | 99.98%
42 | WR1L27 | 400kV VINDHYACHAL-KORBA II | 288.994 | WRTS-I |  | 2015-08-15 | 11:14 | 2015-08-15 | 11:29 |  |  |  | 0 | 0 | 0.010417 | 0 |  |  |  | LINE TRIPPED ON B-E FAULT , DUE TO HEAVY RAIN & THUNDER |  |  | LNCC
42 | WR1L27 | 400kV VINDHYACHAL-KORBA II | 288.994 | WRTS-I |  | 2015-08-15 | 11:29 | 2015-08-16 | 5:27 |  |  |  | 0 | 0 | 0 | 0.74861 |  |  |  | LINE KEPT UNCHAGRED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
|  | 400kV VINDHYACHAL-KORBA II Total | [10 empty] | 0 | 0 | 0.010417 | 0.74861 | [5 empty] | 100%
43 | WR1L28 | 400kV SATPURA-SEONI | 1.5 | WRTS-I
|  | 400kV SATPURA-SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
44 | WR1L29 | 400kV BHILAI-SEONI | 1.5 | WRTS-I
|  | 400kV BHILAI-SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
45 | WR1L30 | 400kV BHILAI-BHATAPARA | 90.453 | WRTS-I
|  | 400kV BHILAI-BHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
46 | WR1L31 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I
|  | 400kV BHATAPARA-KORBA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
47 | WR1L34 | 400kV RAIPUR-SIPAT I | 149.12 | WRTS-I
|  | 400kV RAIPUR-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
48 | WR1L35 | 765kV TAMNAR PS-KOTRA PS I | 47.97 | WRTS-I
|  | 765kV TAMNAR PS-KOTRA PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
49 | WR1L36 | 765kV TAMNAR PS-KOTRA PS II | 47.97 | WRTS-I
|  | 765kV TAMNAR PS-KOTRA PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
50 | WR1L37 | 765kV KOTRA PS-DURG PS I | 239.84 | WRTS-I |  | 2015-08-01 | 0:00 | 2015-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-30 |  |  |  | KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV KOTRA PS-DURG PS I Total | [10 empty] | 0 | 0 | 0 | 1900-01-30 | [5 empty] | 100%
51 | WR1L38 | 765kV KOTRA PS-DURG PS II | 239.84 | WRTS-I
|  | 765kV KOTRA PS-DURG PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
52 | WR1L39 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 52.56 | WRTS-I
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
53 | WR1L40 | 400kV BHADRAVATI-DHARIWAL TPP II | 18.14 | WRTS-I
|  | 400kV BHADRAVATI-DHARIWAL TPP II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
54 | WR1L41 | 400kV DHARIWAL TPP-PARLI II | 391 | WRTS-I
|  | 400kV DHARIWAL TPP-PARLI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
55 | WR1L42 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 52.56 | WRTS-I
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
56 | WR1L62 | 400KV RAIPUR-SIPAT II | 149.12 | WRTS-I
|  | 400KV RAIPUR-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
57 | WR1L63 | 400kV RAIPUR-SIPAT III | 162.04 | WRTS-I
|  | 400kV RAIPUR-SIPAT III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
58 | WR1L64 | 765kV BILASPUR-SIPAT I | 21.51 | WRTS-I
|  | 765kV BILASPUR-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
59 | WR1L65 | 765kV SEONI-BILASPUR I | 337.05 | WRTS-I
|  | 765kV SEONI-BILASPUR I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
60 | WR1L66 | 765kV BILASPUR-SIPAT II | 22.22 | WRTS-I
|  | 765kV BILASPUR-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
61 | WR1L67 | 765kV SEONI-BILASPUR II | 338.33 | WRTS-I
|  | 765kV SEONI-BILASPUR II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I |  | 2015-08-03 | 15:11 | 2015-08-05 | 15:00 |  |  |  | 0 | 1899-12-31 23:49 | 0 | 0 |  |  |  | LINE TRIPPED ON B-PHASE TO EARTH FAULT DUE TO FALLING OF OPGW PILOT WIRE ROPE ON CHARGED CONDUCTOR AT LOC. 694-695-696. BROKEN PILOT WIRE RESTORED ON 05.08.15 DUE TO HEAVY RAINFALL. ONLINE OPGW WORKS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. |  |  | OMSU
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I |  | 2015-08-05 | 15:00 | 2015-08-05 | 17:32 |  |  |  | 0 | 0 | 0 | 0.10556 |  |  |  | LINE WAS READU FOR CHARGING AT 15:00 HRS BUT KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I |  | 2015-08-13 | 13:03 | 2015-08-13 | 18:27 |  |  |  | 0.225 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON Y-N FAULT FC-4.9KA,FL-112.3 KM FROM SEONI AND 142 KM FROM WARDHA END. LINE WAS READY FOR CHARGING AT 18:27 HRS. |  |  | LEFT
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I |  | 2015-08-13 | 18:27 | 2015-08-13 | 22:27 |  |  |  | 0 | 0 | 0 | 0.16667 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I |  | 2015-08-26 | 17:43 | 2015-08-28 | 7:01 |  |  |  | 0 | 0 | 0 | 1899-12-31 13:18 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
62 | WR1L68 | 765kV SEONI-WARDHA I | 267.89 | WRTS-I |  | 2015-08-30 | 18:32 | 2015-08-31 | 6:36 |  |  |  | 0 | 0 | 0 | 0.50278 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV SEONI-WARDHA I Total | [10 empty] | 0.225 | 1899-12-31 23:49 | 0 | 1900-01-01 07:54 | [5 empty] | 99.22%
63 | WR1L69 | 765kV SEONI-WARDHA II | 260.76 | WRTS-I |  | 2015-07-31 | 1:19 | 2015-08-02 | 12:37 |  |  |  | 0 | 0 | 0 | 1899-12-31 12:37 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
63 | WR1L69 | 765kV SEONI-WARDHA II | 260.76 | WRTS-I |  | 2015-08-15 | 15:50 | 2015-08-17 | 9:15 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
63 | WR1L69 | 765kV SEONI-WARDHA II | 260.76 | WRTS-I |  | 2015-08-17 | 17:01 | 2015-08-17 | 17:11 |  |  |  | 0 | 0 | 0.0069444 | 0 |  |  |  | LINE TRIPPED ON O/V AT WARDHA END |  |  | GOVC
63 | WR1L69 | 765kV SEONI-WARDHA II | 260.76 | WRTS-I |  | 2015-08-17 | 17:11 | 2015-08-18 | 8:32 |  |  |  | 0 | 0 | 0 | 0.63958 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV SEONI-WARDHA II Total | [10 empty] | 0 | 0 | 0.0069444 | 1900-01-02 21:23 | [5 empty] | 100%
64 | WR1L70 | 400kV WARDHA-AKOLA I | 161.87 | WRTS-I
|  | 400kV WARDHA-AKOLA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
65 | WR1L71 | 400kV WARDHA-AKOLA II | 161.87 | WRTS-I |  | 2015-08-28 | 9:05 | 2015-08-28 | 19:07 |  |  |  | 0 | 0 | 0 | 0.41806 |  |  |  | H/T FOR AMP WORKS BY MSETCL |  |  | OSPD
|  | 400kV WARDHA-AKOLA II Total | [10 empty] | 0 | 0 | 0 | 0.41806 | [5 empty] | 100%
66 | WR1L72 | 400kV AURANGABAD (PG) -AKOLA I | 241.23 | WRTS-I
|  | 400kV AURANGABAD (PG) -AKOLA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
67 | WR1L73 | 400kV AURANGABAD (PG) -AKOLA II | 289.97 | WRTS-I
|  | 400kV AURANGABAD (PG) -AKOLA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
68 | WR1L74 | 400kV BHADRAVATI-PARLI I | 378.67 | WRTS-I |  | 2015-08-04 | 7:22 | 2015-08-04 | 19:01 |  |  |  | 0 | 0.48542 | 0 | 0 |  |  |  | LINE TRIPPED ON Y-B PHASE FAULT DUE TO FALLING OF OPGW PILOT WIRE ROPE ON CHARGED CONDUCTOR AT LOC. 78-79 DURING ON LINE OPGW WORK. ONLINE OPGW WORKS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. |  |  | OMSU
|  | 400kV BHADRAVATI-PARLI I Total | [10 empty] | 0 | 0.48542 | 0 | 0 | [5 empty] | 100%
69 | WR1L76 | 400kV PARLI(PG)-PARLI(MSETCL) I | 4.96 | WRTS-I
|  | 400kV PARLI(PG)-PARLI(MSETCL) I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
70 | WR1L77 | 400kV PARLI(PG)-PARLI(MSETCL) II | 4.96 | WRTS-I
|  | 400kV PARLI(PG)-PARLI(MSETCL) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
71 | WR1L78 | 400kV KORBA-RAIPUR III | 211.86 | WRTS-I |  | 2015-08-10 | 22:25 | 2015-08-10 | 22:25 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | A/R SUCCESSFUL FROM BOTH ENDS AT 22:25 HRS. ON R PHASE TO E FAULT,FC-3.896KA,FL-101 KM FROM RAIPUR END. |  |  | LART
|  | 400kV KORBA-RAIPUR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
72 | WR1L79 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I |  | 2015-08-10 | 20:33 | 2015-08-10 | 20:33 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | A/R SUCCESSFUL FROM BOTH ENDS AT 20:33 HRS. ON Y PHASE TO E FAULT,FC-6.49KA,FL-59.44 KM FROM RAIPUR END. |  |  | LART
72 | WR1L79 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I |  | 2015-08-12 | 17:39 | 2015-08-12 | 17:39 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 400KV RAIPUR -KORBA CKT # 4 - A/R SUCCESSFUL FROM BOTH ENDS AT 17.39 HRS. ON Y PHASE TO E FAULT , FL-133 KM FROM RAIPUR END.FC=2.849KA |  |  | LART
|  | 400kV KORBA-RAIPUR IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
73 | WR1L80 | 400kV WARDHA-PARLI I | 336.94 | WRTS-I |  | 2015-08-16 | 10:56 | 2015-08-16 | 18:38 |  |  |  | 0.32083 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE AVAILED FOR ATTENDING THE DAMAGED CONDUCTOR BETWEEN LOCATION NO. 878-879 (TOP PHASE). |  |  | OSFT
|  | 400kV WARDHA-PARLI I Total | [10 empty] | 0.32083 | 0 | 0 | 0 | [5 empty] | 98.97%
74 | WR1L81 | 400kV WARDHA-PARLI II | 336.94 | WRTS-I
|  | 400kV WARDHA-PARLI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
75 | WR1L82 | 400kV KORBA-BALCO | 7.45 | WRTS-I
|  | 400kV KORBA-BALCO Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
76 | WR1L83 | 400kV BALCO-BIRSINGHPUR | 219.19 | WRTS-I
|  | 400kV BALCO-BIRSINGHPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
77 | WR1L84 | 400kV WARDHA-MAUDA II | 123.84 | WRTS-I
|  | 400kV WARDHA-MAUDA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
78 | WR1L85 | 400kV KORBA-VANDANA | 14.77 | WRTS-I
|  | 400kV KORBA-VANDANA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
79 | WR1L86 | 400KV VANDANA-BIRSINGHPUR | 211.87 | WRTS-I
|  | 400KV VANDANA-BIRSINGHPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
80 | WR1L87 | 400KV RAIPUR-WARDHA I | 370.57 | WRTS-I |  | 2015-08-11 | 9:21 | 2015-08-11 | 19:19 |  |  |  | 0.41528 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS BY PGCIL CG(O&M) |  |  | OSPT
80 | WR1L87 | 400KV RAIPUR-WARDHA I | 370.57 | WRTS-I |  | 2015-08-31 | 14:58 | 2015-08-31 | 14:58 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | A/R SUCCESSFUL AT BOTH END, B-E FAULT DISTT-48 KM FROM WARDHA END AND 227.7KM FROM RAIPUR END. UNER PGCIL MH PORTION. |  |  | LART
|  | 400KV RAIPUR-WARDHA I Total | [10 empty] | 0.41528 | 0 | 0 | 0 | [5 empty] | 98.66%
81 | WR1L88 | 400KV RAIPUR-WARDHA II | 370.57 | WRTS-I |  | 2015-08-05 | 09:17 | 2015-08-05 | 18:22 |  |  |  | 0.37847 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS BY PGCIL CG(O&M) |  |  | OSPT
81 | WR1L88 | 400KV RAIPUR-WARDHA II | 370.57 | WRTS-I |  | 2015-08-08 | 11:46 | 2015-08-08 | 13:02 |  |  |  | 0.55278 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO FAILURE OF LINE REAACTOR PRV CABLE AT RAIPUR. |  |  | SEFT
81 | WR1L88 | 400KV RAIPUR-WARDHA II | 370.57 | WRTS-I |  | 2015-08-12 | 17:39 | 2015-08-12 | 17:39 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | A/R SUCCESSFUL FROM BOTH ENDS AT 17.39 HRS. ON R PHASE TO E FAULT , FL-81.30 KM FROM WARDHA END. PATROLLING DONE NO ABNORMALITY FOUND. |  |  | LART
|  | 400KV RAIPUR-WARDHA II Total | [10 empty] | 0.93125 | 0 | 0 | 0 | [5 empty] | 97%
82 | WR1L89 | 400KV WARDHA-IEPL | 52.62 | WRTS-I
|  | 400KV WARDHA-IEPL Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
83 | WR1L90 | 400KV IEPL-MAUDA | 70.83 | WRTS-I
|  | 400KV IEPL-MAUDA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
84 | WR1L91 | 400kV RAIPUR-DURG I | 21.5 | WRTS-I |  | 2015-08-08 | 9:11 | 2015-08-08 | 19:04 |  |  |  | 0.41181 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS BY PGCIL CG(O&M) |  |  | OSPT
84 | WR1L91 | 400kV RAIPUR-DURG I | 21.5 | WRTS-I |  | 2015-08-11 | 21:34 | 2015-08-11 | 21:34 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 400KV RAIPUR - DURG PS CKT # 1 & 2 - A/R SUCCESSFUL FROM BOTH ENDS AT 21.34 HRS. |  |  | LART
|  | 400kV RAIPUR-DURG I Total | [10 empty] | 0.41181 | 0 | 0 | 0 | [5 empty] | 98.67%
85 | WR1L92 | 400kV RAIPUR-DURG II | 21.5 | WRTS-I |  | 2015-08-07 | 9:13 | 2015-08-07 | 20:20 |  |  |  | 0.46319 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS BY PGCIL CG(O&M) |  |  | OSPT
85 | WR1L92 | 400kV RAIPUR-DURG II | 21.5 | WRTS-I |  | 2015-08-11 | 21:34 | 2015-08-11 | 21:34 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 400KV RAIPUR - DURG PS CKT # 1 & 2 - A/R SUCCESSFUL FROM BOTH ENDS AT 21.34 HRS. |  |  | LART
|  | 400kV RAIPUR-DURG II Total | [10 empty] | 0.46319 | 0 | 0 | 0 | [5 empty] | 98.51%
86 | WR1L93 | 400kV RAIGARH-KOTRA PS I | 6.29 | WRTS-I
|  | 400kV RAIGARH-KOTRA PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
87 | WR1L94 | 400kV RAIGARH-KOTRA PS II | 6.29 | WRTS-I
|  | 400kV RAIGARH-KOTRA PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
88 | WR1L95 | 765KV DURG PS - D'JAIGARH | 357.62 | WRTS-I
|  | 765KV DURG PS - D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
89 | WR1L99 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2015-08-06 | 13:42 | 2015-08-10 | 8:55 |  |  |  | 0 | 0 | 0 | 1900-01-02 19:13 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
89 | WR1L99 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2015-08-17 | 17:11 | 2015-08-26 | 10:53 |  |  |  | 0 | 0 | 0 | 1900-01-07 17:42 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) I Total | [10 empty] | 0 | 0 | 0 | 1900-01-11 12:55 | [5 empty] | 100%
90 | WR1L100 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2015-08-21 | 14:40 | 2015-08-21 | 23:02 |  |  |  | 0.34861 | 0 | 0 | 0 |  |  |  | H/T FOR REPLACEMENT OF MOG DIAPHRAM GASKET OF 765KV WARDHA - 2 L/RS CONSERVATORS AT AURANGABAD S/S |  |  | OMST
90 | WR1L100 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2015-08-22 | 10:16 | 2015-08-22 | 21:16 |  |  |  | 0.45833 | 0 | 0 | 0 |  |  |  | H/T FOR REPLACEMENT OF MOG DIAPHRAM GASKET OF 765KV WARDHA - 2 L/RS CONSERVATORS AT AURANGABAD S/S |  |  | OMST
|  | 765kV WARDHA - AURANGABAD(PG) II Total | [10 empty] | 0.80694 | 0 | 0 | 0 | [5 empty] | 97.4%
91 | WR1L104 | 400kV KORBA-SIPAT | 68.653 | WRTS-I |  | 2015-08-21 | 9:19 | 2015-08-22 | 19:00 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:41 |  |  |  | OUTAGE AVAILED BY NTPC FOR AMP WORKS. |  |  | OSPD
|  | 400kV KORBA-SIPAT Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 09:41 | [5 empty] | 100%
92 | WR1L108 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2015-08-05 | 16:43 | 2015-08-05 | 17:19 |  |  |  | 0.025 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DURING REPLACEMENT OF FAULTY WTI WITH NEW WTI AT WARDHA DUE TO TOUCHING OF ELECTRICIAN HAND TO OTI DIAL. NO DEFECTS IN LINE , LINE WAS READY FOR CHARGING AT 17:19 |  |  | OMST
92 | WR1L108 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2015-08-05 | 17:19 | 2015-08-06 | 07:01 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  | LINE WAS READY FOR CHARGING BUT KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
92 | WR1L108 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2015-08-16 | 10:48 | 2015-08-17 | 9:30 |  |  |  | 0 | 0 | 0 | 0.94583 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION. |  |  | LPRD
|  | 765kV DURG PS -WARDHA_1 Total | [10 empty] | 0.025 | 0 | 0 | 1899-12-31 12:24 | [5 empty] | 99.92%
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-08-14 | 9:15 | 2015-08-14 | 16:45 |  |  |  | 0.3125 | 0 | 0 | 0 |  |  |  | H/T FOR RECTIFICATION OF OPEN JUMPER AT LOC. NO. 18 IN PGCIL MH PORTION |  |  | OSFT
93 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2015-08-14 | 16:45 | 2015-08-14 | 20:21 |  |  |  | 0 | 0 | 0 | 0.15 |  |  |  | LINE WAS REDAY FOR CHARGING AT 16:45HRS BUT LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV DURG PS -WARDHA_2 Total | [10 empty] | 0.3125 | 0 | 0 | 0.15 | [5 empty] | 98.99%
94 | WR1L112 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2015-08-10 | 7:07 | 2015-08-10 | 16:52 |  |  |  | 0.40625 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE AVAILED FOR ATTENDING HOTSPOTS. |  |  | OSFT
|  | 765kV PUNE(GIS)-SOLAPUR Total | [10 empty] | 0.40625 | 0 | 0 | 0 | [5 empty] | 98.69%
95 | WR1L113 | 400Kv PARLI-PUNE(GIS)_1 | 272.202 | WRTS-I |  | 2015-08-23 | 9:43 | 2015-08-23 | 19:57 |  |  |  | 0 | 0 | 0 | 0.42639 |  |  |  | OUTAGE AVAILED FOR RECTIFICATION/FIXING OF BALANCE SPACERS |  |  | LCSD
|  | 400Kv PARLI-PUNE(GIS)_1 Total | [10 empty] | 0 | 0 | 0 | 0.42639 | [5 empty] | 100%
96 | WR1L114 | 400Kv PARLI-PUNE(GIS)_2 | 272.202 | WRTS-I |  | 2015-08-09 | 7:51 | 2015-08-09 | 08:03 |  |  |  | 0.0083333 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO DT RECEIVED FROM PARLI END. |  |  | OMST
|  | 400Kv PARLI-PUNE(GIS)_2 Total | [10 empty] | 0.0083333 | 0 | 0 | 0 | [5 empty] | 99.97%
97 | WR1L115 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 65 | WRTS-I
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
98 | WR1L116 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 65 | WRTS-I |  | 2015-08-23 | 9:46 | 2015-08-23 | 20:37 |  |  |  | 0 | 0 | 0 | 0.45208 |  |  |  | OUTAGE AVAILED FOR RECTIFICATION/FIXING OF BALANCE SPACERS |  |  | LCSD
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 Total | [10 empty] | 0 | 0 | 0 | 0.45208 | [5 empty] | 100%
99 | WR1L117 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2015-06-28 | 18:27 | 2015-08-10 | 7:40 |  |  |  | 0 | 0 | 0 | 1900-02-10 13:13 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
99 | WR1L117 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2015-08-10 | 7:40 | 2015-08-10 | 19:52 |  |  |  | 0.50833 | 0 | 0 | 0 |  |  |  | LINE H/T FOR JUMPER TIGHTING WORKS |  |  | OMST
99 | WR1L117 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2015-08-10 | 19:52 | 2015-08-17 | 12:14 |  |  |  | 0 | 0 | 0 | 1900-01-05 16:22 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS DUE TO SYSTEM CONSTRAINT FOR VOLTAGE REGULATION |  |  | LVRD
99 | WR1L117 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2015-08-25 | 17:41 | 2015-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-01-05 06:19 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) III Total | [10 empty] | 0.50833 | 0 | 0 | 1900-02-23 11:54 | [5 empty] | 98.36%
100 | WR1L118 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2015-07-23 | 23:56 | 2015-08-06 | 12:59 |  |  |  | 0 | 0 | 0 | 1900-01-04 12:59 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
100 | WR1L118 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2015-08-10 | 9:11 | 2015-08-10 | 19:52 |  |  |  | 0.44514 | 0 | 0 | 0 |  |  |  | LINE H/T FOR JUMPER TIGHTING WORKS |  |  | OMST
100 | WR1L118 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2015-08-10 | 19:52 | 2015-08-12 | 13:01 |  |  |  | 0 | 0 | 0 | 1899-12-31 17:09 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS DUE TO SYSTEM CONSTRAINT FOR VOLTAGE REGULATION |  |  | LVRD
100 | WR1L118 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2015-08-12 | 17:31 | 2015-08-18 | 10:30 |  |  |  | 0 | 0 | 0 | 1900-01-04 16:59 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
100 | WR1L118 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2015-08-18 | 16:43 | 2015-08-21 | 14:33 |  |  |  | 0 | 0 | 0 | 1900-01-01 21:50 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) IV Total | [10 empty] | 0.44514 | 0 | 0 | 1900-01-14 20:57 | [5 empty] | 98.56%
101 | WR1L119 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | 11.2 | WRTS-I
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
102 | WR1L120 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | 11.2 | WRTS-I
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
103 | WR1L121 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I
|  | 765kV DURG PS- CHAMPA_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
104 | WR1L122 | 765kV CHAMPA- KOTRA PS | 96.33 | WRTS-I
|  | 765kV CHAMPA- KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
105 | WR1T1 | ICT1_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT1_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
106 | WR1T2 | ICT2_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT2_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
107 | WR1T3 | ICT1_400/220kv_MAPUSA | 315 | WRTS-I |  | 2015-08-19 | 15:02 | 2015-08-19 | 17:29 |  |  |  | 0.10208 | 0 | 0 | 0 |  |  |  | EMERGENCTY OUTAGE FOR ATTENDING HOT SPOT AT 220KV BUSHING |  |  | OSFT
107 | WR1T3 | ICT1_400/220kv_MAPUSA | 315 | WRTS-I |  | 2015-08-23 | 9:00 | 2015-08-23 | 13:46 |  |  |  | 0 | 0 | 0 | 0.19861 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION DUE TO OUTAGE ON BOTH KOLHAPUR-MAPUSA LINE. |  |  | SPRD
|  | ICT1_400/220kv_MAPUSA Total | [10 empty] | 0.10208 | 0 | 0 | 0.19861 | [5 empty] | 99.67%
108 | WR1T4 | ICT2_400/220kv_MAPUSA | 315 | WRTS-I |  | 2015-08-23 | 14:00 | 2015-08-23 | 19:02 |  |  |  | 0 | 0 | 0 | 0.20972 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
|  | ICT2_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0.20972 | [5 empty] | 100%
109 | WR1T5 | ICT1_400/220kv_BAHATAPARA | 315 | WRTS-I
|  | ICT1_400/220kv_BAHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
110 | WR1T6 | ICT1_400/220kv_RAIGARH | 315 | WRTS-I
|  | ICT1_400/220kv_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
111 | WR1T7 | ICT2_400/220kv_RAIGARH | 315 | WRTS-I
|  | ICT2_400/220kv_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
112 | WR1T8 | ICT1_765/400kv_SEONI | 1500 | WRTS-I
|  | ICT1_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
113 | WR1T9 | ICT2_765/400kv_SEONI | 1500 | WRTS-I
|  | ICT2_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
114 | WR1T10 | ICT3_765/400kv_SEONI | 1500 | WRTS-I
|  | ICT3_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
115 | WR1T11 | ICT1_400/220kv_SEONI | 315 | WRTS-I |  | 2015-08-21 | 10:18 | 2015-08-21 | 19:45 |  |  |  | 0.39375 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR AMP WORKS |  |  | OSPT
|  | ICT1_400/220kv_SEONI Total | [10 empty] | 0.39375 | 0 | 0 | 0 | [5 empty] | 98.73%
116 | WR1T12 | ICT1_765/400kv_WARDHA | 1500 | WRTS-I
|  | ICT1_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
117 | WR1T13 | ICT2_765/400kv_WARDHA | 1500 | WRTS-I
|  | ICT2_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
118 | WR1T14 | ICT3_765/400kv_WARDHA | 1500 | WRTS-I
|  | ICT3_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
119 | WR1T15 | ICT1_765/400kv_BILASPUR | 1500 | WRTS-I |  | 2015-08-25 | 9:22 | 2015-08-25 | 13:15 |  |  |  | 0.16181 | 0 | 0 | 0 |  |  |  | H/T FOR TAN & DELTA MEASUREMENT |  |  | OSPT
|  | ICT1_765/400kv_BILASPUR Total | [10 empty] | 0.16181 | 0 | 0 | 0 | [5 empty] | 99.48%
120 | WR1T16 | ICT2_765/400kv_BILASPUR | 1500 | WRTS-I
|  | ICT2_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
121 | WR1T17 | ICT2_400/220kv_BAHATAPARA | 315 | WRTS-I
|  | ICT2_400/220kv_BAHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
122 | WR1T18 | ICT2_400/220kv_SEONI | 315 | WRTS-I |  | 2015-08-22 | 9:36 | 2015-08-22 | 19:12 |  |  |  | 0.4 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR AMP WORKS |  |  | OSPT
|  | ICT2_400/220kv_SEONI Total | [10 empty] | 0.4 | 0 | 0 | 0 | [5 empty] | 98.71%
123 | WR1T19 | ICT3_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT3_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
124 | WR1T20 | ICT1_400/220kv_WARDHA | 315 | WRTS-I
|  | ICT1_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
125 | WR1T21 | ICT2_400/220kv_WARDHA | 315 | WRTS-I
|  | ICT2_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
126 | WR1T22 | ICT3_400/220kv_WARDHA | 500 | WRTS-I
|  | ICT3_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
127 | WR1T23 | ICT1_400/220kv_SOLAPUR | 315 | WRTS-I
|  | ICT1_400/220kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
128 | WR1T24 | ICT2_400/220kv_SOLAPUR | 315 | WRTS-I
|  | ICT2_400/220kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
129 | WR1T25 | ICT1_400/220kv_PUNE | 315 | WRTS-I
|  | ICT1_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
130 | WR1T26 | ICT2_400/220kv_PUNE | 315 | WRTS-I
|  | ICT2_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
131 | WR1T27 | ICT3_400/220kv_PUNE | 315 | WRTS-I |  | 2015-06-25 | 16:27 | 2015-07-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-02-04 07:33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
|  | ICT3_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 1900-02-04 07:33 | [5 empty] | 100%
132 | WR1T28 | ICT3_765/400kv_BILASPUR | 1500 | WRTS-I
|  | ICT3_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
133 | WR1T29 | ICT1_765/400kv_KOTRA PS | 1500 | WRTS-I |  | 2015-08-27 | 11:40 | 2015-08-27 | 18:42 |  |  |  | 0.29306 | 0 | 0 | 0 |  |  |  | H/T FOR TAN & DELTA MEASUREMENT |  |  | OSPT
|  | ICT1_765/400kv_KOTRA PS Total | [10 empty] | 0.29306 | 0 | 0 | 0 | [5 empty] | 99.05%
134 | WR1T30 | ICT2_765/400kv_KOTRA PS | 1500 | WRTS-I
|  | ICT2_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
135 | WR1T31 | ICT4_765/400kv_KOTRA PS | 1500 | WRTS-I
|  | ICT4_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
136 | WR1T32 | ICT3_400/220kv_MAPUSA | 315 | WRTS-I
|  | ICT3_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
137 | WR1T33 | ICT1_765/400kv_TAMNAR PS | 1500 | WRTS-I
|  | ICT1_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
138 | WR1T34 | ICT2_765/400kv_TAMNAR PS | 1500 | WRTS-I
|  | ICT2_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
139 | WR1T35 | ICT1_765/400kv_DURG PS | 1500 | WRTS-I |  | 2015-08-06 | 11:02 | 2015-08-07 | 20:18 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:16 |  |  |  | H/T FOR CSD COMMISSIONING WORKS. |  |  | SCSD
139 | WR1T35 | ICT1_765/400kv_DURG PS | 1500 | WRTS-I |  | 2015-08-28 | 14:50 | 2015-08-28 | 20:43 |  |  |  | 0 | 0 | 0 | 0.24514 |  |  |  | H/T FOR CONNECTING THE TERTIARY SUPPLY OF ICT TO AUXILLARY EQUIPMENTS. |  |  | SCSD
|  | ICT1_765/400kv_DURG PS Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 15:09 | [5 empty] | 100%
140 | WR1T36 | ICT1_765/400kv_SOLAPUR | 1500 | WRTS-I
|  | ICT1_765/400kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
141 | WR1T37 | ICT2_765/400kv_SOLAPUR | 1500 | WRTS-I
|  | ICT2_765/400kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
142 | WR1T38 | ICT1_400/200kv_AURANGABAD | 315 | WRTS-I
|  | ICT1_400/200kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
143 | WR1T39 | ICT2_400/200kv_AURANGABAD | 315 | WRTS-I
|  | ICT2_400/200kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
144 | WR1T40 | ICT2_765/400kv_AURANGABAD | 1500 | WRTS-I
|  | ICT2_765/400kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
145 | WR1T41 | ICT3_765/400kv_TAMNAR PS | 1500 | WRTS-I
|  | ICT3_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
146 | WR1T42 | ICT3_765/400kv_KOTRA PS | 1500 | WRTS-I
|  | ICT3_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
147 | WR1T43 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I |  | 2015-08-14 | 12:40 | 2015-08-14 | 14:23 |  |  |  | 0.071528 | 0 | 0 | 0 |  |  |  | EMERGENCY SOUTAGE AVAILED FOR ATTENIDING OIL LEAKAGE |  |  | OSFT
|  | ICT1_765/400kv_AURANGABAD Total | [10 empty] | 0.071528 | 0 | 0 | 0 | [5 empty] | 99.77%
148 | WR1T44 | ICT2_765/400kv_D'JAIGARH | 1500 | WRTS-I
|  | ICT2_765/400kv_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
149 | WR1T45 | ICT1_765/400kv_D'JAIGARH | 1500 | WRTS-I
|  | ICT1_765/400kv_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
150 | WR1T46 | ICT1_400/200kv_BHADRAWATI | 315 | WRTS-I
|  | ICT1_400/200kv_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
151 | WR1T47 | ICT1_765/400kv_PUNE(GIS) | 1500 | WRTS-I |  | 2015-08-25 | 9:44 | 2015-08-25 | 20:04 |  |  |  | 0.43056 | 0 | 0 | 0 |  |  |  | H/T FOR BUSHING OIL SAMPLE COLLECTION |  |  | OMST
|  | ICT1_765/400kv_PUNE(GIS) Total | [10 empty] | 0.43056 | 0 | 0 | 0 | [5 empty] | 98.61%
152 | WR1T48 | ICT2_765/400kv_PUNE(GIS) | 1500 | WRTS-I |  | 2015-08-29 | 10:35 | 2015-08-29 | 20:01 |  |  |  | 0.39306 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED TO ATTEND THE LEAKAGE IN BUCHHOLZ RELAY OF B-PH ICT UNIT. |  |  | OMST
|  | ICT2_765/400kv_PUNE(GIS) Total | [10 empty] | 0.39306 | 0 | 0 | 0 | [5 empty] | 98.73%
153 | WR1T49 | ICT1_765/400kv_CHAMPA | 1500 | WRTS-I |  | 2015-06-23 | 14:20 | 2015-07-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1900-02-06 09:40 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
|  | ICT1_765/400kv_CHAMPA Total | [10 empty] | 0 | 0 | 0 | 1900-02-06 09:40 | [5 empty] | 100%
154 | WR1R1 | BUS REACTOR_400kV_63MVAR_RAIGARH | 63 | WRTS-I
|  | BUS REACTOR_400kV_63MVAR_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
155 | WR1R2 | BUS REACTOR_765kV_240MVAR_SEONI | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
156 | WR1R3 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_KORBA 3_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
157 | WR1R4 | BUS REACTOR_400kV_50MVAR_WARDHA | 50 | WRTS-I
|  | BUS REACTOR_400kV_50MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-11 | 10:54 | 2015-08-11 | 15:58 |  |  |  | 0 | 0 | 0 | 0.21111 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-18 | 7:20 | 2015-08-18 | 13:25 |  |  |  | 0 | 0 | 0 | 0.25347 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-19 | 9:20 | 2015-08-19 | 15:50 |  |  |  | 0 | 0 | 0 | 0.27083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-20 | 9:37 | 2015-08-20 | 16:00 |  |  |  | 0 | 0 | 0 | 0.26597 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-21 | 9:25 | 2015-08-21 | 16:38 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-26 | 7:37 | 2015-08-26 | 16:45 |  |  |  | 0 | 0 | 0 | 0.38056 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-27 | 9:43 | 2015-08-27 | 16:41 |  |  |  | 0 | 0 | 0 | 0.29028 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
158 | WR1R5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2015-08-28 | 9:10 | 2015-08-28 | 13:04 |  |  |  | 0 | 0 | 0 | 0.1625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_400kV_63MVAR_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 1900-01-01 03:15 | [5 empty] | 100%
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-18 | 9:46 | 2015-08-18 | 13:24 |  |  |  | 0 | 0 | 0 | 0.15139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-19 | 10:00 | 2015-08-19 | 15:54 |  |  |  | 0 | 0 | 0 | 0.24583 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-20 | 9:25 | 2015-08-20 | 16:35 |  |  |  | 0 | 0 | 0 | 0.29861 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-26 | 9:19 | 2015-08-26 | 17:15 |  |  |  | 0 | 0 | 0 | 0.33056 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-27 | 9:42 | 2015-08-27 | 16:51 |  |  |  | 0 | 0 | 0 | 0.29792 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-28 | 9:04 | 2015-08-28 | 13:05 |  |  |  | 0 | 0 | 0 | 0.16736 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
159 | WR1R6 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2015-08-31 | 8:28 | 2015-08-31 | 18:18 |  |  |  | 0 | 0 | 0 | 0.40972 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | BUS REACTOR_400kV_63MVAR_PARLI Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 21:38 | [5 empty] | 100%
160 | WR1R7 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2015-07-09 | 6:43 | 2015-07-31 | 24:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_400kV_50MVAR_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
161 | WR1R8 | BUS REACTOR_765kV_240MVAR_WARDHA | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
162 | WR1R9 | BUS REACTOR_765kV_240MVAR_BILASPUR | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
163 | WR1R10 | SWITCHABLE LR_765kV_BINA_SEONI | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_BINA_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
164 | WR1R11 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_SEONI 1_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
165 | WR1R12 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_SEONI 2_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
166 | WR1R13 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_D'GARH_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
167 | WR1R14 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
168 | WR1R15 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 80 | WRTS-I
|  | BUS REACTOR_400kV_80MVAR_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
169 | WR1R16 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_DURG 1_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
170 | WR1R17 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 50 | WRTS-I
|  | BUS REACTOR_400kV_50MVAR_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
171 | WR1R18 | BUS REACTOR_400kV_80MVAR_RAIPUR | 80 | WRTS-I
|  | BUS REACTOR_400kV_80MVAR_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
172 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-08-23 | 6:31 | 2015-08-23 | 17:52 |  |  |  | 0 | 0 | 0 | 0.47292 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
172 | WR1R19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2015-08-30 | 9:39 | 2015-08-30 | 16:15 |  |  |  | 0 | 0 | 0 | 0.275 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_400kV_50MVAR_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0.74792 | [5 empty] | 100%
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-18 | 9:52 | 2015-08-18 | 13:40 |  |  |  | 0 | 0 | 0 | 0.15833 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-19 | 9:21 | 2015-08-19 | 16:08 |  |  |  | 0 | 0 | 0 | 0.28264 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-20 | 9:17 | 2015-08-20 | 15:57 |  |  |  | 0 | 0 | 0 | 0.27778 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-26 | 9:39 | 2015-08-26 | 16:45 |  |  |  | 0 | 0 | 0 | 0.29583 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-28 | 9:31 | 2015-08-28 | 13:03 |  |  |  | 0 | 0 | 0 | 0.14722 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-29 | 8:47 | 2015-08-29 | 16:15 |  |  |  | 0 | 0 | 0 | 0.31111 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
173 | WR1R20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2015-08-30 | 9:40 | 2015-08-30 | 15:53 |  |  |  | 0 | 0 | 0 | 0.25903 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_400kV_80MVAR_KOLHAPUR Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 17:34 | [5 empty] | 100%
174 | WR1R21 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_DURG 2_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
175 | WR1R22 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
176 | WR1R23 | BUS REACTOR_765kV_240MVAR_DURG PS | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
177 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-08-11 | 11:02 | 2015-08-11 | 15:49 |  |  |  | 0 | 0 | 0 | 0.19931 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
177 | WR1R24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2015-08-26 | 9:45 | 2015-08-26 | 16:58 |  |  |  | 0 | 0 | 0 | 0.30069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0.5 | [5 empty] | 100%
178 | WR1R25 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | 240 | WRTS-I |  | 2015-08-31 | 12:10 | 2015-08-31 | 13:44 |  |  |  | 0.065278 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE TO SWIPE OUT SPARE REACTOR WITH B-PHASE |  |  | OSFT
|  | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR Total | [10 empty] | 0.065278 | 0 | 0 | 0 | [5 empty] | 99.79%
179 | WR1R26 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
180 | WR1R27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I |  | 2015-07-08 | 9:39 | 2015-08-10 | 8:55 |  |  |  | 0 | 0 | 0 | 1900-01-08 08:55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
180 | WR1R27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I |  | 2015-08-20 | 14:27 | 2015-08-20 | 18:19 |  |  |  | 0 | 0 | 0 | 0.16111 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | SWITCHABLE LR_765kV_A'BAD 1_WARDHA Total | [10 empty] | 0 | 0 | 0 | 1900-01-08 12:47 | [5 empty] | 100%
181 | WR1R28 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 2_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
182 | WR1R29 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
183 | WR1R30 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 2_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
184 | WR1R31 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I
|  | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
185 | WR1R32 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I
|  | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-06 | 9:02 | 2015-08-06 | 22:44 |  |  |  | 0 | 0 | 0 | 0.57083 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-07 | 06:25 | 2015-08-07 | 17:49 |  |  |  | 0 | 0 | 0 | 0.475 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-10 | 9:17 | 2015-08-10 | 18:07 |  |  |  | 0 | 0 | 0 | 0.36806 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-19 | 10:06 | 2015-08-19 | 16:43 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-20 | 7:45 | 2015-08-20 | 16:06 |  |  |  | 0 | 0 | 0 | 0.34792 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-22 | 6:56 | 2015-08-22 | 17:50 |  |  |  | 0 | 0 | 0 | 0.45417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-24 | 10:12 | 2015-08-24 | 17:38 |  |  |  | 0 | 0 | 0 | 0.30972 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-27 | 9:39 | 2015-08-27 | 17:53 |  |  |  | 0 | 0 | 0 | 0.34306 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
186 | WR1R33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2015-08-28 | 9:23 | 2015-08-28 | 14:00 |  |  |  | 0 | 0 | 0 | 0.19236 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1900-01-02 08:05 | [5 empty] | 100%
187 | WR1R34 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I |  | 2015-08-19 | 10:07 | 2015-08-19 | 16:40 |  |  |  | 0 | 0 | 0 | 0.27292 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_400kV_125MVAR_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0.27292 | [5 empty] | 100%
188 | WR1R35 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 240 | WRTS-I |  | 2015-07-01 | 8:00 | 2015-07-31 | 24:00 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
189 | WR1R36 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_BHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
190 | WR1R37 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 1_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
191 | WR1R38 | BUS REACTOR_400kV_125MVAR_RAIGARH | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
192 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-08-03 | 09:19 | 2015-08-03 | 17:58 |  |  |  | 0 | 0 | 0 | 0.36042 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-08-07 | 7:51 | 2015-08-07 | 20:41 |  |  |  | 0 | 0 | 0 | 0.53472 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-08-10 | 6:37 | 2015-08-10 | 7:59 |  |  |  | 0 | 0 | 0 | 0.056944 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-08-20 | 6:36 | 2015-08-20 | 18:29 |  |  |  | 0 | 0 | 0 | 0.49514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
192 | WR1R39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2015-08-21 | 6:44 | 2015-08-21 | 17:45 |  |  |  | 0 | 0 | 0 | 0.45903 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1899-12-31 21:45 | [5 empty] | 100%
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-01 | 10:08 | 2015-08-01 | 18:11 |  |  |  | 0 | 0 | 0 | 0.33542 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-04 | 9:38 | 2015-08-04 | 17:33 |  |  |  | 0 | 0 | 0 | 0.32986 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-08 | 7:40 | 2015-08-08 | 15:45 |  |  |  | 0 | 0 | 0 | 0.33681 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-10 | 9:30 | 2015-08-10 | 17:55 |  |  |  | 0 | 0 | 0 | 0.35069 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-11 | 6:41 | 2015-08-11 | 17:07 |  |  |  | 0 | 0 | 0 | 0.43472 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-18 | 6:55 | 2015-08-18 | 18:23 |  |  |  | 0 | 0 | 0 | 0.47778 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-19 | 7:07 | 2015-08-19 | 18:41 |  |  |  | 0 | 0 | 0 | 0.48194 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
193 | WR1R40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I |  | 2015-08-26 | 7:21 | 2015-08-26 | 18:09 |  |  |  | 0 | 0 | 0 | 0.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 1900-01-02 04:44 | [5 empty] | 100%
194 | WR1R41 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 1_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
195 | WR1R42 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 2_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
196 | WR1R43 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 80 | WRTS-I |  | 2015-08-24 | 10:20 | 2015-08-24 | 15:47 |  |  |  | 0 | 0 | 0 | 0.22708 |  |  |  | OUTAGE AVAILED FOR COMMISSIONING OF 426 TIE BAY |  |  | SCSD
|  | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0.22708 | [5 empty] | 100%
197 | WR1R44 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 80 | WRTS-I |  | 2015-08-25 | 9:24 | 2015-08-25 | 13:19 |  |  |  | 0 | 0 | 0 | 0.16319 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0.16319 | [5 empty] | 100%
198 | WR1R45 | BUS REACTOR_400kV_125MVAR_RAIPUR | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
199 | WR1R46 | BUS REACTOR_765kV_330MVAR_WARDHA | 330 | WRTS-I
|  | BUS REACTOR_765kV_330MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
200 | WR1R47 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 80 | WRTS-I
|  | SWITCHABLE LR_400kV_KARAD_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
201 | WR1R48 | BUS REACTOR_400kV_125MVAR_SEONI | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
202 | WR1R49 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
203 | WR1R50 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
204 | WR1R51 | SWITCHABLE LR_400kV_A'BAD 1_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_A'BAD 1_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
205 | WR1R52 | SWITCHABLE LR_400kV_A'BAD 2_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_A'BAD 2_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-07 | 7:52 | 2015-08-07 | 18:00 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-08 | 7:17 | 2015-08-09 | 17:14 |  |  |  | 0 | 0 | 0 | 1899-12-31 09:57 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-10 | 9:15 | 2015-08-10 | 17:57 |  |  |  | 0 | 0 | 0 | 0.3625 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-18 | 8:52 | 2015-08-18 | 13:29 |  |  |  | 0 | 0 | 0 | 0.19236 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-19 | 8:28 | 2015-08-19 | 16:00 |  |  |  | 0 | 0 | 0 | 0.31389 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-20 | 9:24 | 2015-08-20 | 16:44 |  |  |  | 0 | 0 | 0 | 0.30556 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-24 | 9:55 | 2015-08-24 | 18:19 |  |  |  | 0 | 0 | 0 | 0.35 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-25 | 7:30 | 2015-08-25 | 14:07 |  |  |  | 0 | 0 | 0 | 0.27569 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-26 | 8:55 | 2015-08-26 | 18:12 |  |  |  | 0 | 0 | 0 | 0.38681 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-27 | 9:44 | 2015-08-27 | 17:00 |  |  |  | 0 | 0 | 0 | 0.30278 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-28 | 9:06 | 2015-08-28 | 13:16 |  |  |  | 0 | 0 | 0 | 0.17361 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
206 | WR1R53 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2015-08-31 | 8:29 | 2015-08-31 | 18:11 |  |  |  | 0 | 0 | 0 | 0.40417 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  | BUS REACTOR_400kV_125MVAR_PARLI Total | [10 empty] | 0 | 0 | 0 | 1900-01-03 21:42 | [5 empty] | 100%
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-10 | 7:18 | 2015-08-10 | 17:57 |  |  |  | 0 | 0 | 0 | 0.44375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-11 | 11:03 | 2015-08-11 | 15:42 |  |  |  | 0 | 0 | 0 | 0.19375 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-18 | 8:37 | 2015-08-18 | 12:58 |  |  |  | 0 | 0 | 0 | 0.18125 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-19 | 8:31 | 2015-08-19 | 15:49 |  |  |  | 0 | 0 | 0 | 0.30417 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-20 | 9:36 | 2015-08-20 | 15:17 |  |  |  | 0 | 0 | 0 | 0.23681 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-21 | 9:29 | 2015-08-21 | 16:43 |  |  |  | 0 | 0 | 0 | 0.30139 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-24 | 9:58 | 2015-08-24 | 16:48 |  |  |  | 0 | 0 | 0 | 0.28472 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-25 | 9:37 | 2015-08-25 | 13:40 |  |  |  | 0 | 0 | 0 | 0.16875 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-26 | 7:21 | 2015-08-26 | 17:29 |  |  |  | 0 | 0 | 0 | 0.42222 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-27 | 9:52 | 2015-08-27 | 16:57 |  |  |  | 0 | 0 | 0 | 0.29514 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
207 | WR1R54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-28 | 9:39 | 2015-08-28 | 10:46 |  |  |  | 0 | 0 | 0 | 0.046528 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 1900-01-01 21:05 | [5 empty] | 100%
208 | WR1R55 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 240 | WRTS-I |  | 2015-08-28 | 10:55 | 2015-08-28 | 15:35 |  |  |  | 0 | 0 | 0 | 0.19444 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 0.19444 | [5 empty] | 100%
209 | WR1R56 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I |  | 2015-08-27 | 10:55 | 2015-08-27 | 18:14 |  |  |  | 0 | 0 | 0 | 0.30486 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  | BUS REACTOR_400kV_80MVAR_DHULE Total | [10 empty] | 0 | 0 | 0 | 0.30486 | [5 empty] | 100%
210 | WR1R57 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 3_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
211 | WR1R58 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 4_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
212 | WR1H1 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I |  | 2015-08-05 | 10:53 | 2015-08-05 | 11:23 |  |  |  | 0 | 0.020833 | 0 | 0 |  |  |  | POLE TRIPPED DUE TO VOLTAGE DIP IN AUX. SUPPLY PROVIDED BY MSETCL |  |  | OMSU
212 | WR1H1 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I |  | 2015-08-19 | 10:07 | 2015-08-19 | 18:29 |  |  |  | 0.34861 | 0 | 0 | 0 |  |  |  | H/T FOR HALF YEARLY AMP WORKS. |  |  | OSPT
212 | WR1H1 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I |  | 2015-08-29 | 15:18 | 2015-08-29 | 16:19 |  |  |  | 0.042361 | 0 | 0 | 0 |  |  |  | TRIPPED DUE TO INTERNAL COMMUNICATION CARD FAILURE ALARM ON AD4401 MAIN UNIT (N) WATCH DOG FAULT |  |  | OMST
|  | HVDC_POLE1_BHADRAWATI Total | [10 empty] | 0.39097 | 0.020833 | 0 | 0 | [5 empty] | 98.74%
213 | WR1H2 | HVDC_POLE2_BHADRAWATI | 500 | WRTS-I |  | 2015-08-03 | 02:01 | 2015-08-03 | 16:31 |  |  |  | 0.60417 | 0 | 0 | 0 |  |  |  | TRIPPED ON " VCC-2 MAIN CKT FULL FLOW - VERY LOW " ALARAM DUE TO PIPE RUPTURE IN THE VALVE COOLING SYSTEM CAUSING HEAVY DM WATER LEAKAGE. |  |  | SEFT
|  | HVDC_POLE2_BHADRAWATI Total | [10 empty] | 0.60417 | 0 | 0 | 0 | [5 empty] | 98.05%
|  | Grand Total | [10 empty] | 1900-01-09 01:10 | 1900-01-02 11:53 | 0.017361 | 1900-09-26 15:27
Formulas:
ISTS Licensee = SUBTOTAL(9,[ISTS Licensee, row above]:[ISTS Licensee, row above])
ISTS Licensee = SUBTOTAL(9,N14:[ISTS Licensee, row above])
OTHERS = SUBTOTAL(9,[OTHERS, row above]:[OTHERS, row above])
OTHERS = SUBTOTAL(9,O14:[OTHERS, row above])
Deemed Available = SUBTOTAL(9,[Deemed Available, row above]:[Deemed Available, row above])
Deemed Available = SUBTOTAL(9,Q14:[Deemed Available, row above])
Note on C88: Author:

## Element list
|  | NEW PROPOSED NAME | CODE BY WREPC | TYPE | CODE BY PGCIL | LENGTH |  | DOCO | Type of conductor | Configuration | SN
1 | 1 | 220kV KORBA(EAST)-BUDDHIPADAR III | 63 | LINE | WR1L2 | 184 | WR1-IR1 | 1999-09-01 | AAAC Zebra | Single | 1
2 | 2 | 400kV RAIPUR-RAIGARH I | 74 | LINE | WR1L43 | 217.02 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 2
3 | 3 | 400kV RAIPUR-KWPCL II | 75 | LINE | WR1L44 | 203.02 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 3
4 | 4 | 400kV KWPCL-RAIGARH II | 76 | LINE | WR1L45 | 14 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 4
5 | 5 | 400kV RAIGARH-IBEUL I | 485 | LINE | WR1L110 | 94.43 | WR1-IR2 | 2014-11-13 | ACSR Moose | Twin | 5
6 | 6 | 400kV IBEUL-JHARSUGUDA I | 486 | LINE | WR1L111 | 20.03 | WR1-IR2 | 2014-11-13 | ACSR Moose | Twin | 6
7 | 7 | 400kV JHARSUGUDA-ROURKELA I | 78 | LINE | WR1L49 | 142.45 | WR1-IR2 | 2003-04-01 | ACSR Moose | Twin | 7
8 | 8 | 400kV RAIGARH-ROURKELA II | 433 | LINE | WR1L98 | 212.46 | WR1-IR2 | 2014-07-03 | ACSR Moose | Twin | 8
9 | 9 | 400KV RANCHI-SIPAT I | 124 | LINE | WR1L50 | 405.77 | WR1-IR3 | 2009-01-01 | ACSR Moose | Twin | 9
10 | 10 | 400KV RANCHI-SIPAT II | 125 | LINE | WR1L51 | 405.77 | WR1-IR3 | 2009-01-01 | ACSR Moose | Twin | 10
11 | 11 | 400kV RAIPUR-KSK III | 430 | LINE | WR1L52 | 134.74 | WR1-IR4 | 2014-07-01 | ACSR Moose | Twin | 11
12 | 12 | 400kV KSK-RKKML III | 471 | LINE | WR1L105 | 82.248 | WR1-IR4 | 2014-10-11 | ACSR Moose | Twin | 12
13 | 13 | 400kV RKKML-RAIGARH III | 472 | LINE | WR1L106 | 3.896 | WR1-IR4 | 2014-10-11 | ACSR Moose | Twin | 13
14 | 14 | 400KV RAIPUR-KSK IV | 440 | LINE | WR1L103 | 161.82 | WR1-IR4 | 2014-07-25 | ACSR Moose | Twin | 14
15 | 15 | 400kV KSK-RAIGARH IV | 441 | LINE | WR1L97 | 113.389 | WR1-IR4 | 2014-07-25 | ACSR Moose | Twin | 15
16 | 16 | 400kV RAIGARH-JHARSUGUDA III | 81 | LINE | WR1L56 | 110.98 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 16
17 | 17 | 400kV JHARSUGUDA-ROURKELA III | 82 | LINE | WR1L57 | 143.06 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 17
18 | 18 | 400kV RAIGARH-STERLITE IV | 83 | LINE | WR1L58 | 105 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 18
19 | 19 | 400kV STERLITE-ROURKELA IV | 84 | LINE | WR1L59 | 104.28 | WR1-IR4 | 2003-04-01 | ACSR Moose | Twin | 19
20 | 20 | 765kV D'JAIGARH-BILASPUR | 403 | LINE | WR1L60 | 90 | WR1-IR5 | 2014-04-01 | Bersimis | Quad | 20
21 | 21 | 765kV D'JAIGARH-RANCHI | 404 | LINE | WR1L61 | 303 | WR1-IR5 | 2014-04-01 | Bersimis | Quad | 21
22 | 22 | 765kV D'JAIGARH- JHARSUGUDA I | 444 | LINE | WR1L101 | 149.789 | WR1-IR6 | 2014-07-31 | Bersimis | Quad | 22
23 | 23 | 765kV D'JAIGARH- JHARSUGUDA II | 445 | LINE | WR1L102 | 149.789 | WR1-IR6 | 2014-07-31 | Bersimis | Quad | 23
24 | 24 | 400kV KORBA-KORBA(WEST) | 1 | LINE | WR1L3 | 14 | CG(O&M) | 1983-01-25 | ACSR Moose | Twin | 24
25 | 25 | 400kV KORBA-BHILAI I | 2 | LINE | WR1L4 | 197 | CG(O&M) | 1984-01-01 | ACSR Moose | Twin | 25
26 | 26 | 400kV KORBA-BHILAI II | 3 | LINE | WR1L5 | 192 | CG(O&M) | 1984-01-01 | ACSR Moose | Twin | 26
27 | 27 | 400kV BHILAI-KORADI | 4 | LINE | WR1L6 | 272 | MH(O&M) | 1984-05-01 | ACSR Moose | Twin | 27
28 | 28 | 400kV KORADI-SATPURA | 6 | LINE | WR1L7 | 149 | MH(O&M) | 1987-04-18 | ACSR Moose | Twin | 28
29 | 29 | 400kV RAIPUR-BHILAI I | 14 | LINE | WR1L8 | 13 | CG(O&M) | 1989-03-28 | ACSR Moose | Twin | 29
30 | 30 | 400kV BHILAI-BHADRAVATI I | 19 | LINE | WR1L9 | 322 | WR1-LINE | 1990-01-22 | ACSR Moose | Twin | 30
31 | 31 | 400kV RAIPUR-BHADRAVATI I | 13 | LINE | WR1L10 | 333 | WR1-LINE | 1989-03-28 | ACSR Moose | Twin | 31
32 | 32 | 400kV RAIPUR-BHADRAVATI II | 86 | LINE | WR1L11 | 345.55 | WR1-LINE | 2005-06-01 | ACSR Moose | Twin | 32
33 | 33 | 400kV RAIPUR-BHADRAVATI III | 87 | LINE | WR1L12 | 345.55 | WR1-LINE | 2005-06-01 | ACSR Moose | Twin | 33
34 | 34 | 400kV BHADRAVATI-CHANDRAPUR I | 11 | LINE | WR1L13 | 20 | MH(O&M) | 1989-03-28 | ACSR Moose | Twin | 34
35 | 35 | 400kV BHADRAVATI-CHANDRAPUR II | 12 | LINE | WR1L14 | 20 | MH(O&M) | 1989-03-28 | ACSR Moose | Twin | 35
36 | 36 | 400kV BHADRAVATI-CHANDRAPUR III | 92 | LINE | WR1L15 | 22.42 | MH(O&M) | 2006-05-01 | ACSR Moose | Twin | 36
37 | 37 | 400kV BHADRAVATI-CHANDRAPUR IV | 93 | LINE | WR1L16 | 22.42 | MH(O&M) | 2006-05-01 | ACSR Moose | Twin | 37
38 | 38 | 400kV KOLHAPUR-MAPUSA I | 73 | LINE | WR1L17 | 150 | MH(O&M) | 2003-01-01 | ACSR Moose | Twin | 38
39 | 39 | 400kV KOLHAPUR-MAPUSA II | 72 | LINE | WR1L18 | 150 | MH(O&M) | 2002-12-01 | ACSR Moose | Twin | 39
40 | 40 | 400kV MAHAN-VINDHYACHAL | 8 | LINE | WR1L25 | 19 | CG(O&M) | 1988-07-24 | ACSR Moose | Twin | 40
41 | 41 | 400kV KORBA-MAHAN | 9 | LINE | WR1L26 | 196 | CG(O&M) | 1988-07-24 | ACSR Moose | Twin | 41
42 | 42 | 400kV VINDHYACHAL-KORBA II | 99 | LINE | WR1L27 | 288.994 | CG(O&M) | 2007-06-01 | ACSR Moose | Twin | 42
43 | 43 | 400kV SATPURA-SEONI | 102 | LINE | WR1L28 | 1.5 | MH(O&M) | 2007-11-01 | ACSR Moose | Twin | 43
44 | 44 | 400kV BHILAI-SEONI | 103 | LINE | WR1L29 | 1.5 | MH(O&M) | 2007-11-01 | ACSR Moose | Twin | 44
45 | 45 | 400kV BHILAI-BHATAPARA | 65 | LINE | WR1L30 | 90.453 | CG(O&M) | 2000-01-01 | ACSR Moose | Twin | 45
46 | 46 | 400kV BHATAPARA-KORBA | 64 | LINE | WR1L31 | 123.73 | CG(O&M) | 2000-01-01 | ACSR Moose | Twin | 46
47 | 47 | 400kV RAIPUR-SIPAT I | 122 | LINE | WR1L34 | 149.12 | CG(O&M) | 2008-08-01 | ACSR Moose | Twin | 47
48 | 48 | 765kV TAMNAR PS-KOTRA PS I | 392 | LINE | WR1L35 | 47.97 | CG(O&M) | 2013-11-01 | Zebra | Hexa | 48
49 | 49 | 765kV TAMNAR PS-KOTRA PS II | 393 | LINE | WR1L36 | 47.97 | CG(O&M) | 2013-11-01 | Zebra | Hexa | 49
50 | 50 | 765kV KOTRA PS-DURG PS I | 398 | LINE | WR1L37 | 239.84 | CG(O&M) | 2014-02-01 | Zebra | Hexa | 50
51 | 51 | 765kV KOTRA PS-DURG PS II | 399 | LINE | WR1L38 | 239.84 | CG(O&M) | 2014-02-01 | Zebra | Hexa | 51
52 | 52 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 418 | LINE | WR1L39 | 52.56 | MH(O&M) | 2014-04-29 | ACSR Moose | Quad | 52
53 | 53 | 400kV BHADRAVATI-DHARIWAL TPP II | 416 | LINE | WR1L40 | 18.14 | MH(O&M) | 2014-04-21 | ACSR Moose | Twin | 53
54 | 54 | 400kV DHARIWAL TPP-PARLI II | 417 | LINE | WR1L41 | 391 | MH(O&M) | 2014-04-21 | ACSR Moose | Twin | 54
55 | 55 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 419 | LINE | WR1L42 | 52.56 | MH(O&M) | 2014-04-30 | ACSR Moose | Quad | 55
56 | 56 | 400KV RAIPUR-SIPAT II | 123 | LINE | WR1L62 | 149.12 | CG(O&M) | 2008-08-01 | ACSR Moose | Twin | 56
57 | 57 | 400kV RAIPUR-SIPAT III | 22 | LINE | WR1L63 | 162.04 | CG(O&M) | 1990-02-08 | ACSR Moose | Twin | 57
58 | 58 | 765kV BILASPUR-SIPAT I | 195 | LINE | WR1L64 | 21.51 | CG(O&M) | 2013-04-01 | Bersimis | Quad | 58
59 | 59 | 765kV SEONI-BILASPUR I | 196 | LINE | WR1L65 | 337.05 | WR1-LINE | 2013-04-01 | Bersimis | Quad | 59
60 | 60 | 765kV BILASPUR-SIPAT II | 197 | LINE | WR1L66 | 22.22 | CG(O&M) | 2013-04-01 | Bersimis | Quad | 60
61 | 61 | 765kV SEONI-BILASPUR II | 198 | LINE | WR1L67 | 338.33 | WR1-LINE | 2013-04-01 | Bersimis | Quad | 61
62 | 62 | 765kV SEONI-WARDHA I | 128 | LINE | WR1L68 | 267.89 | MH(O&M) | 2009-04-01 | Bersimis | Quad | 62
63 | 63 | 765kV SEONI-WARDHA II | 165 | LINE | WR1L69 | 260.76 | MH(O&M) | 2012-03-01 | Bersimis | Quad | 63
64 | 64 | 400kV WARDHA-AKOLA I | 126 | LINE | WR1L70 | 161.87 | MH(O&M) | 2009-04-01 | ACSR Moose | Twin | 64
65 | 65 | 400kV WARDHA-AKOLA II | 127 | LINE | WR1L71 | 161.87 | MH(O&M) | 2009-04-01 | ACSR Moose | Twin | 65
66 | 66 | 400kV AURANGABAD (PG) -AKOLA I | 133 | LINE | WR1L72 | 241.23 | MH(O&M) | 2009-12-01 | ACSR Moose | Twin | 66
67 | 67 | 400kV AURANGABAD (PG) -AKOLA II | 134 | LINE | WR1L73 | 289.97 | MH(O&M) | 2009-12-01 | ACSR Moose | Twin | 67
68 | 68 | 400kV BHADRAVATI-PARLI I | 150 | LINE | WR1L74 | 378.67 | MH(O&M) | 2011-06-01 | ACSR Moose | Twin | 68
69 | 69 | 400kV PARLI(PG)-PARLI(MSETCL) I | 152 | LINE | WR1L76 | 4.96 | MH(O&M) | 2011-06-01 | ACSR Moose | Twin | 69
70 | 70 | 400kV PARLI(PG)-PARLI(MSETCL) II | 153 | LINE | WR1L77 | 4.96 | MH(O&M) | 2011-06-01 | ACSR Moose | Twin | 70
71 | 71 | 400kV KORBA-RAIPUR III | 154 | LINE | WR1L78 | 211.86 | CG(O&M) | 2011-07-01 | ACSR Moose | Twin | 71
72 | 72 | 400kV KORBA-RAIPUR IV | 155 | LINE | WR1L79 | 212.83 | CG(O&M) | 2011-07-01 | ACSR Moose | Twin | 72
73 | 73 | 400kV WARDHA-PARLI I | 156 | LINE | WR1L80 | 336.94 | MH(O&M) | 2011-08-01 | ACSR Moose | Quad | 73
74 | 74 | 400kV WARDHA-PARLI II | 157 | LINE | WR1L81 | 336.94 | MH(O&M) | 2011-08-01 | ACSR Moose | Quad | 74
75 | 75 | 400kV KORBA-BALCO | 163 | LINE | WR1L82 | 7.45 | CG(O&M) | 2012-03-01 | ACSR Moose | Twin | 75
76 | 76 | 400kV BALCO-BIRSINGHPUR | 164 | LINE | WR1L83 | 219.19 | CG(O&M) | 2012-03-01 | ACSR Moose | Twin | 76
77 | 77 | 400kV WARDHA-MAUDA II | 175 | LINE | WR1L84 | 123.84 | MH(O&M) | 2012-06-01 | ACSR Moose | Quad | 77
78 | 78 | 400kV KORBA-VANDANA | 168 | LINE | WR1L85 | 14.77 | CG(O&M) | 2012-04-01 | ACSR Moose | Twin | 78
79 | 79 | 400KV VANDANA-BIRSINGHPUR | 169 | LINE | WR1L86 | 211.87 | CG(O&M) | 2012-04-01 | ACSR Moose | Twin | 79
80 | 80 | 400KV RAIPUR-WARDHA I | 179 | LINE | WR1L87 | 370.57 | WR1-LINE | 2013-01-01 | ACSR Moose | Quad | 80
81 | 81 | 400KV RAIPUR-WARDHA II | 180 | LINE | WR1L88 | 370.57 | WR1-LINE | 2013-01-01 | ACSR Moose | Quad | 81
82 | 82 | 400KV WARDHA-IEPL | 171 | LINE | WR1L89 | 52.62 | MH(O&M) | 2012-04-01 | ACSR Moose | Quad | 82
83 | 83 | 400KV IEPL-MAUDA | 170 | LINE | WR1L90 | 70.83 | MH(O&M) | 2012-04-01 | ACSR Moose | Quad | 83
84 | 84 | 400kV RAIPUR-DURG I | 190 | LINE | WR1L91 | 21.5 | CG(O&M) | 2013-04-01 | ACSR Moose | Twin | 84
85 | 85 | 400kV RAIPUR-DURG II | 191 | LINE | WR1L92 | 21.5 | CG(O&M) | 2013-04-01 | ACSR Moose | Twin | 85
86 | 86 | 400kV RAIGARH-KOTRA PS I | 389 | LINE | WR1L93 | 6.29 | CG(O&M) | 2013-05-01 | ACSR Moose | Twin | 86
87 | 87 | 400kV RAIGARH-KOTRA PS II | 390 | LINE | WR1L94 | 6.29 | CG(O&M) | 2013-05-01 | ACSR Moose | Twin | 87
88 | 88 | 765KV DURG PS - D'JAIGARH | 424 | LINE | WR1L95 | 357.62 | CG(O&M) | 2014-05-24 | Bersimis | Quad | 88
89 | 89 | 765kV WARDHA - AURANGABAD(PG) I | 435 | LINE | WR1L99 | 347.577 | MH(O&M) | 2014-07-08 | Bersimis | Quad | 89
90 | 90 | 765kV WARDHA - AURANGABAD(PG) II | 436 | LINE | WR1L100 | 347.577 | MH(O&M) | 2014-07-08 | Bersimis | Quad | 90
91 | 91 | 400kV KORBA-SIPAT | 458 | LINE | WR1L104 | 68.653 | CG(O&M) | 2014-09-03 | ACSR Moose | Twin | 91
92 | 92 | 765kV DURG PS -WARDHA_1 | 480 | LINE | WR1L108 | 369.107 | WR1-LINE | 2014-11-17 | zebra | Hexa | 92
93 | 93 | 765kV DURG PS -WARDHA_2 | 481 | LINE | WR1L109 | 369.107 | WR1-LINE | 2014-11-17 | Zebra | Hexa | 93
94 | 94 | 765kV PUNE(GIS)-SOLAPUR | 512 | LINE | WR1L112 | 269.842 | MH(O&M) | 2015-03-02 | Bersimis | Quad | 94
95 | 95 | 400Kv PARLI-PUNE(GIS)_1 | 513 | LINE | WR1L113 | 272.202 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 95
96 | 96 | 400Kv PARLI-PUNE(GIS)_2 | 514 | LINE | WR1L114 | 272.202 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 96
97 | 97 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 515 | LINE | WR1L115 | 65 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 97
98 | 98 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 516 | LINE | WR1L116 | 65 | MH(O&M) | 2015-03-02 | ACSR Moose | Twin | 98
99 | 99 | 765kV WARDHA - AURANGABAD(PG) III |  | LINE | WR1L117 | 355 | MH(O&M) | 2015-04-01 | zebra | Hexa | 99
100 | 100 | 765kV WARDHA - AURANGABAD(PG) IV |  | LINE | WR1L118 | 355 | MH(O&M) | 2015-04-01 | zebra | Hexa | 100
101 | 101 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 |  | LINE | WR1L119 | 11.2 | MH(O&M) | 2015-04-03 | ACSR Moose | Twin | 101
102 | 102 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 |  | LINE | WR1L120 | 11.2 | MH(O&M) | 2015-04-03 | ACSR Moose | Twin | 102
103 | 103 | 765kV DURG PS- CHAMPA_1 |  | LINE | WR1L121 | 149.15 | CG(O&M) | 2015-05-30 | zebra | Hexa | 103
104 | 104 | 765kV CHAMPA- KOTRA PS |  | LINE | WR1L122 | 96.33 | CG(O&M) | 2015-05-31 | Bersimis | Quad | 104
105 | 1 | ICT1_400/220kv_RAIPUR | 233 | ICT | WR1T1 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 105
106 | 2 | ICT2_400/220kv_RAIPUR | 234 | ICT | WR1T2 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 106
107 | 3 | ICT1_400/220kv_MAPUSA | 235 | ICT | WR1T3 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 107
108 | 4 | ICT2_400/220kv_MAPUSA | 236 | ICT | WR1T4 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 108
109 | 5 | ICT1_400/220kv_BAHATAPARA | 239 | ICT | WR1T5 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 109
110 | 6 | ICT1_400/220kv_RAIGARH | 240 | ICT | WR1T6 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 110
111 | 7 | ICT2_400/220kv_RAIGARH | 241 | ICT | WR1T7 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 111
112 | 8 | ICT1_765/400kv_SEONI | 242 | ICT | WR1T8 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 112
113 | 9 | ICT2_765/400kv_SEONI | 243 | ICT | WR1T9 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 113
114 | 10 | ICT3_765/400kv_SEONI | 244 | ICT | WR1T10 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 114
115 | 11 | ICT1_400/220kv_SEONI | 245 | ICT | WR1T11 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 115
116 | 12 | ICT1_765/400kv_WARDHA | 246 | ICT | WR1T12 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 116
117 | 13 | ICT2_765/400kv_WARDHA | 247 | ICT | WR1T13 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 117
118 | 14 | ICT3_765/400kv_WARDHA | 248 | ICT | WR1T14 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 118
119 | 15 | ICT1_765/400kv_BILASPUR | 249 | ICT | WR1T15 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 119
120 | 16 | ICT2_765/400kv_BILASPUR | 250 | ICT | WR1T16 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 120
121 | 17 | ICT2_400/220kv_BAHATAPARA | 251 | ICT | WR1T17 | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | 121
122 | 18 | ICT2_400/220kv_SEONI | 252 | ICT | WR1T18 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 122
123 | 19 | ICT3_400/220kv_RAIPUR | 253 | ICT | WR1T19 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 123
124 | 20 | ICT1_400/220kv_WARDHA | 254 | ICT | WR1T20 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 124
125 | 21 | ICT2_400/220kv_WARDHA | 255 | ICT | WR1T21 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 125
126 | 22 | ICT3_400/220kv_WARDHA | 256 | ICT | WR1T22 | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | 126
127 | 23 | ICT1_400/220kv_SOLAPUR | 257 | ICT | WR1T23 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 127
128 | 24 | ICT2_400/220kv_SOLAPUR | 258 | ICT | WR1T24 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 128
129 | 25 | ICT1_400/220kv_PUNE | 259 | ICT | WR1T25 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 129
130 | 26 | ICT2_400/220kv_PUNE | 260 | ICT | WR1T26 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 130
131 | 27 | ICT3_400/220kv_PUNE | 261 | ICT | WR1T27 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 131
132 | 28 | ICT3_765/400kv_BILASPUR | 262 | ICT | WR1T28 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 132
133 | 29 | ICT1_765/400kv_KOTRA PS | 263 | ICT | WR1T29 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 133
134 | 30 | ICT2_765/400kv_KOTRA PS | 264 | ICT | WR1T30 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 134
135 | 31 | ICT4_765/400kv_KOTRA PS | 265 | ICT | WR1T31 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 135
136 | 32 | ICT3_400/220kv_MAPUSA | 266 | ICT | WR1T32 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 136
137 | 33 | ICT1_765/400kv_TAMNAR PS | 267 | ICT | WR1T33 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 137
138 | 34 | ICT2_765/400kv_TAMNAR PS | 268 | ICT | WR1T34 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 138
139 | 35 | ICT1_765/400kv_DURG PS | 269 | ICT | WR1T35 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 139
140 | 36 | ICT1_765/400kv_SOLAPUR | 270 | ICT | WR1T36 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 140
141 | 37 | ICT2_765/400kv_SOLAPUR | 271 | ICT | WR1T37 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 141
142 | 38 | ICT1_400/200kv_AURANGABAD | 272 | ICT | WR1T38 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 142
143 | 39 | ICT2_400/200kv_AURANGABAD | 273 | ICT | WR1T39 | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | 143
144 | 40 | ICT2_765/400kv_AURANGABAD | 274 | ICT | WR1T40 | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | 144
145 | 41 | ICT3_765/400kv_TAMNAR PS | 275 | ICT | WR1T41 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 145
146 | 42 | ICT3_765/400kv_KOTRA PS | 276 | ICT | WR1T42 | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | 146
147 | 43 | ICT1_765/400kv_AURANGABAD | 429 | ICT | WR1T43 | 1500 | MH(O&M) | 2014-07-01 | 1500 | 1500 | 147
148 | 44 | ICT2_765/400kv_D'JAIGARH | 426 | ICT | WR1T44 | 1500 | CG(O&M) | 2014-06-19 | 1500 | 1500 | 148
149 | 45 | ICT1_765/400kv_D'JAIGARH | 437 | ICT | WR1T45 | 1500 | CG(O&M) | 2014-07-09 | 1500 | 1500 | 149
150 | 46 | ICT1_400/200kv_BHADRAWATI | 517 | ICT | WR1T46 | 315 | MH(O&M) | 2015-03-19 | 315 | 315 | 150
151 | 47 | ICT1_765/400kv_PUNE(GIS) | 518 | ICT | WR1T47 | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | 151
152 | 48 | ICT2_765/400kv_PUNE(GIS) | 519 | ICT | WR1T48 | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | 152
153 | 49 | ICT1_765/400kv_CHAMPA |  | ICT | WR1T49 | 1500 | CG(O&M) | 2015-06-13 | 1500 | 1500 | 153
154 | 1 | BUS REACTOR_400kV_63MVAR_RAIGARH | 282 | BR | WR1R1 | 63 | CG(O&M) | 2013-04-01 | 63 | 63 | 154
155 | 2 | BUS REACTOR_765kV_240MVAR_SEONI | 288 | BR | WR1R2 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 155
156 | 3 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 279 | BR | WR1R3 | 50 | CG(O&M) | 2013-04-01 | 50 | 50 | 156
157 | 4 | BUS REACTOR_400kV_50MVAR_WARDHA | 280 | BR | WR1R4 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 157
158 | 5 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 283 | BR | WR1R5 | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | 158
159 | 6 | BUS REACTOR_400kV_63MVAR_PARLI | 284 | BR | WR1R6 | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | 159
160 | 7 | BUS REACTOR_400kV_50MVAR_PUNE | 281 | BR | WR1R7 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 160
161 | 8 | BUS REACTOR_765kV_240MVAR_WARDHA | 289 | BR | WR1R8 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 161
162 | 9 | BUS REACTOR_765kV_240MVAR_BILASPUR | 290 | BR | WR1R9 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 162
163 | 10 | SWITCHABLE LR_765kV_BINA_SEONI | 291 | BR | WR1R10 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 163
164 | 11 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 292 | BR | WR1R11 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 164
165 | 12 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 293 | BR | WR1R12 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 165
166 | 13 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 294 | BR | WR1R13 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 166
167 | 14 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 295 | BR | WR1R14 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 167
168 | 15 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 287 | BR | WR1R15 | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | 168
169 | 16 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 296 | BR | WR1R16 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 169
170 | 17 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 277 | BR | WR1R17 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 170
171 | 18 | BUS REACTOR_400kV_80MVAR_RAIPUR | 285 | BR | WR1R18 | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | 171
172 | 19 | BUS REACTOR_400kV_50MVAR_MAPUSA | 278 | BR | WR1R19 | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | 172
173 | 20 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 286 | BR | WR1R20 | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | 173
174 | 21 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 297 | BR | WR1R21 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 174
175 | 22 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 298 | BR | WR1R22 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 175
176 | 23 | BUS REACTOR_765kV_240MVAR_DURG PS | 299 | BR | WR1R23 | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | 176
177 | 24 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 300 | BR | WR1R24 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 177
178 | 25 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | 301 | BR | WR1R25 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 178
179 | 26 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | 302 | BR | WR1R26 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 179
180 | 27 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 305 | BR | WR1R27 | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | 180
181 | 28 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 306 | BR | WR1R28 | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | 181
182 | 29 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 303 | BR | WR1R29 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 182
183 | 30 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 407 | BR | WR1R30 | 240 | MH(O&M) | 2014-04-01 | 240 | 240 | 183
184 | 31 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 408 | BR | WR1R31 | 330 | CG(O&M) | 2014-04-01 | 240 | 240 | 184
185 | 32 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 415 | BR | WR1R32 | 330 | CG(O&M) | 2014-04-18 | 240 | 240 | 185
186 | 33 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 304 | BR | WR1R33 | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | 186
187 | 34 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 420 | BR | WR1R34 | 125 | MH(O&M) | 2014-04-30 | 125 | 125 | 187
188 | 35 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 425 | BR | WR1R35 | 240 | CG(O&M) | 2014-05-26 | 240 | 240 | 188
189 | 36 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 442 | BR | WR1R36 | 125 | CG(O&M) | 2014-07-26 | 125 | 125 | 189
190 | 37 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 423 | BR | WR1R37 | 240 | MH(O&M) | 2014-05-02 | 240 | 240 | 190
191 | 38 | BUS REACTOR_400kV_125MVAR_RAIGARH | 446 | BR | WR1R38 | 125 | CG(O&M) | 2014-08-01 | 125 | 125 | 191
192 | 39 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 448 | BR | WR1R39 | 240 | MH(O&M) | 2014-08-02 | 240 | 240 | 192
193 | 40 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 450 | BR | WR1R40 | 240 | MH(O&M) | 2014-08-07 | 240 | 240 | 193
194 | 41 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 456 | BR | WR1R41 | 240 | CG(O&M) | 2014-08-21 | 240 | 240 | 194
195 | 42 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 457 | BR | WR1R42 | 240 | CG(O&M) | 2014-08-29 | 240 | 240 | 195
196 | 43 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 462 | BR | WR1R43 | 80 | MH(O&M) | 2014-10-01 | 80 | 80 | 196
197 | 44 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 464 | BR | WR1R44 | 80 | MH(O&M) | 2014-10-02 | 80 | 80 | 197
198 | 45 | BUS REACTOR_400kV_125MVAR_RAIPUR | 465 | BR | WR1R45 | 125 | CG(O&M) | 2014-10-02 | 125 | 125 | 198
199 | 46 | BUS REACTOR_765kV_330MVAR_WARDHA | 475 | BR | WR1R46 | 330 | MH(O&M) | 2014-11-03 | 330 | 330 | 199
200 | 47 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 484 | BR | WR1R47 | 80 | MH(O&M) | 2014-11-26 | 80 | 80 | 200
201 | 48 | BUS REACTOR_400kV_125MVAR_SEONI | 489 | BR | WR1R48 | 125 | MH(O&M) | 2014-12-13 | 125 | 125 | 201
202 | 49 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 490 | BR | WR1R49 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 202
203 | 50 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 491 | BR | WR1R50 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 203
204 | 51 | SWITCHABLE LR_400kV_A'BAD 1_PUNE | 492 | BR | WR1R51 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 204
205 | 52 | SWITCHABLE LR_400kV_A'BAD 2_PUNE | 493 | BR | WR1R52 | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | 205
206 | 53 | BUS REACTOR_400kV_125MVAR_PARLI | 505 | BR | WR1R53 | 125 | MH(O&M) | 2015-01-10 | 125 | 125 | 206
207 | 54 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 520 | BR | WR1R54 | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | 207
208 | 55 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 521 | BR | WR1R55 | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | 208
209 | 56 | BUS REACTOR_400kV_80MVAR_DHULE | 365 | BR | WR1R56 | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | 209
210 | 57 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA |  | BR | WR1R57 | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | 210
211 | 58 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA |  | BR | WR1R58 | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | 211
212 | 1 | HVDC_POLE1_BHADRAWATI | 307 | HVDC | WR1H1 | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | 212
213 | 2 | HVDC_POLE2_BHADRAWATI | 308 | HVDC | WR1H2 | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | 213
Note on I105: DOCO earlier but splitted into two line 30.05.15 & 31.05.15

## tRIPPING
L
ELEMENT WISE TRIPPING DETAILS FOR POWERGRID WRTS-I FOR THE MONTH OF AUG-15 | [17 empty] | O
S
|  | POWERGRID WRTS-I | MONTH: | 2015-08-31 |  |  |  |  | ATTRIBUTED TO ( IN HRS:MIN) | [8 empty] | D
SN | EVENT NO. | NAME OF LINE/ICT | OWNERSHIP | Tripping No. | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | LICENCEE | OTHERS | SYSTEM CONSTR. | DEEMED AVAILABLE | OUTAGE CATEGORY | UNIT OUT DUE TO TRIPPING OF LINE | REASON | CATEGORY | Tripping Code | Restoration Code
1 | 706180 | ICT1_765/400kv_CHAMPA | WRTS-I | 0 | 2015-06-23 | 14:20 | 2015-07-31 | 24:00 | 0 | 0 | 0 | 1900-02-06 09:40 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | SPRD | 06/2544, NL-06/672 | ---
2 | 706189 | ICT3_400/220kv_PUNE | WRTS-I | 0 | 2015-06-25 | 16:27 | 2015-07-31 | 24:00 | 0 | 0 | 0 | 1900-02-04 07:33 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | SPRD | 06/2872
3 | 706201 | 765kV WARDHA - AURANGABAD(PG) III | WRTS-I | 0 | 2015-06-28 | 18:27 | 2015-08-10 | 7:40 | 0 | 0 | 0 | 1900-02-10 13:13 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 06/3198 06/831 | 08/880, NL-08/218
4 | 707001 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | WRTS-I | 0 | 2015-07-01 | 8:00 | 2015-07-31 | 24:00 | 0 | 0 | 0 | 0 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 07/07, NL-07/02
5 | 707059 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | WRTS-I | 0 | 2015-07-08 | 9:39 | 2015-08-10 | 8:55 | 0 | 0 | 0 | 1900-01-08 08:55 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 07/782, NL- 07/211 | 08/882, NL-08/220
6 | 707062 | BUS REACTOR_400kV_50MVAR_PUNE | WRTS-I | 0 | 2015-07-09 | 6:43 | 2015-07-31 | 24:00 | 0 | 0 | 0 | 0 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 07/911
7 | 707133 | 400kV KORBA-KORBA(WEST) | WRTS-I | 0 | 2015-07-17 | 11:03 | 2015-07-26 | 18:49 | 0 | 0 | 0 | 1900-01-08 07:46 | D | N | EMERGENCY OUTAGE AVAILED BY KORBA WEST (CSPTCL) | OSFD | 07/1924. | 07/2803
8 | 707163 | 765kV WARDHA - AURANGABAD(PG) IV | WRTS-I | 0 | 2015-07-23 | 23:56 | 2015-08-06 | 12:59 | 0 | 0 | 0 | 1900-01-04 12:59 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 7/2759 7/756 | 8/543 8/132
9 | 707205 | 765kV SEONI-WARDHA II | WRTS-I | 0 | 2015-07-31 | 1:19 | 2015-08-02 | 12:37 | 0 | 0 | 0 | 1899-12-31 12:37 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 7/3633 7/973 | 08/132 08/39
10 | 707206 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-07-31 | 16:50 | 2015-08-01 | 09:54 | 0 | 0 | 0 | 0.4125 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 7/3692 | 8/18
11 | 708001 | 765kV KOTRA PS-DURG PS I | WRTS-I | 0 | 2015-08-01 | 0:00 | 2015-08-31 | 24:00 | 0 | 0 | 0 | 1900-01-30 | D | N | KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD
12 | 708002 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-01 | 16:38 | 2015-08-03 | 09:28 | 0 | 0 | 0 | 1899-12-31 16:50 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/49 | 08/208.
13 | 708003 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-01 | 10:08 | 2015-08-01 | 18:11 | 0 | 0 | 0 | 0.33542 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/17, NL-08/07 | 08/56, NL-08/20
14 | 708004 | HVDC_POLE2_BHADRAWATI | WRTS-I | 0 | 2015-08-03 | 02:01 | 2015-08-03 | 16:31 | 0.60417 | 0 | 0 | 0 | L | N | TRIPPED ON " VCC-2 MAIN CKT FULL FLOW - VERY LOW " ALARAM DUE TO PIPE RUPTURE IN THE VALVE COOLING SYSTEM CAUSING HEAVY DM WATER LEAKAGE. | SEFT |  | 08/251 08/66 SR/08/66
15 | 708005 | 400kV RAIGARH-JHARSUGUDA III | WRTS-I | 2 | 2015-08-03 | 06:13 | 2015-08-03 | 08:39 | 0.10139 | 0 | 0 | 0 | L | N | TRIPPED DUE TO A/R UNSUCCESSFUL ON FAULT.86B RELAY OPERATED AT RAIGARH END. | SEMT |  | 08/201 8/56 ER/43
16 | 708006 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-08-03 | 09:19 | 2015-08-03 | 17:58 | 0 | 0 | 0 | 0.36042 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/207 08/57 | 08/258 08/70
17 | 708007 | 400kV BHADRAVATI-CHANDRAPUR III | WRTS-I | 0 | 2015-08-03 | 09:52 | 2015-08-03 | 15:18 | 0 | 0.22639 | 0 | 0 | O | N | OUTAGE AVAILED FOR REPLACEMENT OF INSULATORS FOR PUBLIC SAFETY AT NH/SH. | OMSU | 08/209 | 08/249
18 | 708008 | 400kV RAIGARH-ROURKELA II | WRTS-I | 0 | 2015-08-03 | 9:53 | 2015-08-03 | 10:56 | 0.04375 | 0 | 0 | 0 | L | N | H/T FOR REACTOR WORKS AT ROURKELA END. | OSPT | 08/210 08/58 ER/08/44 | 08/216 08/61 08/46
19 | 708009 | 400kV RAIGARH-JHARSUGUDA III | WRTS-I | 3 | 2015-08-03 | 10:01 | 2015-08-03 | 12:57 | 0.62222 | 0 | 0 | 0 | L | N | DT RECEIVED AT RAIGARH END. | OMST |  | 08/237 08/65 ER/08/50
20 | 708010 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-03 | 16:43 | 2015-08-04 | 7:09 | 0 | 0 | 0 | 0.60139 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/252 | 08/298
21 | 708011 | 765kV SEONI-WARDHA I | WRTS-I | 0 | 2015-08-03 | 15:11 | 2015-08-05 | 15:00 | 0 | 1899-12-31 23:49 | 0 | 0 | O | N | LINE TRIPPED ON B-PHASE TO EARTH FAULT DUE TO FALLING OF OPGW PILOT WIRE ROPE ON CHARGED CONDUCTOR AT LOC. 694-695-696. BROKEN PILOT WIRE RESTORED ON 05.08.15 DUE TO HEAVY RAINFALL. ONLINE OPGW WORKS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. | OMSU
22 | 708012 | 400kV BHADRAVATI-PARLI I | WRTS-I | 0 | 2015-08-04 | 7:22 | 2015-08-04 | 19:01 | 0 | 0.48542 | 0 | 0 | O | N | LINE TRIPPED ON Y-B PHASE FAULT DUE TO FALLING OF OPGW PILOT WIRE ROPE ON CHARGED CONDUCTOR AT LOC. 78-79 DURING ON LINE OPGW WORK. ONLINE OPGW WORKS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. | OMSU |  | 08/362
23 | 708013 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-04 | 9:38 | 2015-08-04 | 17:33 | 0 | 0 | 0 | 0.32986 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/309, NL-08/77 | 08/358, NL-08/90
24 | 708014 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-04 | 17:04 | 2015-08-05 | 7:16 | 0 | 0 | 0 | 0.59167 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/354 | 08/411
25 | 708015 | 765kV SEONI-WARDHA I | WRTS-I | 0 | 2015-08-05 | 15:00 | 2015-08-05 | 17:32 | 0 | 0 | 0 | 0.10556 | D | N | LINE WAS READU FOR CHARGING AT 15:00 HRS BUT KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD |  | 08/472, NL- 08/115
26 | 708016 | 400KV RAIPUR-WARDHA II | WRTS-I | 0 | 2015-08-05 | 09:17 | 2015-08-05 | 18:22 | 0.37847 | 0 | 0 | 0 | L | N | H/T FOR AMP WORKS BY PGCIL CG(O&M) | OSPT | 08/424 | 08/477
27 | 708017 | HVDC_POLE1_BHADRAWATI | WRTS-I | 0 | 2015-08-05 | 10:53 | 2015-08-05 | 11:23 | 0 | 0.020833 | 0 | 0 | O | N | POLE TRIPPED DUE TO VOLTAGE DIP IN AUX. SUPPLY PROVIDED BY MSETCL | OMSU |  | 08/440, NL-08/104,SR - 08/112
28 | 708018 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-05 | 16:13 | 2015-08-06 | 06:54 | 0 | 0 | 0 | 0.61181 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/469 | 08/515
29 | 708019 | 765kV DURG PS -WARDHA_1 | WRTS-I | 1 | 2015-08-05 | 16:43 | 2015-08-05 | 17:19 | 0.025 | 0 | 0 | 0 | L | N | LINE TRIPPED DURING REPLACEMENT OF FAULTY WTI WITH NEW WTI AT WARDHA DUE TO TOUCHING OF ELECTRICIAN HAND TO OTI DIAL. NO DEFECTS IN LINE , LINE WAS READY FOR CHARGING AT 17:19 | OMST
30 | 708020 | 765kV DURG PS -WARDHA_1 | WRTS-I | 0 | 2015-08-05 | 17:19 | 2015-08-06 | 07:01 | 0 | 0 | 0 | 0.57083 | D | N | LINE WAS READY FOR CHARGING BUT KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | LVRD |  | 08/516 8/125
31 | 708021 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-06 | 9:02 | 2015-08-06 | 22:44 | 0 | 0 | 0 | 0.57083 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/523 7/127 | 08/582 7/144
32 | 708022 | 400kV RAIPUR-BHADRAVATI II | WRTS-I | 0 | 2015-08-06 | 11:25 | 2015-08-06 | 18:47 | 0 | 0.30694 | 0 | 0 | O | N | OUTAGE AVAILED FOR REPLACEMENT OF INSULATORS FOR PUBLIC SAFETY AT NH/SH. | OMSU | 08/535 | 5/561
33 | 708023 | ICT1_765/400kv_DURG PS | WRTS-I | 0 | 2015-08-06 | 11:02 | 2015-08-07 | 20:18 | 0 | 0 | 0 | 1899-12-31 09:16 | D | N | H/T FOR CSD COMMISSIONING WORKS. | SCSD | 8/532 8/128 | 8/672 8/170
34 | 708024 | 765kV WARDHA - AURANGABAD(PG) I | WRTS-I | 0 | 2015-08-06 | 13:42 | 2015-08-10 | 8:55 | 0 | 0 | 0 | 1900-01-02 19:13 | D | N | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/546 8/134 | 08/882, NL-08/220
35 | 708025 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-06 | 16:42 | 2015-08-07 | 07:16 | 0 | 0 | 0 | 0.60694 | D | N | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/554 | 8/606
36 | 708026 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-07 | 06:25 | 2015-08-07 | 17:49 | 0 | 0 | 0 | 0.475 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/600 8/146 | 8/ 659 8/162
37 | 708027 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-08-07 | 7:51 | 2015-08-07 | 20:41 | 0 | 0 | 0 | 0.53472 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/609 8/148 | 8/675 8/171
38 | 708028 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-07 | 7:52 | 2015-08-07 | 18:00 | 0 | 0 | 0 | 0.42222 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/610 | 8/660
39 | 708029 | 400kV RAIPUR-DURG II | WRTS-I | 0 | 2015-08-07 | 9:13 | 2015-08-07 | 20:20 | 0.46319 | 0 | 0 | 0 | L | N | H/T FOR AMP WORKS BY PGCIL CG(O&M) | OSPT | 8/612 | 8/674
40 | 708030 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-07 | 16:43 | 2015-08-08 | 09:33 | 0 | 0 | 0 | 0.70139 | D | N | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/651 | 8/705
41 | 708031 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-08 | 7:17 | 2015-08-09 | 17:14 | 0 | 0 | 0 | 1899-12-31 09:57 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/697 | 8/828
42 | 708032 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-08 | 7:40 | 2015-08-08 | 15:45 | 0 | 0 | 0 | 0.33681 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/701 8/177 | 8/728 8/183
43 | 708033 | 400kV RAIPUR-DURG I | WRTS-I | 0 | 2015-08-08 | 9:11 | 2015-08-08 | 19:04 | 0.41181 | 0 | 0 | 0 | L | N | H/T FOR AMP WORKS BY PGCIL CG(O&M) | OSPT | 8/703 | 8/746
44 | 708034 | 400KV RAIPUR-WARDHA II | WRTS-I | 3 | 2015-08-08 | 11:46 | 2015-08-08 | 13:02 | 0.55278 | 0 | 0 | 0 | L | N | LINE TRIPPED DUE TO FAILURE OF LINE REAACTOR PRV CABLE AT RAIPUR. | SEFT | - | 8/726
45 | 708035 | 400kV RAIGARH-IBEUL I | WRTS-I | 0 | 2015-08-08 | 14:30 | 2015-08-08 | 17:44 | 0 | 0.13472 | 0 | 0 | O | N | LINE TRIPPED IN R-E FAULT, ZONE-2 ,FC-0.6KA AT RAIGARH END. FAULT IS IN INDBHARAT SECTION. | OMSU |  | WR/732 NL/187 ER/178
46 | 708036 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-08 | 16:46 | 2015-08-09 | 7:13 | 0 | 0 | 0 | 0.60208 | D | N | CHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/737
47 | 708037 | 400Kv PARLI-PUNE(GIS)_2 | WRTS-I | 1 | 2015-08-09 | 7:51 | 2015-08-09 | 08:03 | 0.0083333 | 0 | 0 | 0 | L | N | LINE TRIPPED DUE TO DT RECEIVED FROM PARLI END. | OMST |  | 8/787
48 | 708038 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-09 | 16:13 | 2015-08-10 | 7:13 | 0 | 0 | 0 | 0.625 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/821 | 08/873
49 | 708039 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-08-10 | 6:37 | 2015-08-10 | 7:59 | 0 | 0 | 0 | 0.056944 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/867, NL-08/212 | 08/881, NL-08/219
50 | 708040 | 765kV PUNE(GIS)-SOLAPUR | WRTS-I | 0 | 2015-08-10 | 7:07 | 2015-08-10 | 16:52 | 0.40625 | 0 | 0 | 0 | L | N | EMERGENCY OUTAGE AVAILED FOR ATTENDING HOTSPOTS. | OSFT | 08/870, NL-08/213 | 08/933, NL-08/233
51 | 708041 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-10 | 7:18 | 2015-08-10 | 17:57 | 0 | 0 | 0 | 0.44375 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/875, NL-08/214 | 08/941, NL-08/236
52 | 708042 | 765kV WARDHA - AURANGABAD(PG) III | WRTS-I | 0 | 2015-08-10 | 7:40 | 2015-08-10 | 19:52 | 0.50833 | 0 | 0 | 0 | L | N | LINE H/T FOR JUMPER TIGHTING WORKS | OMST | 08/880, NL-08/218 | -
53 | 708043 | 765kV WARDHA - AURANGABAD(PG) III | WRTS-I | 0 | 2015-08-10 | 19:52 | 2015-08-17 | 12:14 | 0 | 0 | 0 | 1900-01-05 16:22 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS DUE TO SYSTEM CONSTRAINT FOR VOLTAGE REGULATION | LVRD | - | 08/1571, NL-08/384
54 | 708044 | 765kV WARDHA - AURANGABAD(PG) IV | WRTS-I | 0 | 2015-08-10 | 9:11 | 2015-08-10 | 19:52 | 0.44514 | 0 | 0 | 0 | L | N | LINE H/T FOR JUMPER TIGHTING WORKS | OMST | 08/887, NL-08/221 | 08/1122 08/281
55 |  | 765kV WARDHA - AURANGABAD(PG) IV | WRTS-I | 0 | 2015-08-10 | 19:52 | 2015-08-12 | 13:01 | 0 | 0 | 0 | 1899-12-31 17:09 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS DUE TO SYSTEM CONSTRAINT FOR VOLTAGE REGULATION | LVRD
56 | 708045 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-10 | 9:15 | 2015-08-10 | 17:57 | 0 | 0 | 0 | 0.3625 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/888 | 08/939
57 | 708046 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-10 | 9:17 | 2015-08-10 | 18:07 | 0 | 0 | 0 | 0.36806 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/889, NL-08/222 | 08/943, NL-08/238
58 | 708047 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-10 | 9:30 | 2015-08-10 | 17:55 | 0 | 0 | 0 | 0.35069 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/890, NL-08/223 | 08/938, NL-08/234
59 | 708048 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-10 | 16:11 | 2015-08-11 | 7:22 | 0 | 0 | 0 | 0.63264 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/930 | 08/992
60 | 708049 | 400kV KORBA-RAIPUR III | WRTS-I | 0 | 2015-08-10 | 22:25 | 2015-08-10 | 22:25 | 0 | 0 | 0 | 0 | L | N | A/R SUCCESSFUL FROM BOTH ENDS AT 22:25 HRS. ON R PHASE TO E FAULT,FC-3.896KA,FL-101 KM FROM RAIPUR END. | LART | --- | ---
61 | 708050 | 400kV KORBA-RAIPUR IV | WRTS-I | 0 | 2015-08-10 | 20:33 | 2015-08-10 | 20:33 | 0 | 0 | 0 | 0 | L | N | A/R SUCCESSFUL FROM BOTH ENDS AT 20:33 HRS. ON Y PHASE TO E FAULT,FC-6.49KA,FL-59.44 KM FROM RAIPUR END. | LART | --- | ---
62 | 708051 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-11 | 6:41 | 2015-08-11 | 17:07 | 0 | 0 | 0 | 0.43472 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/989 08/249 | 08/1050 08/266
63 | 708052 | 400KV RAIPUR-WARDHA I | WRTS-I | 0 | 2015-08-11 | 9:21 | 2015-08-11 | 19:19 | 0.41528 | 0 | 0 | 0 | L | N | H/T FOR AMP WORKS BY PGCIL CG(O&M) | OSPT | 08/996 | 08/1066
64 | 708053 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-11 | 10:54 | 2015-08-11 | 15:58 | 0 | 0 | 0 | 0.21111 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1008 | 08/1041
65 | 708054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-11 | 11:03 | 2015-08-11 | 15:42 | 0 | 0 | 0 | 0.19375 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1010 08/257 | 08/1038 08/261
66 | 708055 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-11 | 11:02 | 2015-08-11 | 15:49 | 0 | 0 | 0 | 0.19931 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1011 08/258 | 08/1039 08/262
67 | 708056 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-11 | 16:11 | 2015-08-12 | 7:09 | 0 | 0 | 0 | 0.62361 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1045 | 08/1095
68 | 708057 | 400kV RAIPUR-DURG I | WRTS-I | 0 | 2015-08-11 | 21:34 | 2015-08-11 | 21:34 | 0 | 0 | 0 | 0 | L | N | 400KV RAIPUR - DURG PS CKT # 1 & 2 - A/R SUCCESSFUL FROM BOTH ENDS AT 21.34 HRS. | LART
69 | 708058 | 400kV RAIPUR-DURG II | WRTS-I | 0 | 2015-08-11 | 21:34 | 2015-08-11 | 21:34 | 0 | 0 | 0 | 0 | L | N | 400KV RAIPUR - DURG PS CKT # 1 & 2 - A/R SUCCESSFUL FROM BOTH ENDS AT 21.34 HRS. | LART
70 | 708059 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-12 | 17:12 | 2015-08-13 | 9:23 | 0 | 0 | 0 | 0.67431 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1146 | 08/1198
71 | 708060 | 765kV WARDHA - AURANGABAD(PG) IV | WRTS-I | 0 | 2015-08-12 | 17:31 | 2015-08-18 | 10:30 | 0 | 0 | 0 | 1900-01-04 16:59 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1146 08/286 | 08/1667 08/416
72 | 708061 | 400kV KORBA-RAIPUR IV | WRTS-I | 0 | 2015-08-12 | 17:39 | 2015-08-12 | 17:39 | 0 | 0 | 0 | 0 | L | N | 400KV RAIPUR -KORBA CKT # 4 - A/R SUCCESSFUL FROM BOTH ENDS AT 17.39 HRS. ON Y PHASE TO E FAULT , FL-133 KM FROM RAIPUR END.FC=2.849KA | LART | - | -
73 | 708062 | 400KV RAIPUR-WARDHA II | WRTS-I | 0 | 2015-08-12 | 17:39 | 2015-08-12 | 17:39 | 0 | 0 | 0 | 0 | L | N | A/R SUCCESSFUL FROM BOTH ENDS AT 17.39 HRS. ON R PHASE TO E FAULT , FL-81.30 KM FROM WARDHA END. PATROLLING DONE NO ABNORMALITY FOUND. | LART | - | -
74 | 708063 | 765kV SEONI-WARDHA I | WRTS-I | 2 | 2015-08-13 | 13:03 | 2015-08-13 | 18:27 | 0.225 | 0 | 0 | 0 | L | N | LINE TRIPPED ON Y-N FAULT FC-4.9KA,FL-112.3 KM FROM SEONI AND 142 KM FROM WARDHA END. LINE WAS READY FOR CHARGING AT 18:27 HRS. | LEFT | --- | ---
75 | 708064 | 765kV SEONI-WARDHA I | WRTS-I | 0 | 2015-08-13 | 18:27 | 2015-08-13 | 22:27 | 0 | 0 | 0 | 0.16667 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | --- | 08/1247 08/308
76 | 708065 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-13 | 16:16 | 2015-08-16 | 9:09 | 0 | 0 | 0 | 1900-01-01 16:53 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1219 | 08/1491
77 | 708066 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-08-14 | 9:15 | 2015-08-14 | 16:45 | 0.3125 | 0 | 0 | 0 | L | N | H/T FOR RECTIFICATION OF OPEN JUMPER AT LOC. NO. 18 IN PGCIL MH PORTION | OSFT | 08/1276 8/313
78 | 708067 | ICT1_765/400kv_AURANGABAD | WRTS-I | 0 | 2015-08-14 | 12:40 | 2015-08-14 | 14:23 | 0.071528 | 0 | 0 | 0 | L | N | EMERGENCY SOUTAGE AVAILED FOR ATTENIDING OIL LEAKAGE | OSFT | 08/1295 8/319 | 8/1308 8/322
79 | 708068 | 765kV DURG PS -WARDHA_2 | WRTS-I | 0 | 2015-08-14 | 16:45 | 2015-08-14 | 20:21 | 0 | 0 | 0 | 0.15 | D | N | LINE WAS REDAY FOR CHARGING AT 16:45HRS BUT LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD |  | 8/1337 8/330
80 | 708069 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-14 | 16:20 | 2015-08-15 | 6:42 | 0 | 0 | 0 | 0.59861 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/1319
81 | 708070 | 400kV VINDHYACHAL-KORBA II | WRTS-I | 0 | 2015-08-15 | 11:14 | 2015-08-15 | 11:29 | 0 | 0 | 0.010417 | 0 | S | N | LINE TRIPPED ON B-E FAULT , DUE TO HEAVY RAIN & THUNDER | LNCC
82 | 708071 | 400kV VINDHYACHAL-KORBA II | WRTS-I | 0 | 2015-08-15 | 11:29 | 2015-08-16 | 5:27 | 0 | 0 | 0 | 0.74861 | D | N | LINE KEPT UNCHAGRED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | LVRD |  | 08/1478
83 | 708072 | 765kV SEONI-WARDHA II | WRTS-I | 0 | 2015-08-15 | 15:50 | 2015-08-17 | 9:15 | 0 | 0 | 0 | 1899-12-31 17:25 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | LVRD | 08/1421 08/345 | 08/1561, NL-08/374
84 | 708073 | 765kV DURG PS -WARDHA_1 | WRTS-I | 0 | 2015-08-16 | 10:48 | 2015-08-17 | 9:30 | 0 | 0 | 0 | 0.94583 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION. | LPRD | 08/1498, NL-08/359 | 08/1560, NL-08/373
85 | 708074 | 400kV WARDHA-PARLI I | WRTS-I | 0 | 2015-08-16 | 10:56 | 2015-08-16 | 18:38 | 0.32083 | 0 | 0 | 0 | L | N | EMERGENCY OUTAGE AVAILED FOR ATTENDING THE DAMAGED CONDUCTOR BETWEEN LOCATION NO. 878-879 (TOP PHASE). | OSFT | 08/1499, NL-08/360 | 08/1521
86 | 708075 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-16 | 16:09 | 2015-08-17 | 7:50 | 0 | 0 | 0 | 0.65347 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1512 | 08/1552
87 | 708076 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-17 | 16:38 | 2015-08-18 | 7:10 | 0 | 0 | 0 | 0.60556 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1593 | 08/1644
88 | 708077 | 765kV SEONI-WARDHA II | WRTS-I | 0 | 2015-08-17 | 17:01 | 2015-08-17 | 17:11 | 0 | 0 | 0.0069444 | 0 | S | N | LINE TRIPPED ON O/V AT WARDHA END | GOVC | --- | ---
89 | 708078 | 765kV SEONI-WARDHA II | WRTS-I | 0 | 2015-08-17 | 17:11 | 2015-08-18 | 8:32 | 0 | 0 | 0 | 0.63958 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | --- | 08/1653 08/410
90 | 708079 | 765kV WARDHA - AURANGABAD(PG) I | WRTS-I | 0 | 2015-08-17 | 17:11 | 2015-08-26 | 10:53 | 0 | 0 | 0 | 1900-01-07 17:42 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1596, NL-08/395 | 08/2564 08/634
91 | 708080 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-18 | 6:55 | 2015-08-18 | 18:23 | 0 | 0 | 0 | 0.47778 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1643 08/407 | 08/1722 08/430
92 | 708081 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-18 | 7:20 | 2015-08-18 | 13:25 | 0 | 0 | 0 | 0.25347 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1647 | 08/1696
93 | 708082 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-18 | 8:37 | 2015-08-18 | 12:58 | 0 | 0 | 0 | 0.18125 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1656 08/411 | 08/1692 08/492
94 | 708083 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-18 | 8:52 | 2015-08-18 | 13:29 | 0 | 0 | 0 | 0.19236 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/16559 | 36008
95 | 708084 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-18 | 9:46 | 2015-08-18 | 13:24 | 0 | 0 | 0 | 0.15139 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1668 | 08/1697
96 | 708085 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-18 | 9:52 | 2015-08-18 | 13:40 | 0 | 0 | 0 | 0.15833 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1670 | 08/1695
97 | 708086 | 765kV WARDHA - AURANGABAD(PG) IV | WRTS-I | 0 | 2015-08-18 | 16:43 | 2015-08-21 | 14:33 | 0 | 0 | 0 | 1900-01-01 21:50 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1713 08/427 | 8/2036 8/519
98 | 708087 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-18 | 16:48 | 2015-08-19 | 6:44 | 0 | 0 | 0 | 0.58056 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1715 | 08/1762
99 | 708088 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-19 | 7:07 | 2015-08-19 | 18:41 | 0 | 0 | 0 | 0.48194 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1766 08/444 | 08/1840 465
100 | 708089 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-19 | 8:28 | 2015-08-19 | 16:00 | 0 | 0 | 0 | 0.31389 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1774 | 08/1820
101 | 708090 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-19 | 8:31 | 2015-08-19 | 15:49 | 0 | 0 | 0 | 0.30417 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1775 08/447 | 08/1817 08/458
102 | 708091 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-19 | 9:20 | 2015-08-19 | 15:50 | 0 | 0 | 0 | 0.27083 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1780 | 08/1818
103 | 708092 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-19 | 9:21 | 2015-08-19 | 16:08 | 0 | 0 | 0 | 0.28264 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1781 | 08/1824
104 | 708093 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-19 | 10:00 | 2015-08-19 | 15:54 | 0 | 0 | 0 | 0.24583 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1785 | 08/1819
105 | 708094 | BUS REACTOR_400kV_125MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-19 | 10:07 | 2015-08-19 | 16:40 | 0 | 0 | 0 | 0.27292 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1786 | 08/1825
106 | 708095 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-19 | 10:06 | 2015-08-19 | 16:43 | 0 | 0 | 0 | 0.27569 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/1784 08/452 | 08/1826 08/459
107 | 708096 | HVDC_POLE1_BHADRAWATI | WRTS-I | 0 | 2015-08-19 | 10:07 | 2015-08-19 | 18:29 | 0.34861 | 0 | 0 | 0 | L | N | H/T FOR HALF YEARLY AMP WORKS. | OSPT | 08/1788 08/453 SR08/406 | 08/1843 466 426
108 | 708097 | ICT1_400/220kv_MAPUSA | WRTS-I | 0 | 2015-08-19 | 15:02 | 2015-08-19 | 17:29 | 0.10208 | 0 | 0 | 0 | L | N | EMERGENCTY OUTAGE FOR ATTENDING HOT SPOT AT 220KV BUSHING | OSFT | 08/1811 | 08/1834
109 | 708098 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-19 | 16:39 | 2015-08-20 | 7:14 | 0 | 0 | 0 | 0.60764 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/1828 | 8/1877
110 | 708099 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-08-20 | 6:36 | 2015-08-20 | 18:29 | 0 | 0 | 0 | 0.49514 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1874 8/475 | 8/1920 8/492
111 | 708100 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-20 | 7:45 | 2015-08-20 | 16:06 | 0 | 0 | 0 | 0.34792 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1882 8/478 | 8/1923 8/491
112 | 708101 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-20 | 9:24 | 2015-08-20 | 16:44 | 0 | 0 | 0 | 0.30556 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1893 | 8/1927
113 | 708102 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-20 | 9:25 | 2015-08-20 | 16:35 | 0 | 0 | 0 | 0.29861 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1894 | 8/1926
114 | 708103 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-20 | 9:17 | 2015-08-20 | 15:57 | 0 | 0 | 0 | 0.27778 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1892 | 8/1922
115 | 708104 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-20 | 9:37 | 2015-08-20 | 16:00 | 0 | 0 | 0 | 0.26597 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1896 | 8/1921
116 | 708105 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-20 | 9:36 | 2015-08-20 | 15:17 | 0 | 0 | 0 | 0.23681 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1897 8/482 | 8/1919 8/491
117 | 708106 | 400kV RAIGARH-ROURKELA II | WRTS-I | 0 | 2015-08-20 | 11:17 | 2015-08-20 | 11:45 | 0.019444 | 0 | 0 | 0 | L | N | H/T FOR TAKING REACTOR IN SERVICE | OMST
118 | 708107 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | WRTS-I | 0 | 2015-08-20 | 14:27 | 2015-08-20 | 18:19 | 0 | 0 | 0 | 0.16111 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1916 8/490 | 8/1936 8/495
119 | 708108 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-20 | 16:39 | 2015-08-21 | 6:33 | 0 | 0 | 0 | 0.57917 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/1928 | 8/1978
120 | 708109 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WRTS-I | 0 | 2015-08-21 | 6:44 | 2015-08-21 | 17:45 | 0 | 0 | 0 | 0.45903 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/1980 | 8/2055
121 | 708110 | 400kV KORBA-SIPAT | WRTS-I | 0 | 2015-08-21 | 9:19 | 2015-08-22 | 19:00 | 0 | 0 | 0 | 1899-12-31 09:41 | D | N | OUTAGE AVAILED BY NTPC FOR AMP WORKS. | OSPD | 8/1997 | 08/2173
122 | 708111 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-21 | 9:25 | 2015-08-21 | 16:38 | 0 | 0 | 0 | 0.30069 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2002 | 8/2049
123 | 708112 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-21 | 9:29 | 2015-08-21 | 16:43 | 0 | 0 | 0 | 0.30139 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2003 8/512 | 8/2050 8/523
124 | 708113 | ICT1_400/220kv_SEONI | WRTS-I | 0 | 2015-08-21 | 10:18 | 2015-08-21 | 19:45 | 0.39375 | 0 | 0 | 0 | L | N | OUTAGE AVAILED FOR AMP WORKS | OSPT | 8/2011
125 | 708114 | 400kV RAIGARH-IBEUL I | WRTS-I | 0 | 2015-08-21 | 13:05 | 2015-08-21 | 17:27 | 0 | 0 | 0 | 0.18194 | D | N | LINE H/T TO ATTEND HOT SPOT IN LILO PORTION BY M/S IBEUL. FAULT IN M/S BEUL SECTION. | OSFD | WRLC 2031 / NLDC 518 / ERLDC 499 | 2047 / 522 / 507
126 | 708115 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-21 | 16:39 | 2015-08-22 | 7:15 | 0 | 0 | 0 | 0.60833 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/2048 | 08/2107
127 | 708116 | 765kV WARDHA - AURANGABAD(PG) II | WRTS-I | 0 | 2015-08-21 | 14:40 | 2015-08-21 | 23:02 | 0.34861 | 0 | 0 | 0 | L | N | H/T FOR REPLACEMENT OF MOG DIAPHRAM GASKET OF 765KV WARDHA - 2 L/RS CONSERVATORS AT AURANGABAD S/S | OMST | 08/2133, NL-08/541 | 08/2104, NL-08/534
128 |  | 765kV WARDHA - AURANGABAD(PG) II | WRTS-I | 0 | 2015-08-22 | 10:16 | 2015-08-22 | 21:16 | 0.45833 | 0 | 0 | 0 | L | N | H/T FOR REPLACEMENT OF MOG DIAPHRAM GASKET OF 765KV WARDHA - 2 L/RS CONSERVATORS AT AURANGABAD S/S | OMST
129 | 708117 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-22 | 6:56 | 2015-08-22 | 17:50 | 0 | 0 | 0 | 0.45417 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2105, NL-08/535 | 08/2170, NL-08/552
130 | 708118 | 765kV D'JAIGARH- JHARSUGUDA II | WRTS-I | 0 | 2015-08-22 | 8:14 | 2015-08-23 | 0:13 | 0 | 0 | 0 | 0.66597 | D | N | OUTAGE AVAILED BY FOR PROTECTION AUDIT APPROVED BY CEA | OSPD | 08/2115, NL-08/537,ER-08/517 | 08/2206, NL-08/560,ER-08/542
131 | 708119 | ICT2_400/220kv_SEONI | WRTS-I | 0 | 2015-08-22 | 9:36 | 2015-08-22 | 19:12 | 0.4 | 0 | 0 | 0 | L | N | OUTAGE AVAILED FOR AMP WORKS | OSPT | 08/2127 | 08/2176
132 | 708120 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-22 | 16:43 | 2015-08-23 | 6:22 | 0 | 0 | 0 | 0.56875 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2160 | 08/2219
133 | 708121 | 400kV KORBA-MAHAN | WRTS-I | 1 | 2015-08-23 | 4:47 | 2015-08-23 | 4:57 | 0.0069444 | 0 | 0 | 0 | L | N | LINE TRIPPED DUE ON R PHASE TO E FAULT,FC-3.502 KA, FL-114 KM FROM KORBA END AND FC-1.25KA,FL-99.3 KM FROM MAHAN END. | LEFT | --- | ---
134 | 708122 | 400kV KORBA-MAHAN | WRTS-I | 0 | 2015-08-23 | 4:57 | 2015-08-23 | 8:05 | 0 | 0.13056 | 0 | 0 | O | N | LINE CHARGING DELAYED BY NTPC KORBA END. | OMSU | --- | 08/2229
135 | 708123 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-23 | 6:22 | 2015-08-23 | 17:32 | 0 | 0 | 0 | 0.46528 | D | N | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE | LCSD | 08/2219 | 08/2270
136 | 708124 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-23 | 6:26 | 2015-08-23 | 17:37 | 0 | 0 | 0 | 0.46597 | D | N | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE | LCSD | 08/2218 | 08/2269
137 | 708125 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-08-23 | 6:31 | 2015-08-23 | 17:52 | 0 | 0 | 0 | 0.47292 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2220 | 08/2272
138 | 708126 | 765kV D'JAIGARH- JHARSUGUDA I | WRTS-I | 0 | 2015-08-23 | 8:27 | 2015-08-23 | 23:09 | 0 | 0 | 0 | 0.6125 | D | N | H/T FOR PROTECTION AUDIT APPROVED BY CEA. | OSPD | 08/2233 | 08/2293, NL-08/569,ER-08/558
139 | 708127 | ICT1_400/220kv_MAPUSA | WRTS-I | 0 | 2015-08-23 | 9:00 | 2015-08-23 | 13:46 | 0 | 0 | 0 | 0.19861 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION DUE TO OUTAGE ON BOTH KOLHAPUR-MAPUSA LINE. | SPRD | 08/2239 | 08/2258
140 | 708128 | 400Kv PARLI-PUNE(GIS)_1 | WRTS-I | 0 | 2015-08-23 | 9:43 | 2015-08-23 | 19:57 | 0 | 0 | 0 | 0.42639 | D | N | OUTAGE AVAILED FOR RECTIFICATION/FIXING OF BALANCE SPACERS | LCSD | 08/2243 | 08/2282
141 | 708129 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | WRTS-I | 0 | 2015-08-23 | 9:46 | 2015-08-23 | 20:37 | 0 | 0 | 0 | 0.45208 | D | N | OUTAGE AVAILED FOR RECTIFICATION/FIXING OF BALANCE SPACERS | LCSD | 08/2243 | 08/2284
142 | 708130 | ICT2_400/220kv_MAPUSA | WRTS-I | 0 | 2015-08-23 | 14:00 | 2015-08-23 | 19:02 | 0 | 0 | 0 | 0.20972 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION | SPRD | 08/2260 | 08/2279
143 | 708131 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-23 | 17:32 | 2015-08-24 | 7:46 | 0 | 0 | 0 | 0.59306 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2270 | 08/2313
144 | 708132 | 400kV RAIGARH-JHARSUGUDA III | WRTS-I | 0 | 2015-08-24 | 9:21 | 2015-08-24 | 19:54 | 0 | 0 | 0 | 0.43958 | D | N | H/T FOR PROTECTION AUDIT APPROVED BY CEA. | OSPD | 08/2323, NL-08/576, ER-08/561 | 08/2387, NL-08/595, ER-08/574
145 | 708133 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-24 | 9:55 | 2015-08-24 | 18:19 | 0 | 0 | 0 | 0.35 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2330 | 08/2380
146 | 708134 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-24 | 9:58 | 2015-08-24 | 16:48 | 0 | 0 | 0 | 0.28472 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2331, NL-08/577 | 08/2364, NL-08/588
147 | 708135 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-24 | 10:12 | 2015-08-24 | 17:38 | 0 | 0 | 0 | 0.30972 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2332, NL-08/578 | 08/2366, NL-08/589
148 | 708136 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | WRTS-I | 0 | 2015-08-24 | 10:20 | 2015-08-24 | 15:47 | 0 | 0 | 0 | 0.22708 | D | N | OUTAGE AVAILED FOR COMMISSIONING OF 426 TIE BAY | SCSD | 08/2337 | 08/2359
149 | 708137 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-24 | 17:16 | 2015-08-25 | 6:58 | 0 | 0 | 0 | 0.57083 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2371 | 08/2416
150 | 708138 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-25 | 7:30 | 2015-08-25 | 14:07 | 0 | 0 | 0 | 0.27569 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2421 | 08/2467
151 | 708139 | ICT1_765/400kv_PUNE(GIS) | WRTS-I | 0 | 2015-08-25 | 9:44 | 2015-08-25 | 20:04 | 0.43056 | 0 | 0 | 0 | L | N | H/T FOR BUSHING OIL SAMPLE COLLECTION | OMST | 08/22434 08/602 | 08/2497 08/623
152 | 708140 | ICT1_765/400kv_BILASPUR | WRTS-I | 0 | 2015-08-25 | 9:22 | 2015-08-25 | 13:15 | 0.16181 | 0 | 0 | 0 | L | N | H/T FOR TAN & DELTA MEASUREMENT | OSPT | 08/2436 08/604 | 08/2459 611
153 | 708141 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | WRTS-I | 0 | 2015-08-25 | 9:24 | 2015-08-25 | 13:19 | 0 | 0 | 0 | 0.16319 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2437 | 08/2464
154 | 708142 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-25 | 9:37 | 2015-08-25 | 13:40 | 0 | 0 | 0 | 0.16875 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2438 605 | 08/2465
155 | 708143 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-25 | 16:16 | 2015-08-26 | 6:47 | 0 | 0 | 0 | 0.60486 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2475 | 08/2525
156 | 708144 | 765kV WARDHA - AURANGABAD(PG) III | WRTS-I | 0 | 2015-08-25 | 17:41 | 2015-08-31 | 24:00 | 0 | 0 | 0 | 1900-01-05 06:19 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2481 617
157 | 708145 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-26 | 7:21 | 2015-08-26 | 17:29 | 0 | 0 | 0 | 0.42222 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2529 08/628 | 08/2608 08/646
158 | 708146 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-26 | 7:37 | 2015-08-26 | 16:45 | 0 | 0 | 0 | 0.38056 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 0/2531 | 08/2604
159 | 708147 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | WRTS-I | 0 | 2015-08-26 | 7:21 | 2015-08-26 | 18:09 | 0 | 0 | 0 | 0.45 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2530 08/629 | 08/2626….08/651
160 | 708148 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-26 | 8:55 | 2015-08-26 | 18:12 | 0 | 0 | 0 | 0.38681 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2543 | 08/2606
161 | 708149 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-26 | 9:19 | 2015-08-26 | 17:15 | 0 | 0 | 0 | 0.33056 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2548 | 08/2607
162 | 708150 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-26 | 9:39 | 2015-08-26 | 16:45 | 0 | 0 | 0 | 0.29583 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2553 | 08/2603
163 | 708151 | BUS REACTOR_765kV_240MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-26 | 9:45 | 2015-08-26 | 16:58 | 0 | 0 | 0 | 0.30069 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2554 08/632 | 08/2605 08/644
164 | 708152 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-26 | 16:43 | 2015-08-27 | 7:06 | 0 | 0 | 0 | 0.59931 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2602 | 8/2668
165 | 708153 | 765kV SEONI-WARDHA I | WRTS-I | 0 | 2015-08-26 | 17:43 | 2015-08-28 | 7:01 | 0 | 0 | 0 | 1899-12-31 13:18 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/2806 8/690 | 8/2618 8/647
166 | 708154 | 400kV RAIGARH-IBEUL I | WRTS-I | 1 | 2015-08-26 | 21:54 | 2015-08-27 | 0:02 | 0.088889 | 0 | 0 | 0 | L | N | TRIPPED ON B- E FAULT. FC=15.2KA, FL:4.94KM FROM RAIGARH END. | LEFT | ---- | 08/2653 08/657 & ER/08/607
167 | 708155 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-27 | 9:42 | 2015-08-27 | 16:51 | 0 | 0 | 0 | 0.29792 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2692 | 8/2739
168 | 708156 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-27 | 9:44 | 2015-08-27 | 17:00 | 0 | 0 | 0 | 0.30278 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2692 | 8/2740
169 | 708157 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-27 | 9:39 | 2015-08-27 | 17:53 | 0 | 0 | 0 | 0.34306 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2693 8/664 | 8/2749 8/676
170 | 708158 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-27 | 9:43 | 2015-08-27 | 16:41 | 0 | 0 | 0 | 0.29028 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2694 | 8/2738
171 | 708159 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-27 | 9:52 | 2015-08-27 | 16:57 | 0 | 0 | 0 | 0.29514 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2696 8/666 | 8/2737 8/675
172 | 708160 | BUS REACTOR_400kV_80MVAR_DHULE | WRTS-I | 0 | 2015-08-27 | 10:55 | 2015-08-27 | 18:14 | 0 | 0 | 0 | 0.30486 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2700 | 313592
173 | 708161 | ICT1_765/400kv_KOTRA PS | WRTS-I | 0 | 2015-08-27 | 11:40 | 2015-08-27 | 18:42 | 0.29306 | 0 | 0 | 0 | L | N | H/T FOR TAN & DELTA MEASUREMENT | OSPT | 8/2707 8/668 | 8/2762 8/680
174 | 708162 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-27 | 16:49 | 2015-08-28 | 6:43 | 0 | 0 | 0 | 0.57917 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 8/2744 | 8/2801
175 | 708163 | 765kV D'JAIGARH-RANCHI | WRTS-I | 0 | 2015-08-28 | 8:34 | 2015-08-28 | 22:21 | 0 | 0 | 0 | 0.57431 | D | N | H/T FOR PROTECTION AUDIT APPROVED BY CEA. | OSPD | 8/2818 8/693 8/695ER | 8/2918 8/713 8/724ER
176 | 708164 | 400kV WARDHA-AKOLA II | WRTS-I | 0 | 2015-08-28 | 9:05 | 2015-08-28 | 19:07 | 0 | 0 | 0 | 0.41806 | D | N | H/T FOR AMP WORKS BY MSETCL | OSPD | 8/2825 | 8/2902
177 | 708165 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-28 | 9:04 | 2015-08-28 | 13:05 | 0 | 0 | 0 | 0.16736 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2826 | 8/2855
178 | 708166 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-28 | 9:06 | 2015-08-28 | 13:16 | 0 | 0 | 0 | 0.17361 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2827 | 8/2856
179 | 708167 | BUS REACTOR_400kV_63MVAR_SOLAPUR | WRTS-I | 0 | 2015-08-28 | 9:10 | 2015-08-28 | 13:04 | 0 | 0 | 0 | 0.1625 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2828 | 8/2854
180 | 708168 | BUS REACTOR_765kV_240MVAR_AURANGABAD | WRTS-I | 0 | 2015-08-28 | 9:23 | 2015-08-28 | 14:00 | 0 | 0 | 0 | 0.19236 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2831 8/695 | 8/2859 8/701
181 | 708169 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-28 | 9:31 | 2015-08-28 | 13:03 | 0 | 0 | 0 | 0.14722 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2833 | 8/2853
182 | 708170 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WRTS-I | 0 | 2015-08-28 | 9:39 | 2015-08-28 | 10:46 | 0 | 0 | 0 | 0.046528 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2834 8/696 | 8/2841 8/698
183 | 708171 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WRTS-I | 0 | 2015-08-28 | 10:55 | 2015-08-28 | 15:35 | 0 | 0 | 0 | 0.19444 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 8/2842 8/699 | 8/2869 8/706
184 | 708172 | ICT1_765/400kv_DURG PS | WRTS-I | 0 | 2015-08-28 | 14:50 | 2015-08-28 | 20:43 | 0 | 0 | 0 | 0.24514 | D | N | H/T FOR CONNECTING THE TERTIARY SUPPLY OF ICT TO AUXILLARY EQUIPMENTS. | SCSD | 8/2866 8/703 | 8/2911 8/712
185 | 708173 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-29 | 8:47 | 2015-08-29 | 16:15 | 0 | 0 | 0 | 0.31111 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/2945 | 08/2984
186 | 708174 | ICT2_765/400kv_PUNE(GIS) | WRTS-I | 0 | 2015-08-29 | 10:35 | 2015-08-29 | 20:01 | 0.39306 | 0 | 0 | 0 | L | N | OUTAGE AVAILED TO ATTEND THE LEAKAGE IN BUCHHOLZ RELAY OF B-PH ICT UNIT. | OMST | 08/2957,NL-08/720 | 08/3005,NL-08/735
187 | 708175 | HVDC_POLE1_BHADRAWATI | WRTS-I | 0 | 2015-08-29 | 15:18 | 2015-08-29 | 16:19 | 0.042361 | 0 | 0 | 0 | L | N | TRIPPED DUE TO INTERNAL COMMUNICATION CARD FAILURE ALARM ON AD4401 MAIN UNIT (N) WATCH DOG FAULT | OMST | --- | 08/2981,NL-08/730,ER-08/750
188 | 708176 | 765kV D'JAIGARH- JHARSUGUDA II | WRTS-I | 0 | 2015-08-29 | 16:05 | 2015-08-29 | 18:06 | 0 | 0 | 0 | 0.084028 | D | N | OUTAGE AVAILED FOR FRA TEST ON 765KV JABALPUR # 4 - L/R AT DHARAMJAYGARH S/S.(JABALPUR # 4 LINE REACTOR IS ADJACENT TO THE JHARSUGUDA CKT # 2). | SCSD | 08/2981,NL-08/730,ER-08/750 | 08/2994,NL-08/734,ER-08/760
189 | 708177 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-29 | 17:10 | 2015-08-30 | 7:00 | 0 | 0 | 0 | 0.57639 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/2987 | 08/3042
190 | 708178 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-30 | 8:54 | 2015-08-30 | 15:32 | 0 | 0 | 0 | 0.27639 | D | N | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE | LCSD | 08/3050 | ---
191 | 708179 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-30 | 9:35 | 2015-08-30 | 15:46 | 0 | 0 | 0 | 0.25764 | D | N | OUTAGE AVAILED FOR STRINGING OF 765 KV KUDGI-KOLHAPUR D/C LINE OVER 400 KV KOLHAPUR - MAPUSA D/C LINE | LCSD | 08/3053 | 08/3073
192 | 708180 | BUS REACTOR_400kV_50MVAR_MAPUSA | WRTS-I | 0 | 2015-08-30 | 9:39 | 2015-08-30 | 16:15 | 0 | 0 | 0 | 0.275 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/3054 | 08/3078
193 | 708181 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WRTS-I | 0 | 2015-08-30 | 9:40 | 2015-08-30 | 15:53 | 0 | 0 | 0 | 0.25903 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | SVRD | 08/3055 | 08/3076
194 | 708182 | 400kV KOLHAPUR-MAPUSA II | WRTS-I | 0 | 2015-08-30 | 15:32 | 2015-08-31 | 07:00 | 0 | 0 | 0 | 0.64444 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | --- | ---
195 | 708183 | 765kV SEONI-WARDHA I | WRTS-I | 0 | 2015-08-30 | 18:32 | 2015-08-31 | 6:36 | 0 | 0 | 0 | 0.50278 | D | N | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/3087, NL-08/745 | 08/3121, NL-08/749
196 | 708184 | BUS REACTOR_400kV_63MVAR_PARLI | WRTS-I | 0 | 2015-08-31 | 8:28 | 2015-08-31 | 18:18 | 0 | 0 | 0 | 0.40972 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/3135 | 08/3186
197 | 708185 | BUS REACTOR_400kV_125MVAR_PARLI | WRTS-I | 0 | 2015-08-31 | 8:29 | 2015-08-31 | 18:11 | 0 | 0 | 0 | 0.40417 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/3136 | 08/3183
198 | 708186 | 400kV BHADRAVATI-CHANDRAPUR IV | WRTS-I | 0 | 2015-08-31 | 9:41 | 2015-08-31 | 14:26 | 0 | 0.19792 | 0 | 0 | O | N | FOR INSULATOR REPLACMENT ON NH, RAILWAY CROSSING FOR PUBLIC SAFTEY | OMSU | 08/3139 | 08/3162
199 | 708187 | 765kV D'JAIGARH-RANCHI | WRTS-I | 1 | 2015-08-31 | 11:07 | 2015-08-31 | 11:59 | 0.036111 | 0 | 0 | 0 | L | N | MAL OPRETION OF PLCC AT RANCHI AND DT RECIVED AT DHARAMJAYGARH, FAULT UNDER-ER-1 | SPLT | …… | 08/3149 NL-08/756 ER-08/788
200 | 708188 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | WRTS-I | 0 | 2015-08-31 | 12:10 | 2015-08-31 | 13:44 | 0.065278 | 0 | 0 | 0 | L | N | EMERGENCY OUTAGE TO SWIPE OUT SPARE REACTOR WITH B-PHASE | OSFT | 08/3151 NL-757 | 08/3160 Nl-08/759
201 | 708189 | 400kV KOLHAPUR-MAPUSA I | WRTS-I | 0 | 2015-08-31 | 16:42 | 2015-08-31 | 24:00 | 0 | 0 | 0 | 0.30417 | D | N | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | LVRD | 08/3173
202 | 708190 | 400kV RAIGARH-ROURKELA II | WRTS-I | 1 | 2015-08-31 | 9:41 | 2015-08-31 | 22:44 | 0.54375 | 0 | 0 | 0 | L | N | A/R SUCCESSFUL AT RAIGARH END BUT LINE WAS TRIPPED AT ROURKELA END ON R-E FAULT. FAULY UNDER ER-2 | LEFT | …….. | 08/3199 NL-763 ER-800
203 | 708191 | 400KV RAIPUR-WARDHA I | WRTS-I | 0 | 2015-08-31 | 14:58 | 2015-08-31 | 14:58 | 0 | 0 | 0 | 0 | L | N | A/R SUCCESSFUL AT BOTH END, B-E FAULT DISTT-48 KM FROM WARDHA END AND 227.7KM FROM RAIPUR END. UNER PGCIL MH PORTION. | LART
TOTAL |  | GRAND TOTAL IN HRS:MIN | [6 empty] | 1900-01-09 01:10 | 1900-01-02 11:53 | 0.017361 | 1900-09-26 15:27
|  | GRAND TOTAL IN HRS | [6 empty] | 241.17 | 83.88 | 0.42 | 6495.45
Ouatge hrs due to more than 2 tripping
|  | 400kV RAIPUR-WARDHA II | [6 empty] | 12
|  | 400kV RAIGARH-JHARSUGUDA III | [6 empty] | 12
|  | TOTAL HRS AS PER WRLDC= | [6 empty] | 217.17
|  | GRAND TOTAL HRS (includingOuatge hrs due to more than 2 tripping) = | [6 empty] | 241.17
Formulas:
ATTRIBUTED TO ( IN HRS:MIN) = SUM(J6:[ATTRIBUTED TO ( IN HRS:MIN), row above])
OTHERS = SUM(K6:[OTHERS, row above])
SYSTEM CONSTR. = SUM(L6:[SYSTEM CONSTR., row above])
DEEMED AVAILABLE = SUM(M6:[DEEMED AVAILABLE, row above])
Note on C17: Author:

## Sheet3
Total Element Nos. | To be included | Element having tripping
1 | 1 | 5
2 | 2 | 8
3 | 3 | 16
4 | 4 | 21
5 | 0 | 22
6 | 6 | 23
7 | 7 | 24
8 | 0 | 32
9 | 9 | 36
10 | 10 | 37
11 | 11 | 38
12 | 12 | 39
13 | 13 | 41
14 | 14 | 42
15 | 15 | 50
16 | 0 | 62
17 | 17 | 63
18 | 18 | 65
19 | 19 | 68
20 | 20 | 71
21 | 0 | 72
22 | 0 | 73
23 | 0 | 80
24 | 0 | 81
25 | 25 | 84
26 | 26 | 85
27 | 27 | 89
28 | 28 | 90
29 | 29 | 91
30 | 30 | 92
31 | 31 | 93
32 | 0 | 94
33 | 33 | 95
34 | 34 | 96
35 | 35 | 98
36 | 0 | 99
37 | 0 | 100
38 | 0 | 107
39 | 0 | 108
40 | 40 | 115
41 | 0 | 119
42 | 0 | 122
43 | 43 | 131
44 | 44 | 133
45 | 45 | 139
46 | 46 | 147
47 | 47 | 151
48 | 48 | 152
49 | 49 | 153
50 | 0 | 158
51 | 51 | 159
52 | 52 | 160
53 | 53 | 172
54 | 54 | 173
55 | 55 | 177
56 | 56 | 178
57 | 57 | 180
58 | 58 | 186
59 | 59 | 187
60 | 60 | 188
61 | 61 | 192
62 | 0 | 193
63 | 0 | 196
64 | 64 | 197
65 | 0 | 206
66 | 66 | 207
67 | 67 | 208
68 | 0 | 209
69 | 69 | 212
70 | 70 | 213
71 | 0
72 | 0
73 | 0
74 | 74
75 | 75
76 | 76
77 | 77
78 | 78
79 | 79
80 | 0
81 | 0
82 | 82
83 | 83
84 | 0
85 | 0
86 | 86
87 | 87
88 | 88
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 97
98 | 0
99 | 0
100 | 0
101 | 101
102 | 102
103 | 103
104 | 104
105 | 105
106 | 106
107 | 0
108 | 0
109 | 109
110 | 110
111 | 111
112 | 112
113 | 113
114 | 114
115 | 0
116 | 116
117 | 117
118 | 118
119 | 0
120 | 120
121 | 121
122 | 0
123 | 123
124 | 124
125 | 125
126 | 126
127 | 127
128 | 128
129 | 129
130 | 130
131 | 0
132 | 132
133 | 0
134 | 134
135 | 135
136 | 136
137 | 137
138 | 138
139 | 0
140 | 140
141 | 141
142 | 142
143 | 143
144 | 144
145 | 145
146 | 146
147 | 0
148 | 148
149 | 149
150 | 150
151 | 0
152 | 0
153 | 0
154 | 154
155 | 155
156 | 156
157 | 157
158 | 0
159 | 0
160 | 0
161 | 161
162 | 162
163 | 163
164 | 164
165 | 165
166 | 166
167 | 167
168 | 168
169 | 169
170 | 170
171 | 171
172 | 0
173 | 0
174 | 174
175 | 175
176 | 176
177 | 0
178 | 0
179 | 179
180 | 0
181 | 181
182 | 182
183 | 183
184 | 184
185 | 185
186 | 0
187 | 0
188 | 0
189 | 189
190 | 190
191 | 191
192 | 0
193 | 0
194 | 194
195 | 195
196 | 0
197 | 0
198 | 198
199 | 199
200 | 200
201 | 201
202 | 202
203 | 203
204 | 204
205 | 205
206 | 0
207 | 0
208 | 0
209 | 0
210 | 210
211 | 211
212 | 0
213 | 0

## Sheet4
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213