## Index
WRTS-I SYSTEM AVAILABILITY DETAILS :
AVAILABILITY INDEX FOR NOV-2012
[8 empty] | 0 | 0
SN | Element Name | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element | Target
[6 empty] | attr. to | attr. to | Individual |  | NSC1 | OH1*NSC1*CktKm1 | Cktkm1 * NSC1 | THM *Cktkm1 * NSC1 | NAFM | Availability | wise | Availability
[6 empty] | POWERGRID | OTHERS | THM | Ckrkm1 | [5 empty] | =100-100*O | Availability | as per
|  | Hrs | Mints | Hrs | Mints | OH1 | OH2 | =30*24-OH2 | [7 empty] | Achieved | SOP
[6 empty] | Hours | Hours
1 | 220kV Tarapur - Boisar |  |  |  |  | 0 | 0 | 720 | 20.56 | 1 | 0 | 20.56 | 14803.2 | 0 | 100 | 100% | 90% | 0%
2 | 400kV Korba-Korba (W) |  |  |  |  | 0 | 0 | 720 | 14 | 2 | 0 | 28 | 20160 | 0 | 100 | 100% | 90% | 0%
3 | 400kV Korba-Bhilai # 1 |  |  |  |  | 0 | 0 | 720 | 197 | 2 | 0 | 394 | 283680 | 0 | 100 | 100% | 90% | 0%
4 | 400kV Korba-Bhilai # 2 |  |  |  |  | 0 | 0 | 720 | 192 | 2 | 0 | 384 | 276480 | 0 | 100 | 100% | 90% | 0%
5 | 400kV Bhilai-Koradi |  |  |  |  | 0 | 0 | 720 | 272 | 2 | 0 | 544 | 391680 | 0 | 100 | 100% | 90% | 0%
6 | 400kV Koradi-Satpura |  |  |  |  | 0 | 0 | 720 | 149 | 2 | 0 | 298 | 214560 | 0 | 100 | 100% | 90% | 0%
7 | 400kV Bhilai - Raipur # 1 |  |  |  |  | 0 | 0 | 720 | 13 | 2 | 0 | 26 | 18720 | 0 | 100 | 100% | 90% | 0%
8 | 400 KV Bhilai - Bhadrawati |  |  |  |  | 0 | 0 | 720 | 322 | 2 | 0 | 644 | 463680 | 0 | 100 | 100% | 90% | 0%
9 | 400 kV Raipur - Bhadrawati # 1 |  |  |  |  | 0 | 0 | 720 | 333 | 2 | 0 | 666 | 479520 | 0 | 100 | 100% | 90% | 0%
10 | 400kV Raipur - Bhadrawati # 2 |  |  |  |  | 0 | 0 | 720 | 345.55 | 2 | 0 | 691.1 | 497592 | 0 | 100 | 100% | 90% | 0%
11 | 400kV Raipur - Bhadrawati # 3 |  |  | 0 | 10 | 0 | 0.16667 | 719.8333 | 345.55 | 2 | 0 | 691.1 | 497476.8167 | 0 | 100 | 100% | 90% | 0%
12 | 400kV B'vati-Chandrapur # 1 |  |  |  |  | 0 | 0 | 720 | 20 | 2 | 0 | 40 | 28800 | 0 | 100 | 100% | 90% | 0%
13 | 400kV B'vati-Chandrapur # 2 |  |  |  |  | 0 | 0 | 720 | 20 | 2 | 0 | 40 | 28800 | 0 | 100 | 100% | 90% | 0%
14 | 400kV B'vati-Chandrapur # 3 |  |  |  |  | 0 | 0 | 720 | 22.42 | 2 | 0 | 44.84 | 32284.8 | 0 | 100 | 100% | 90% | 0%
15 | 400kV B'vati-Chandrapur # 4 |  |  |  |  | 0 | 0 | 720 | 22.42 | 2 | 0 | 44.84 | 32284.8 | 0 | 100 | 100% | 90% | 0%
16 | 400kV Kolhapur - Mapusa # 1 |  |  | 0 | 15 | 0 | 0.25 | 719.75 | 150 | 2 | 0 | 300 | 215925 | 0 | 100 | 100% | 90% | 0%
17 | 400kV Kolhapur - Mapusa # 2 |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 150 | 2 | 0 | 300 | 215975 | 0 | 100 | 100% | 90% | 0%
18 | 400kV Tarapur - Padghe # 1 |  |  |  |  | 0 | 0 | 720 | 91.119 | 2 | 0 | 182.238 | 131211.36 | 0 | 100 | 100% | 90% | 0%
19 | 400kV Tarapur - Padghe # 2 |  |  |  |  | 0 | 0 | 720 | 91.119 | 2 | 0 | 182.238 | 131211.36 | 0 | 100 | 100% | 90% | 0%
20 | 400 KV BOISAR - Padge |  |  |  |  | 0 | 0 | 720 | 101 | 2 | 0 | 202 | 145440 | 0 | 100 | 100% | 90% | 0%
21 | 400kV Tarapur - Boisar #1 |  |  |  |  | 0 | 0 | 720 | 20.881 | 2 | 0 | 41.762 | 30068.64 | 0 | 100 | 100% | 90% | 0%
22 | 400kV Tarapur - Boisar #2 |  |  |  |  | 0 | 0 | 720 | 20.881 | 2 | 0 | 41.762 | 30068.64 | 0 | 100 | 100% | 90% | 0%
23 | 400 KV Vapi - Boisar |  |  |  |  | 0 | 0 | 720 | 91 | 2 | 0 | 182 | 131040 | 0 | 100 | 100% | 90% | 0%
24 | 400kV Vindhyachal - Mahan ( Essar) |  |  |  |  | 0 | 0 | 720 | 19 | 2 | 0 | 38 | 27360 | 0 | 100 | 100% | 90% | 0%
25 | 400kV Mahan ( Essar) - Korba |  |  |  |  | 0 | 0 | 720 | 196 | 2 | 0 | 392 | 282240 |  |  | 100% | 90% | 0%
26 | 400 kV Vindyanchal-Korba #2 |  |  |  |  | 0 | 0 | 720 | 288.994 | 2 | 0 | 577.988 | 416151.36 | 0 | 100 | 100% | 90% | 0%
27 | 400 KV Satpura - Seoni (LILO portion) |  |  |  |  | 0 | 0 | 720 | 1.507 | 2 | 0 | 3.014 | 2170.08 | 0 | 100 | 100% | 90% | 0%
28 | 400 KV Seoni - Bhilai (LILO portion) |  |  |  |  | 0 | 0 | 720 | 1.498 | 2 | 0 | 2.996 | 2157.12 | 0 | 100 | 100% | 90% | 0%
29 | 400KV Korba - Bhatapara |  |  |  |  | 0 | 0 | 720 | 123.73 | 2 | 0 | 247.46 | 178171.2 | 0 | 100 | 100% | 90% | 0%
30 | 400KV Bhilai- Bhatapara |  |  |  |  | 0 | 0 | 720 | 90.453 | 2 | 0 | 180.906 | 130252.32 | 0 | 100 | 100% | 90% | 0%
31 | 400kV Korba - Pathadi |  |  |  |  | 0 | 0 | 720 | 39.536 | 2 | 0 | 79.072 | 56931.84 | 0 | 100 | 100% | 90% | 0%
32 | 400kV Pathadi - Sipat |  |  |  |  | 0 | 0 | 720 | 29.117 | 2 | 0 | 58.234 | 41928.48 | 0 | 100 | 100% | 90% | 0%
33 | 400 KV D/C Raipur-Sipat # 1 |  |  |  |  | 0 | 0 | 720 | 149.12 | 2 | 0 | 298.24 | 214732.8 | 0 | 100 | 100% | 90% | 0%
34 | 400 KV D/C Raipur-Sipat # 2 |  |  |  |  | 0 | 0 | 720 | 149.12 | 2 | 0 | 298.24 | 214732.8 | 0 | 100 | 100% | 90% | 0%
35 | 400 kV S/C Raipur-Sipat # 3 |  |  |  |  | 0 | 0 | 720 | 160 | 2 | 0 | 320 | 230400 | 0 | 100 | 100% | 90% | 0%
36 | 765 KV S/C Sipat - Bilaspur # 1 |  |  |  |  | 0 | 0 | 720 | 21.507 | 4 | 0 | 86.028 | 61940.16 | 0 | 100 | 100% | 90% | 0%
37 | 765 KV S/C Bilaspur - Seoni # 1 |  |  |  |  | 0 | 0 | 720 | 337.046 | 4 | 0 | 1348.184 | 970692.48 | 0 | 100 | 100% | 90% | 0%
38 | 765 KV S/C Sipat - Bilaspur # 2 |  |  |  |  | 0 | 0 | 720 | 22.216 | 4 | 0 | 88.864 | 63982.08 | 0 | 100 | 100% | 90% | 0%
39 | 765 KV S/C Bilaspur - Seoni # 2 |  |  |  |  | 0 | 0 | 720 | 338.33 | 4 | 0 | 1353.32 | 974390.4 | 0 | 100 | 100% | 90% | 0%
40 | 765 KV S/C Seoni-Wardha # 1 |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 267.894 | 4 | 0 | 1071.576 | 771445.422 | 0 | 100 | 100% | 90% | 0%
41 | 400 KV D/C Wardha-Akola # 1 |  |  | 0 | 10 | 0 | 0.16667 | 719.8333 | 161.865 | 2 | 0 | 323.73 | 233031.645 | 0 | 100 | 100% | 90% | 0%
42 | 400 KV D/C Wardha-Akola # 2 |  |  |  |  | 0 | 0 | 720 | 161.865 | 2 | 0 | 323.73 | 233085.6 | 0 | 100 | 100% | 90% | 0%
43 | 400 KV D/C Akola-Aurangabad # 1 |  |  |  |  | 0 | 0 | 720 | 241.23 | 2 | 0 | 482.46 | 347371.2 | 0 | 100 | 100% | 90% | 0%
44 | 400 KV D/C Akola-Aurangabad # 2 | 0 | 12 |  |  | 0.2 | 0 | 720 | 241.23 | 2 | 96.492 | 482.46 | 347371.2 | 0.00027778 | 99.9722 | 99.97% | 90% | -0.02778%
45 | 400KV Bhadrawati-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 378.667 | 2 | 0 | 757.334 | 545280.48 |  |  | 100% | 90% | 0%
46 | 400KV Bhadrawati-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 378.667 | 2 | 0 | 757.334 | 545280.48 |  |  | 100% | 90% | 0%
47 | 400KV Parli-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 4.958 | 2 | 0 | 9.916 | 7139.52 |  |  | 100% | 90% | 0%
48 | 400KV Parli-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 4.958 | 2 | 0 | 9.916 | 7139.52 |  |  | 100% | 90% | 0%
49 | 400KV Korba-Raipur # 3 | 3 | 0 | 2 | 36 | 3 | 2.6 | 717.4 | 212.83 | 2 | 1276.98 | 425.66 | 305368.484 |  |  | 99.58% | 90% | -0.4182%
50 | 400KV Korba-Raipur # 4 |  |  |  |  | 0 | 0 | 720 | 212.83 | 2 | 0 | 425.66 | 306475.2 |  |  | 100% | 90% | 0%
51 | 400KV Wardha-Parli # 1 |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 336.939 | 4 | 0 | 1347.756 | 970272.007 |  |  | 100% | 90% | 0%
52 | 400KV Wardha-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 336.939 | 4 | 0 | 1347.756 | 970384.32 |  |  | 100% | 90% | 0%
53 | 400KV Korba-Balco ( Portion of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 720 | 7.454 | 2 | 0 | 14.908 | 10733.76 |  |  | 100% | 90% | 0%
54 | 400KV D/C Balco-Birsinghpur ( Portion of Korba-Biringsinghpur # 2) |  |  | 7 | 28 | 0 | 7.4667 | 712.5333 | 219.188 | 2 | 0 | 438.376 | 312357.5125 |  |  | 100% | 90% | 0%
55 | 400KV D/C Vandana-Birsingpur (Portion of Korba-Birsingpur # 1) |  |  |  |  | 0 | 0 | 720 | 211.874 | 2 | 0 | 423.748 | 305098.56 |  |  | 100% | 90% | 0%
56 | 765 KV S/C Seoni-Wardha # 2 |  |  |  |  | 0 | 0 | 720 | 260.763 | 4 | 0 | 1043.052 | 750997.44 | 0 | 100 | 100% | 90% | 0%
57 | 400KV Mouda-Wardha # 1 |  |  | 0 | 15 | 0 | 0.25 | 719.75 | 123.45 | 4 | 0 | 493.8 | 355412.55 |  |  | 100% | 90% | 0%
58 | 400KV Mouda-Wardha # 2 |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 123.45 | 4 | 0 | 493.8 | 355494.85 |  |  | 100% | 90% | 0%
59 | 400KV Korba-Vandana ( Portion of Korba-Birsingpur # 1) |  |  |  |  | 0 | 0 | 720 | 14.768 | 2 | 0 | 29.536 | 21265.92 |  |  | 100% | 90% | 0%
60 | 400KV Raipur - Raigarh # 1 |  |  |  |  | 0 | 0 | 720 | 217.02 | 2 | 0 | 434.04 | 312508.8 |  |  | 100% | 90% | 0%
61 | 400KV Raipur - Raigarh # 2 |  |  | 0 | 10 | 0 | 0.16667 | 719.8333 | 217.02 | 2 | 0 | 434.04 | 312436.46 |  |  | 100% | 90% | 0%
62 | 400kV Raigarh - Rourkela # 1 |  |  |  |  | 0 | 0 | 720 | 212.46 | 2 | 0 | 424.92 | 305942.4 |  |  | 100% | 90% | 0%
63 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] |  |  | 0 | 12 | 0 | 0.2 | 719.8 | 99.46 | 2 | 0 | 198.92 | 143182.616 |  |  | 100% | 90% | 0%
64 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 720 | 113 | 2 | 0 | 226 | 162720 |  |  | 100% | 90% | 0%
65 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 134.74 | 2 | 0 | 269.48 | 194003.1433 |  |  | 100% | 90% | 0%
66 | 400KV KSK (Mahanadi) - Raigarh [lilo of Raipur - Raigarh # 3] |  |  | 0 | 38 | 0 | 0.63333 | 719.3667 | 86.14 | 2 | 0 | 172.28 | 123932.4893 |  |  | 100% | 90% | 0%
67 | 400KV Raipur - Raigarh # 4 |  |  |  |  | 0 | 0 | 720 | 220.884 | 2 | 0 | 441.768 | 318072.96 |  |  | 100% | 90% | 0%
68 | 400KV Raigarh-Rourkela # 3 |  |  |  |  | 0 | 0 | 720 | 209.283 | 2 | 0 | 418.566 | 301367.52 |  |  | 100% | 90% | 0%
69 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] |  |  | 44 | 16 | 0 | 44.2667 | 675.7333 | 105 | 2 | 0 | 210 | 141904 |  |  | 100% | 90% | 0%
70 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] |  |  |  |  | 0 | 0 | 720 | 104.28 | 2 | 0 | 208.56 | 150163.2 |  |  | 100% | 90% | 0%
71 | 400KV D/C Sipat-Ranchi # 1 |  |  |  |  | 0 | 0 | 720 | 405.772 | 2 | 0 | 811.544 | 584311.68 |  |  | 100% | 90% | 0%
72 | 400KV D/C Sipat-Ranchi # 2 |  |  |  |  | 0 | 0 | 720 | 405.772 | 2 | 0 | 811.544 | 584311.68 |  |  | 100% | 90% | 0%
73 | 220KV Korba-Bhudhipadar # 3 |  |  |  |  | 0 | 0 | 720 | 184 | 1 | 0 | 184 | 132480 |  |  | 100% | 90% | 0%
1 | 400/220kV ICT # 1 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
2 | 400/220kV ICT # 2 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
3 | 400/220kV ICT # 1 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
4 | 400/220kV ICT # 2 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
5 | 400/220kV ICT # 1 / Boisar | 4 | 37 |  |  | 4.6167 | 0 | 720 | 315 | 2.5 | 3635.625 | 787.5 | 567000 | 0.006412 | 99.3588 | 99.36% | 90% | -0.6412%
6 | 400/220kV ICT # 2 / Boisar |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
7 | 400/220kV ICT # 1 / Bhatapara |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
8 | 400/220kV ICT # 1 / Raigarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
9 | 400/220kV ICT # 2 / Raigarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
10 | 765/400kV AT # 1 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100% | 90% | 0%
11 | 765/400kV AT # 2 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100% | 90% | 0%
12 | 765/400kV AT # 3 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100% | 90% | 0%
13 | 400/220kV ICT # 1 / Seoni |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90% | 0%
14 | 765/220kV AT # 1 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 |  |  | 100% | 90% | 0%
15 | 765/220kV AT # 2 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 |  |  | 100% | 90% | 0%
16 | 765/220kV AT # 3 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 |  |  | 100% | 90% | 0%
17 | 765/220kV AT # 1 / Bilaspur |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 |  |  | 100% | 90% | 0%
18 | 765/220kV AT # 2 / Bilaspur |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 |  |  | 100% | 90% | 0%
19 | 400/220kV ICT # 2 / Bhatapara |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
20 | 400/220kV ICT # 2 / Seoni |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
21 | 400/220kV ICT # 3 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
22 | 400/220kV ICT # 1 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
23 | 400/220kV ICT # 2 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
24 | 400/220kV ICT # 3 / Wardha |  |  |  |  | 0 | 0 | 720 | 500 | 2.5 | 0 | 1250 | 900000 |  |  | 100% | 90% | 0%
25 | 400/220kV ICT # 1 / Solapur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
26 | 400/220kV ICT # 2 / Solapur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
27 | 400/220kV ICT # 1 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
28 | 400/220kV ICT # 2 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
29 | 400/220kV ICT # 3 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 |  |  | 100% | 90% | 0%
30 | 765/220kV AT # 3 / Bilaspur |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 |  |  | 100% | 90% | 0%
1 | Bus reactor / B'vati |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90% | 0%
2 | Bus Reactor / Raipur |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 0 | 100 | 100% | 90% | 0%
3 | Bus Reactor / Mapusa |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90% | 0%
4 | Bus Reactor / Kolhapur |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 0 | 100 | 100% | 90% | 0%
5 | Bus Reactor / Raigarh |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90% | 0%
6 | Bus Reactor / Seoni (3 x 80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100% | 90% | 0%
7 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 |  |  | 100% | 90% | 0%
8 | Bus Reactor / Wardha |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90% | 0%
9 | Bus Reactor / Solapur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 |  |  | 100% | 90% | 0%
10 | Bus Reactor / Parli |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 |  |  | 100% | 90% | 0%
11 | Bus Reactor / Pune |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 |  |  | 100% | 90% | 0%
12 | 765KV Bus Reactor / Wardha(3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100% | 90% | 0%
13 | 765KV Bus Reactor / Bilaspur(3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100% | 90% | 0%
1 | 500 MW HVDC B'vati Pole # 1 | [14 empty] | 99.15% | 85% | -0.85%
2 | 500 MW HVDC B'vati Pole # 2 | [14 empty] | 100% | 85% | 0%
173

## Nov-2012
ANNEXURE-I
OUTAGE DETAILS FOR THE MONTH OF : NOVEMBER-2012
AC TRANSMISSION LINE
SN | EVENT No. | ELEMENTS NAME | TRIPPING |  | RESTORATION |  | OUTAGE HOURS (HRS.MIN) | [11 empty] | CAT. CODE | DETAILED REASONS OF TRIPPING | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
|  |  | DATE | TIME | DATE | TIME | Attributed to PGCIL HRS:MIN | Attributed to PGCIL |  | Attributed to Other HRS:MIN | Attributed to Other |  | Attributed to sys conts. HRS:MIN | Attributed to sys conts. |  | Outage deemed available HRS:MIN | Outage deemed available |  |  |  | TRIPPING | CHARGING | A | B | C | D=A*B*C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN | [8 empty] | 720
1 |  | 220kV Tarapur-Boisar
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20.56 | 1 | 0 | 0 | 720 | 20.56 | 14803.2 | 0 | 100%
2 |  | 400KV Korba-Korba(W)
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 14 | 2 | 0 | 0 | 720 | 28 | 20160 | 0 | 100%
3 |  | 400KV Korba-Bhilai # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 197 | 2 | 0 | 0 | 720 | 394 | 283680 | 0 | 100%
4 |  | 400KV Korba - Bhilai # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 192 | 2 | 0 | 0 | 720 | 384 | 276480 | 0 | 100%
5 |  | 400KV Bhilai- Koradi | [5 empty] | 0 | 0
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 272 | 2 | 0 | 0 | 720 | 544 | 391680 | 0 | 100%
6 |  | 400KV Koradi - Satpura
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 149 | 2 | 0 | 0 | 720 | 298 | 214560 | 0 | 100%
7 |  | 400KV Raipur-Bhilai#1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 2 | 0 | 0 | 720 | 26 | 18720 | 0 | 100%
8 |  | 400KV Bhilai-Bhadrawati
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 322 | 2 | 0 | 0 | 720 | 644 | 463680 | 0 | 100%
9 |  | 400KV Raipur - Bhadrawati # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 333 | 2 | 0 | 0 | 720 | 666 | 479520 | 0 | 100%
10 |  | 400KV Bhadrawati - Raipur # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 345.55 | 2 | 0 | 0 | 720 | 691.1 | 497592 | 0 | 100%
11 | 711011 | 400KV Raipur-Bhadrawati # 3 | 2012-11-03 | 1:31 | 2012-11-03 | 1:41 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to Over Voltage at Raipur end & DT receive at Bhadrawati end | … | ..
| 711012 | 400KV Raipur-Bhadrawati # 3 | 2012-11-03 | 1:41 | 2012-11-03 | 5:56 | [9 empty] | 0.17708 | 4 | 15 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | … | .WR-11/214
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 10 |  | 4 | 15
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 4.25 |  |  |  |  | 345.55 | 2 | 0 | 0 | 719.8333 | 691.1 | 497476.8167 | 0 | 100%
12 |  | 400KV Bhadrawati- Chandrapur # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20 | 2 | 0 | 0 | 720 | 40 | 28800 | 0 | 100%
13 |  | 400KV Bhadrawati- Chandrapur # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20 | 2 | 0 | 0 | 720 | 40 | 28800 | 0 | 100%
14 |  | 400KV Bhadrawati-Chandrapur # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 22.42 | 2 | 0 | 0 | 720 | 44.84 | 32284.8 | 0 | 100%
15 |  | 400KV Bhadrawati-Chandrapur # 4
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 22.42 | 2 | 0 | 0 | 720 | 44.84 | 32284.8 | 0 | 100%
16 | 710076 | 400KV Kolhapur-Mapusa # 1 | 2012-11-01 | 0:00 | 2012-11-01 | 11:32 | [9 empty] | 11:32 | 11 | 32 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/2363 | 11/50
| 711017 | 400KV Kolhapur-Mapusa # 1 | 2012-11-05 | 17:28 | 2012-11-07 | 9:33 | [9 empty] | 1899-12-31 16:05 | 40 | 5 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/401 | 11/574
| 711026 | 400KV Kolhapur-Mapusa # 1 | 2012-11-08 | 19:41 | 2012-11-13 | 18:09 | [9 empty] | 1900-01-03 22:28 | 118 | 28 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/754 | 11/1181
| 711045 | 400KV Kolhapur-Mapusa # 1 | 2012-11-14 | 1:39 | 2012-11-14 | 1:44 | [6 empty] | 0.0034722 | 0 | 5 |  | 0 | 0 | GOVC | Line tripped on overvoltage at kolhapur end , DT received at Mapusa end . | -- | 11/1198
| 711046 | 400KV Kolhapur-Mapusa # 1 | 2012-11-14 | 1:44 | 2012-11-14 | 5:37 | [9 empty] | 0.16181 | 3 | 53 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/1198
| 711068 | 400KV Kolhapur-Mapusa # 1 | 2012-11-19 | 0:00 | 2012-11-19 | 0:10 | [6 empty] | 0.0069444 | 0 | 10 |  | 0 | 0 | GOVC | Line was tripped on overvoltage at Kolhapur end. | -- | --
| 711069 | 400KV Kolhapur-Mapusa # 1 | 2012-11-19 | 0:10 | 2012-11-27 | 15:48 | [9 empty] | 1900-01-07 15:38 | 207 | 38 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/2399
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 15 |  | 379 | 156
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.25 |  |  | 381.6 |  |  |  |  | 150 | 2 | 0 | 0 | 719.75 | 300 | 215925 | 0 | 100%
17 | 711003 | 400KV Kolhapur - Mapusa # 2 | 2012-11-01 | 16:41 | 2012-11-05 | 11:38 | [9 empty] | 1900-01-02 18:57 | 90 | 57 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/85 | 11/366
| 711020 | 400KV Kolhapur - Mapusa # 2 | 2012-11-07 | 16:24 | 2012-11-08 | 11:47 | [9 empty] | 0.80764 | 19 | 23 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/614 | 11/688
| 711039 | 400KV Kolhapur - Mapusa # 2 | 2012-11-13 | 16:30 | 2012-11-13 | 16:35 | [6 empty] | 0.0034722 | 0 | 5 |  | 0 | 0 | GOVC | Line tripped on overvoltage at kolhapur end , DT received at Mapusa end . | -- | --
| 711040 | 400KV Kolhapur - Mapusa # 2 | 2012-11-13 | 16:35 | 2012-11-19 | 5:54 | [9 empty] | 1900-01-04 13:19 | 133 | 19 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/1610
| 711088 | 400KV Kolhapur - Mapusa # 2 | 2012-11-27 | 15:53 | 2012-11-30 | 24:00 | [9 empty] | 1900-01-02 08:07 | 80 | 7 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/2400
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 322 | 106
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 323.7667 |  |  |  |  | 150 | 2 | 0 | 0 | 719.9167 | 300 | 215975 | 0 | 100%
18 |  | 400KV Tarapur - Padghe # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 91.119 | 2 | 0 | 0 | 720 | 182.238 | 131211.36 | 0 | 100%
19 |  | 400KV Tarapur - Padghe # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 91.119 | 2 | 0 | 0 | 720 | 182.238 | 131211.36 | 0 | 100%
20 |  | 400KV Boisar - Padghe
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 101 | 2 | 0 | 0 | 720 | 202 | 145440 | 0 | 100%
21 | 711082 | 400kV Tarapur-Boisar # 1 | 2012-11-26 | 9:08 | 2012-11-26 | 20:03 | [9 empty] | 0.45486 | 10 | 55 | OSPD | outage availed by M/S NPCIL for maintenance work | 11/2245 | 11/2327
| 711085 | 400kV Tarapur-Boisar # 1 | 2012-11-27 | 9:09 | 2012-11-27 | 19:10 | [9 empty] | 0.41736 | 10 | 1 | OSPD | Outage availed by M/S NPCIL for maintenance work | 11/2364 | 11/2369
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 20 | 56
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 20.9333 |  |  |  |  | 20.881 | 2 | 0 | 0 | 720 | 41.762 | 30068.64 | 0 | 100%
22 |  | 400kV Tarapur-Boisar # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20.881 | 2 | 0 | 0 | 720 | 41.762 | 30068.64 | 0 | 100%
23 |  | 400KV Boisar - Vapi
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 91 | 2 | 0 | 0 | 720 | 182 | 131040 | 0 | 100%
24 |  | 400KV Vindhyachal - Mahan
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 19 | 2 | 0 | 0 | 720 | 38 | 27360 | 0 | 100%
25 |  | 400KV Korba - Mahan
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 196 | 2 | 0 | 0 | 720 | 392 | 282240 | 0 | 100%
26 |  | 400KV Korba - Vindhyachal # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 288.99 | 2 | 0 | 0 | 720 | 577.98 | 416145.6 | 0 | 100%
27 |  | 400KV Seoni-Satpura
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1.507 | 2 | 0 | 0 | 720 | 3.014 | 2170.08 | 0 | 100%
28 |  | 400KV Seoni-Bhilai
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1.498 | 2 | 0 | 0 | 720 | 2.996 | 2157.12 | 0 | 100%
29 |  | 400KV Korba-Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 123.73 | 2 | 0 | 0 | 720 | 247.46 | 178171.2 | 0 | 100%
30 |  | 400KV Bhilai -Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 90.453 | 2 | 0 | 0 | 720 | 180.906 | 130252.32 | 0 | 100%
31 |  | 400kv Korba- Pathadi
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 39.536 | 2 | 0 | 0 | 720 | 79.072 | 56931.84 | 0 | 100%
32 |  | 400KV Sipat-Pathadi
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.117 | 2 | 0 | 0 | 720 | 58.234 | 41928.48 | 0 | 100%
33 | 711004 | 400KV Raipur-Sipat # 1 | 2012-11-01 | 22:22 | 2012-11-09 | 10:57 | [9 empty] | 1900-01-06 12:35 | 180 | 35 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/115 | 11/795
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 180 | 35
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 180.5833 |  |  |  |  | 149.12 | 2 | 0 | 0 | 720 | 298.24 | 214732.8 | 0 | 100%
34 |  | 400KV Raipur-Sipat # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 149.12 | 2 | 0 | 0 | 720 | 298.24 | 214732.8 | 0 | 100%
35 |  | 400KV Raipur - Sipat # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 160 | 2 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
[17 empty] | 0 | 0
36 |  | 765KV Sipat- Bilaspur# 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21.507 | 4 | 0 | 0 | 720 | 86.028 | 61940.16 | 0 | 100%
37 |  | 765KV Seoni-Bilaspur # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337.046 | 4 | 0 | 0 | 720 | 1348.184 | 970692.48 | 0 | 100%
38 | 711075 | 765KV Sipat- Bilaspur# 2 | 2012-11-23 | 10:13 | 2012-11-23 | 13:57 | [9 empty] | 0.15556 | 3 | 44 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1947 | 11/1968
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 3 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 3.7333 |  |  |  |  | 22.216 | 4 | 0 | 0 | 720 | 88.864 | 63982.08 | 0 | 100%
39 |  | 765KV Seoni - Bilaspur# 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 338.33 | 4 | 0 | 0 | 720 | 1353.32 | 974390.4 | 0 | 100%
40 | 711047 | 765KV Seoni - Wardha # 1 | 2012-11-14 | 17:27 | 2012-11-14 | 18:48 | [9 empty] | 0.05625 | 1 | 21 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 1/883 | 01/1026
| 711050 | 765KV Seoni - Wardha # 1 | 2012-11-15 | 22:03 | 2012-11-16 | 7:33 | [9 empty] | 0.39583 | 9 | 30 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 02/238 | WRLC:- 02/697, NLDC:-02/48
| 711061 | 765KV Seoni - Wardha # 1 | 2012-11-17 | 22:23 | 2012-11-18 | 12:15 | [9 empty] | 0.57778 | 13 | 52 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 02/1791 | 02/1956
| 711080 | 765KV Seoni - Wardha # 1 | 2012-11-25 | 22:10 | 2012-11-26 | 9:22 | [9 empty] | 0.46667 | 11 | 12 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | WR:02/2074, NLDC:229 | 02/2179
| 711095 | 765KV Seoni - Wardha # 1 | 2012-11-29 | 21:06 | 2012-11-29 | 21:11 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due on Over Voltage | 03/ 01 | 03/ 71
| 711096 | 765KV Seoni - Wardha # 1 | 2012-11-29 | 21:11 | 2012-11-29 | 21:19 | [9 empty] | 0.0055556 | 0 | 8 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 03/119 | WR : 03/235, NLDC: 03/34
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 34 | 123
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 36.05 |  |  |  |  | 267.894 | 4 | 0 | 0 | 719.9167 | 1071.576 | 771445.422 | 0 | 100%
41 | 711055 | 400KV Wardha-Akola # 1 | 2012-11-16 | 21:58 | 2012-11-16 | 22:03 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line Tripped on over voltage at akola end ,DT Received at wardha end and line keep out as per WRLDC instruction | -- | 11/1415
| 711056 | 400KV Wardha-Akola # 1 | 2012-11-16 | 22:03 | 2012-11-17 | 7:52 | [9 empty] | 0.40903 | 9 | 49 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1415 | 11/1432
| 711099 | 400KV Wardha-Akola # 1 | 2012-11-29 | 21:06 | 2012-11-29 | 21:11 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due on Over Voltage | ..
| 711100 | 400KV Wardha-Akola # 1 | 2012-11-29 | 21:11 | 2012-11-29 | 21:49 | [9 empty] | 0.026389 | 0 | 38 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | .. | 11/2634
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 10 |  | 9 | 87
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 10.45 |  |  |  |  | 161.865 | 2 | 0 | 0 | 719.8333 | 323.73 | 233031.645 | 0 | 100%
42 | 711062 | 400kv Wardha-Akola # 2 | 2012-11-18 | 0:32 | 2012-11-18 | 6:29 | [9 empty] | 0.24792 | 5 | 57 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1521 | 11/1533
| 711074 | 400kv Wardha-Akola # 2 | 2012-11-20 | 22:00 | 2012-11-21 | 7:06 | [9 empty] | 0.37917 | 9 | 6 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1773 | 11/1789
| 711089 | 400kv Wardha-Akola # 2 | 2012-11-28 | 14:03 | 2012-11-28 | 17:46 | [9 empty] | 0.15486 | 3 | 43 | OSPD | Outage availed by M/S MSCETCL for attending hotspots in tie bay at Akola end | 11/2496 | 11/2514
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 17 | 106
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 18.7667 |  |  |  |  | 161.865 | 2 | 0 | 0 | 720 | 323.73 | 233085.6 | 0 | 100%
43 |  | 400KV Akola - Aurangabad # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 241.23 | 2 | 0 | 0 | 720 | 482.46 | 347371.2 | 0 | 100%
44 | 711002 | 400KV Akola - Aurangabad # 2 | 2012-11-01 | 16:23 | 2012-11-01 | 16:35 | 0.0083333 | 0 | 12 | [9 empty] | OSPT | Line H/T to take out line reactor at Akola ( MSETCL) end. | 11/78 | 11/80
| 711057 | 400KV Akola - Aurangabad # 2 | 2012-11-16 | 21:25 | 2012-11-17 | 8:07 | [9 empty] | 0.44583 | 10 | 42 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1416 | --
| 711063 | 400KV Akola - Aurangabad # 2 | 2012-11-18 | 0:29 | 2012-11-18 | 6:15 | [9 empty] | 0.24028 | 5 | 46 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1522 | 11/1530
| 711067 | 400KV Akola - Aurangabad # 2 | 2012-11-18 | 23:42 | 2012-11-19 | 6:42 | [9 empty] | 0.29167 | 7 | 0 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1594 | --
|  | Sub-Total= | [5 empty] | 0 | 12 |  | 0 | 0 |  | 0 | 0 |  | 22 | 88
|  | Element Availability= | [6 empty] | 0.2 |  |  | 0 |  |  | 0 |  |  | 23.4667 |  |  |  |  | 241.23 | 2 | 0.2 | 96.492 | 720 | 482.46 | 347371.2 | 0.00027778 | 99.97%
45 | 711016 | 400KV Bhadrawati - Parli # 1 | 2012-11-05 | 11:40 | 2012-11-16 | 10:47 | [9 empty] | 1900-01-09 23:07 | 263 | 7 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/367 | 11/1359
| 711059 | 400KV Bhadrawati - Parli # 1 | 2012-11-16 | 23:53 | 2012-11-24 | 7:51 | [9 empty] | 1900-01-06 07:58 | 175 | 58 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1423 | 11/2037
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 438 | 65
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 439.0833 |  |  |  |  | 378.667 | 2 | 0 | 0 | 720 | 757.334 | 545280.48 | 0 | 100%
46 | 710073 | 400KV Bhadrawati - Parli # 2 | 2012-11-01 | 00:00 | 2012-11-05 | 14:18 | [9 empty] | 1900-01-03 14:18 | 110 | 18 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation. | 10/2225 | 11/379
| 711084 | 400KV Bhadrawati - Parli # 2 | 2012-11-26 | 21:16 | 2012-11-28 | 7:43 | [9 empty] | 1899-12-31 10:27 | 34 | 27 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/2338 | 11/2461
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 144 | 45
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 144.75 |  |  |  |  | 378.667 | 2 | 0 | 0 | 720 | 757.334 | 545280.48 | 0 | 100%
47 |  | 400KV Parli -Parli # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 4.958 | 2 | 0 | 0 | 720 | 9.916 | 7139.52 | 0 | 100%
48 |  | 400KV Parli- Parli # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 4.958 | 2 | 0 | 0 | 720 | 9.916 | 7139.52 | 0 | 100%
49 | 711022 | 400KV Korba- Raipur # 3 | 2012-11-08 | 9:42 | 2012-11-08 | 12:42 | 0.125 | 3 | 0 | [9 empty] | OSFT | Outage availed for attending line defect. | 11/659 | 11/717
| 711023 | 400KV Korba- Raipur # 3 | 2012-11-08 | 12:42 | 2012-11-08 | 15:18 |  |  |  | 0.10833 | 2 | 36 | [6 empty] | OMSU | Delay in restoration due to problem at NTPC end. | 11/659 | 11/717
|  | Sub-Total= | [5 empty] | 3 | 0 |  | 2 | 36 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 3 |  |  | 2.6 |  |  | 0 |  |  | 0 |  |  |  |  | 212.83 | 2 | 3 | 1276.98 | 717.4 | 425.66 | 305368.484 | 0.0041818 | 99.58%
50 |  | 400KV Korba-Raipur # 4
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.83 | 2 | 0 | 0 | 720 | 425.66 | 306475.2 | 0 | 100%
51 | 711049 | 400KV Wardha- Parli # 1 | 2012-11-14 | 22:18 | 2012-11-15 | 7:18 | [9 empty] | 0.375 | 9 | 0 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1249 | 11/1264
| 711051 | 400KV Wardha- Parli # 1 | 2012-11-15 | 20:53 | 2012-11-16 | 7:21 | [9 empty] | 0.43611 | 10 | 28 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1313 | 11/1337
| 711058 | 400KV Wardha- Parli # 1 | 2012-11-16 | 23:15 | 2012-11-17 | 9:58 | [9 empty] | 0.44653 | 10 | 43 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1422 | 11/1442
| 711073 | 400KV Wardha- Parli # 1 | 2012-11-19 | 23:18 | 2012-11-20 | 7:19 | [9 empty] | 0.33403 | 8 | 1 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1693 | --
| 711079 | 400KV Wardha- Parli # 1 | 2012-11-24 | 22:57 | 2012-11-25 | 11:24 | [9 empty] | 0.51875 | 12 | 27 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/2147 | 11/2171
| 711097 | 400KV Wardha- Parli # 1 | 2012-11-29 | 21:06 | 2012-11-29 | 21:11 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due on Over Voltage | ..
| 711098 | 400KV Wardha- Parli # 1 | 2012-11-29 | 21:11 | 2012-11-29 | 21:27 | [9 empty] | 0.011111 | 0 | 16 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | .. | 11/2633
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 49 | 115
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 50.9167 |  |  |  |  | 336.939 | 4 | 0 | 0 | 719.9167 | 1347.756 | 970272.007 | 0 | 100%
52 | 711041 | 400KV Wardha-Parli # 2 | 2012-11-13 | 22:21 | 2012-11-14 | 6:52 | [9 empty] | 0.35486 | 8 | 31 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1187 | 11/1206
| 711060 | 400KV Wardha-Parli # 2 | 2012-11-17 | 21:48 | 2012-11-19 | 16:11 | [9 empty] | 1899-12-31 18:23 | 42 | 23 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1511 | 11/1654
| 711081 | 400KV Wardha-Parli # 2 | 2012-11-25 | 22:30 | 2012-11-27 | 7:25 | [9 empty] | 1899-12-31 08:55 | 32 | 55 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/2221 | 11/2359
| 711090 | 400KV Wardha-Parli # 2 | 2012-11-28 | 22:13 | 2012-11-29 | 8:17 | [9 empty] | 0.41944 | 10 | 4 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/2524 | ..
| 711093 | 400KV Wardha-Parli # 2 | 2012-11-29 | 12:18 | 2012-11-30 | 20:00 | [9 empty] | 1899-12-31 07:42 | 31 | 42 | LCSD | For constrution works at Wardha SS. | 11/2573 | ..
| 711106 | 400KV Wardha-Parli # 2 | 2012-11-30 | 20:00 | 2012-11-30 | 24:00 | [9 empty] | 0.16667 | 4 | 0 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 127 | 155
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 129.5833 |  |  |  |  | 336.939 | 4 | 0 | 0 | 720 | 1347.756 | 970384.32 | 0 | 100%
53 |  | 400KV Korba - Balco
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 7.454 | 2 | 0 | 0 | 720 | 14.908 | 10733.76 | 0 | 100%
54 | 711027 | 400KV Balco- Birsinghpur | 2012-11-08 | 14:10 | 2012-11-08 | 21:38 |  |  |  | 0.31111 | 7 | 28 | [6 empty] | SBBU | Line tripped due to B/B protection operated at Birsinghpur end | -- | 11/758
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 7 | 28 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 7.4667 |  |  | 0 |  |  | 0 |  |  |  |  | 219.188 | 2 | 0 | 0 | 712.5333 | 438.376 | 312357.5125 | 0 | 100%
55 | 710071 | 400KV Vandana - Bhirsingpur | 2012-11-01 | 0:00 | 2012-11-11 | 9:25 | [9 empty] | 1900-01-09 09:25 | 249 | 25 | GOMD | Line unable to restore after line tripped on ovar-voltage due to Relay problem at M/s Vandana end. | -- | 11/996
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 249 | 25
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 249.4167 |  |  |  |  | 211.874 | 2 | 0 | 0 | 720 | 423.748 | 305098.56 | 0 | 100%
56 | 711005 | 765KV Seoni - Wardha # 2 | 2012-11-01 | 22:35 | 2012-11-02 | 11:29 | [9 empty] | 0.5375 | 12 | 54 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/117 | 11/150
| 711042 | 765KV Seoni - Wardha # 2 | 2012-11-13 | 23:29 | 2012-11-14 | 6:02 | [9 empty] | 0.27292 | 6 | 33 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1191 | 11/1201
| 711048 | 765KV Seoni - Wardha # 2 | 2012-11-14 | 21:12 | 2012-11-15 | 7:59 | [9 empty] | 0.44931 | 10 | 47 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1247 | 11/1265
| 711094 | 765KV Seoni - Wardha # 2 | 2012-11-29 | 21:05 | 2012-11-30 | 7:09 | [9 empty] | 0.41944 | 10 | 4 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/2628 | 11/2657
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 38 | 138
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 40.3 |  |  |  |  | 260.763 | 4 | 0 | 0 | 720 | 1043.052 | 750997.44 | 0 | 100%
57 | 711071 | 400KV Wardha - Mauda #1 | 2012-11-19 | 21:37 | 2012-11-19 | 21:47 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to overvoltage at Mauda end | -- | --
| 711072 | 400KV Wardha - Mauda #1 | 2012-11-19 | 21:47 | 2012-11-20 | 11:20 | [9 empty] | 0.56458 | 13 | 33 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
| 711101 | 400KV Wardha - Mauda #1 | 2012-11-29 | 21:06 | 2012-11-29 | 21:11 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due on Over Voltage | ..
| 711102 | 400KV Wardha - Mauda #1 | 2012-11-29 | 21:11 | 2012-11-29 | 22:17 | [9 empty] | 0.045833 | 1 | 6 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | .. | 11/2636
| 711105 | 400KV Wardha - Mauda #1 | 2012-11-30 | 22:45 | 2012-11-30 | 24:00 | [9 empty] | 0.052083 | 1 | 15 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/2735
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 15 |  | 15 | 54
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.25 |  |  | 15.9 |  |  |  |  | 123.45 | 4 | 0 | 0 | 719.75 | 493.8 | 355412.55 | 0 | 100%
58 | 711025 | 400KV Wardha-Mouda # 2 | 2012-11-08 | 10:36 | 2012-11-10 | 19:35 | [9 empty] | 1900-01-01 08:59 | 56 | 59 | OSPD | Outage availed by NTPC for maintenance activities | 11/673 | 11/952
| 711103 | 400KV Wardha-Mouda # 2 | 2012-11-29 | 21:06 | 2012-11-29 | 21:11 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due on Over Voltage | .. | ..
| 711104 | 400KV Wardha-Mouda # 2 | 2012-11-29 | 21:11 | 2012-11-30 | 14:30 | [9 empty] | 0.72153 | 17 | 19 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/2640 | 11/2690
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 73 | 78
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 74.3 |  |  |  |  | 123.45 | 4 | 0 | 0 | 719.9167 | 493.8 | 355494.85 | 0 | 100%
59 |  | 400KV Korba-Vandana
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 14.768 | 2 | 0 | 0 | 720 | 29.536 | 21265.92 | 0 | 100%
[8 empty] | 3 | 12 |  | 9 | 64 |  | 0 | 70 |  | 2123 | 1491 | [7 empty] | 1373.472 |  |  | 15880694.6472
[9 empty] | 3.2 |  |  | 10.0667 |  |  | 1.1667 |  |  | 2147.85 | [10 empty] | 8.6487e-05
99.99%
60 | 710053 | 400KV Raipur-Raigarh # 1 | 2012-11-01 | 0:00 | 2012-11-01 | 9:42 | [9 empty] | 0.40417 | 9 | 42 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1715 | 11/20
| 711028 | 400KV Raipur-Raigarh # 1 | 2012-11-09 | 23:25 | 2012-11-16 | 11:57 | [9 empty] | 1900-01-05 12:32 | 156 | 32 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/880 | 11/1367
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 165 | 74
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 166.2333 |  |  |  |  | 217.02 | 2 | 0 | 0 | 720 | 434.04 | 312508.8 | 0 | 100%
61 | 711001 | 400KV Raipur-Raigarh # 2 | 2012-11-01 | 10:50 | 2012-11-01 | 15:58 | [9 empty] | 0.21389 | 5 | 8 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/21 | 11/74
| 711030 | 400KV Raipur-Raigarh # 2 | 2012-11-11 | 2:30 | 2012-11-11 | 2:40 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on Overvoltage at Raigarh end | -- | --
| 711031 | 400KV Raipur-Raigarh # 2 | 2012-11-11 | 2:40 | 2012-11-11 | 3:30 | [9 empty] | 0.034722 | 0 | 50 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/983
| 711052 | 400KV Raipur-Raigarh # 2 | 2012-11-16 | 12:01 | 2012-11-30 | 24:00 | [9 empty] | 1900-01-13 11:59 | 347 | 59 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1368
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 10 |  | 352 | 117
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 353.95 |  |  |  |  | 217.02 | 2 | 0 | 0 | 719.8333 | 434.04 | 312436.46 | 0 | 100%
62 |  | 400KV Raigarh-Rourkela # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.46 | 2 | 0 | 0 | 720 | 424.92 | 305942.4 | 0 | 100%
63 | 711032 | 400KV Raigarh-SEL # 1 | 2012-11-11 | 2:28 | 2012-11-11 | 2:40 | [6 empty] | 0.0083333 | 0 | 12 |  |  |  | GOVC | Line tripped on Overvoltage at Raigarh end
| 711033 | 400KV Raigarh-SEL # 1 | 2012-11-11 | 2:40 | 2012-11-12 | 0:54 | [9 empty] | 0.92639 | 22 | 14 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-11/1064 NLDC-11/47 SRLDC -11/250
| 703063 | 400KV Raigarh-SEL # 1 | 2013-03-19 | 11:53 | 2013-03-19 | 13:33 |  |  |  | 0.069444 | 1 | 40 | [6 empty] | OMSU | Line tripped on Y- ph to earth fault ,FL= 9.8Km from SEL end ,comes in SEL's LILO Portion. | -- | 03/1593
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 1 | 40 |  | 0 | 12 |  | 22 | 14
|  | Element Availability= | [6 empty] | 0 |  |  | 1.6667 |  |  | 0.2 |  |  | 22.2333 |  |  |  |  | 99.46 | 2 | 0 | 0 | 718.1333 | 198.92 | 142851.0827 | 0 | 100%
64 |  | 400KV SEL -Rourkela #1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 113 | 2 | 0 | 0 | 720 | 226 | 162720 | 0 | 100%
65 | 710066 | 400KV Raipur-KSK | 2012-11-01 | 0:00 | 2012-11-05 | 15:05 | [9 empty] | 111:05 | 111 | 5 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | -- | 11/385
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 111 | 5
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 111.0833 |  |  |  |  | 134.74 | 2 | 0 | 0 | 720 | 269.48 | 194025.6 | 0 | 100%
66 | 711006 | 400KV Raigarh - KSK | 2012-11-01 | 22:22 | 2012-11-01 | 22:32 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to Over Voltage at KSK end & DT receive at Raipur end | -- | --
| 711007 | 400KV Raigarh - KSK | 2012-11-01 | 22:32 | 2012-11-02 | 7:41 | [9 empty] | 0.38125 | 9 | 9 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/126
| 711008 | 400KV Raigarh - KSK | 2012-11-02 | 21:14 | 2012-11-02 | 21:24 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to Over Voltage at KSK end & DT receive at Raipur end | … | ..
| 711009 | 400KV Raigarh - KSK | 2012-11-02 | 21:24 | 2012-11-03 | 8:51 | [9 empty] | 0.47708 | 11 | 27 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | … | 11/229
| 711029 | 400KV Raigarh - KSK | 2012-11-09 | 23:25 | 2012-11-16 | 11:15 | [9 empty] | 1900-01-05 11:50 | 155 | 50 | LVRD | Line Tripped on over voltage DT Received at KSK and line keep out as per WRLDC instruction | 11/883 | 11/1358
| 711043 | 400KV Raigarh - KSK | 2012-11-13 | 23:24 | 2012-11-13 | 23:29 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line Tripped only at ksk on over voltage (at KSK) DT Received at Raigarh. | -- | 11/1192
| 711044 | 400KV Raigarh - KSK | 2012-11-13 | 23:29 | 2012-11-14 | 5:51 | [9 empty] | 0.26528 | 6 | 22 | LVRD | Line H/T at raipur end and kept uncharged as per WRLDC instructions for Voltage regulation | 11/1192 | 11/1200
| 711053 | 400KV Raigarh - KSK | 2012-11-16 | 13:02 | 2012-11-16 | 13:07 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line Tripped on over voltage DT Received at KSK and line keep out as per WRLDC instruction | -- | 11/1378
| 711054 | 400KV Raigarh - KSK | 2012-11-16 | 13:07 | 2012-11-25 | 10:42 | [12 empty] | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/1378 | 11/2182
| 711065 | 400KV Raigarh - KSK | 2012-11-18 | 23:10 | 2012-11-18 | 23:18 | [6 empty] | 0.0055556 | 0 | 8 |  |  |  | GOVC | Line was tripped on overvoltage at KSK end. | -- | --
| 711066 | 400KV Raigarh - KSK | 2012-11-18 | 23:18 | 2012-11-19 | 8:15 | [9 empty] | 0.37292 | 8 | 57 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/1618
| 711091 | 400KV Raigarh - KSK | 2012-11-29 | 3:09 | 2012-11-29 | 3:14 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | tripped due to Overvoltage at Raigarh ,DT sent to KSK end | .. | ..
| 711092 | 400KV Raigarh - KSK | 2012-11-29 | 3:14 | 2012-11-30 | 24:00 | [9 empty] | 1899-12-31 20:46 | 44 | 46 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | .. | 11/2543
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 43 |  | 233 | 211
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.71667 |  |  | 236.5167 |  |  |  |  | 86.14 | 2 | 0 | 0 | 719.2833 | 172.28 | 123918.1327 | 0 | 100%
67 | 711015 | 400KV Raipur-Raigarh # 4 | 2012-11-04 | 22:13 | 2012-11-11 | 9:00 | [9 empty] | 1900-01-05 10:47 | 154 | 47 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 11/327 | 11/993
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 154 | 47
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 154.7833 |  |  |  |  | 220.884 | 2 | 0 | 0 | 720 | 441.768 | 318072.96 | 0 | 100%
68 | 711010 | 400KV Raigarh-Rourkela # 3 | 2012-11-03 | 1:36 | 2012-11-03 | 13:40 | [9 empty] | 0.50278 | 12 | 4 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | WRLDC: 11/212, ER:11/45, NLDC :11/09 | WR-11/242 NLDC-11/11 ER-11/51
| 711038 | 400KV Raigarh-Rourkela # 3 | 2012-11-13 | 11:49 | 2012-11-13 | 11:49 | 0 | 0 | 0 | [9 empty] | LART | Line autoreclosed successfully on B-E fault , fault location 68Km from Rourkela end. | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 12 | 4
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 12.0667 |  |  |  |  | 209.283 | 2 | 0 | 0 | 720 | 418.566 | 301367.52 | 0 | 100%
69 | 710074 | 400KV Raigarh - SEL # 2 | 2012-11-01 | 0:00 | 2012-11-02 | 20:06 | [6 empty] | 1899-12-31 20:06 | 44 | 6 |  |  |  | LNCC | Outage availed to restore line on new towers and remove ERS system (Which was put inplace of collapsed tower. | WR: 10/2244 ER:10/663 NLDC :10/195 | WRLDC: 11/187 ER:11/41 NLDC :11/08
| 711034 | 400KV Raigarh - SEL # 2 | 2012-11-11 | 2:30 | 2012-11-11 | 2:40 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on Overvoltage at Raigarh end | -- | --
| 711035 | 400KV Raigarh - SEL # 2 | 2012-11-11 | 2:40 | 2012-11-30 | 24:00 | [9 empty] | 1900-01-18 21:20 | 477 | 20 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 44 | 16 |  | 477 | 20
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 44.2667 |  |  | 477.3333 |  |  |  |  | 105 | 2 | 0 | 0 | 675.7333 | 210 | 141904 | 0 | 100%
70 |  | 400KV SEL -Rourkela #2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 104.28 | 2 | 0 | 0 | 720 | 208.56 | 150163.2 | 0 | 100%
71 | 710029 | 400KV Ranchi - Sipat # 1 | 2012-11-01 | 0:00 | 2012-11-16 | 11:45 | [9 empty] | 1900-01-14 11:45 | 371 | 45 | OSPD | Outage availed by NTPC Sipat for CB replacement at NTPC Sipat end. | WRLDC :10/743 ER: 10/229 NLDC : 10/63 | 11/1357 ER334, NLDC 66
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 371 | 45
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 371.75 |  |  |  |  | 405.772 | 2 | 0 | 0 | 720 | 811.544 | 584311.68 | 0 | 100%
72 | 711070 | 400KV Ranchi- Sipat # 2 | 2012-11-19 | 1:19 | 2012-11-21 | 12:46 | [9 empty] | 1900-01-01 11:27 | 59 | 27 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | WR- 11/ 1604 , NL - 11/ 74 , ER - 11/372 | WR- 11/ 1817 , NL - 11/ 80 , ER - 11/399
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 59 | 27
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 59.45 |  |  |  |  | 405.772 | 2 | 0 | 0 | 720 | 811.544 | 584311.68 | 0 | 100%
73 |  | 220KV Korba( e) -Budipadar # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 184 | 1 | 0 | 0 | 720 | 184 | 132480 | 0 | 100%
[8 empty] | 0 | 0 |  | 1 | 40 |  | 44 | 81 |  | 1956 | 564
[9 empty] | 0 |  |  | 1.6667 |  |  | 45.35 |  |  | 1965.4
1 |  | ICT # 1 400/220KV at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
2 |  | ICT # 2 400/220KV at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
3 |  | ICT # 1 400/220KV at Mapusa
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
4 |  | ICT # 2 400/220KV at Mapusa
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
5 | 711064 | ICT# 1 400/220KV at Boisar | 2012-11-18 | 7:15 | 2012-11-18 | 11:52 | 0.19236 | 4 | 37 | [9 empty] | OSPT | Outage avail for bushing Replacement of IV winding of B phase. | 11/1536 | 11/1556
|  | Sub-Total= | [5 empty] | 4 | 37 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 4.6167 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 4.6167 | 3635.625 | 720 | 787.5 | 567000 | 0.006412 | 99.36%
6 |  | ICT# 2 400/220KV at Boisar
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
7 |  | ICT # 1 400/220kV at Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
8 |  | ICT # 1 400/220kV at Raigarh
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
9 |  | ICT # 2 400/220kV at Raigarh
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
10 |  | AT-1 765/400KV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
11 |  | AT-2 765/400KV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
12 |  | AT-3 765/400KV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
13 |  | ICT # 1 400/220kV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
14 | 711021 | AT -I 765/400 KV at Wardha | 2012-11-08 | 7:56 | 2012-11-08 | 19:40 | [9 empty] | 0.48889 | 11 | 44 | SCSD | Outage availed for comissioning activity 400 KV spare Reactor at Wardha. | 11/655 | 11/751
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 11 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.7333 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
15 |  | AT - 2 765/400 KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
16 | 711078 | AT - 3 765/400 KV at Wardha | 2012-11-22 | 16:06 | 2012-11-24 | 15:18 | [9 empty] | 1899-12-31 23:12 | 47 | 12 | SCSD | Outage availed for jumpering works of spare reactor at wardha end . | 11/1908 | 11/2085
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 47 | 12
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 47.2 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
17 |  | AT-1 765/400KV at Bilaspur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
18 |  | AT-2 765/400KV at Bilaspur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
19 |  | ICT # 2 400/220kV at Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
20 |  | ICT # 2 400/220kV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
21 |  | ICT- 3 400/220KVat Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
22 |  | ICT-1 400/220KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
23 |  | ICT-2 400/220KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
24 |  | ICT-3 400/220KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 500 | 2.5 | 0 | 0 | 720 | 1250 | 900000 | 0 | 100%
25 |  | ICT-1 400/220KV at Solapur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
26 |  | ICT-2 400/220KV at Solapur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
27 |  | ICT-1 400/220KV at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
28 |  | ICT-2 400/220KV at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
29 |  | ICT-3 400/220KV at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
30 |  | AT-3 765/400KV at Bilaspur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
[9 empty] | 4.6167 |  |  | 0 |  |  | 0 |  |  | 58.9333 | [7 empty] | 3635.625 |  |  | 36540000
9.9497e-05
99.99%
1 |  | 400 KV Bus reactor at Bhadrawati
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
2 |  | 400 KV Bus reactor at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
3 | 711087 | Bus reactor at Mapusa | 2012-11-27 | 14:51 | 2012-11-27 | 20:38 | [9 empty] | 0.24097 | 5 | 47 | SVRD | handtripped as per WRLDC instructions for Voltage regulation | 11/2398 | 11/2441
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 5 | 47
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 5.7833 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
4 |  | Bus reactor at Kolhapur
|  | Sub-Total= | [8 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [5 empty] | 0 | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
5 |  | 400 KV Bus reactor at Raigarh
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
6 |  | 765 KV Bus reactor at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
7 |  | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
8 |  | 400 KV Bus reactor at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
[17 empty] | 0 | 0
9 | 711024 | Bus Reactor at Solapur | 2012-11-08 | 10:35 | 2012-11-08 | 18:11 | [9 empty] | 0.31667 | 7 | 36 | LVRD | B/R handtripped as per WRLDC instructions for Voltage regulation | 11/677 | 11/742
| 711083 | Bus Reactor at Solapur | 2012-11-26 | 7:37 | 2012-11-26 | 16:53 | [9 empty] | 0.38611 | 9 | 16 | SVRD | handtripped as per WRLDC instructions for Voltage regulation | 11/2238 | 11/2284
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 16 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 16.8667 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
10 |  | 400 KV Bus reactor at Parli
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
11 |  | 400 KV Bus reactor at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
12 |  | 765KV Bus reactor at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
13 |  | 765KV Bus reactor at Bilapsur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
14 | 711018 | 765KV Ranchi # 1 Switchable reactor at Bilaspur | 2012-11-06 | 16:25 | 2012-11-06 | 19:04 | [9 empty] | 0.11042 | 2 | 39 | SCSD | Hand tripped for Commissioning of control switching relay equipment. | 11/508 | 11/536
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 2 | 39
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 2.65 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
[8 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 23 | 138 | [7 empty] | 0 |  |  | 4489920
[9 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 25.3 | [10 empty] | 0
100%
[26 empty] | 5009.097 |  |  | 56910614.6472
8.8017e-05
99.99%
SN | EVENT No. | HVDC POLE | TRIPPING |  | RESTORATION |  | OUTAGE HOURS (HRS.MIN) | [11 empty] | CAT. CODE | DETAILED REASONS OF TRIPPING | WRLDC CODE FOR |  | TCR Pole Capacity ( 50:50%) WR & SR | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | =TCR X OH | THM | RC ( Rated Capacity) Pole Capacity ( 50:50%) WR & SR | =THM X RC | NAFM | TAFM (in Percentage)
|  |  | DATE | TIME | DATE | TIME | Attributed to PGCIL HRS:MIN | Attributed to PGCIL |  | Attributed to Other HRS:MIN | Attributed to Other |  | Attributed to sys conts. HRS:MIN | Attributed to sys conts. |  | Outage deemed available HRS:MIN | Outage deemed available |  |  |  | TRIPPING | CHARGING | A | B | C | D=A X C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 | 711013 | HVDC Pole-1 at Bhadrawati | 2012-11-03 | 8:51 | 2012-11-03 | 9:32 | 0.028472 | 0 | 41 | [9 empty] | OMST | Pole tripped due to problem in Valve Base Electronics Card | .. | WR-11/234 NLDC-11/10 SR-11/83
| 711014 | HVDC Pole-1 at Bhadrawati | 2012-11-04 | 8:53 | 2012-11-04 | 11:39 | 0.11528 | 2 | 46 | [9 empty] | OMST | Pole tripped due to problem in Valve Base Electronics Card | .. | WR-11/310 NLDC-11/15 SR-11/120
| 711036 | HVDC Pole-1 at Bhadrawati | 2012-11-11 | 5:10 | 2012-11-11 | 6:44 | 0.065278 | 1 | 34 | [9 empty] | OMST | Pole tripped due to VBE Card failure |  | WR-11/990 NLDC-11/43 SRLDC -11/290
| 711037 | HVDC Pole-1 at Bhadrawati | 2012-11-11 | 9:18 | 2012-11-11 | 10:23 | 0.045139 | 1 | 5 | [9 empty] | OMST | Pole tripped due to VBE Card failure |  | WR-11/1007 NLDC-11/44 SRLDC -11/296
| 711076 | HVDC Pole-1 at Bhadrawati | 2012-11-23 | 10:41 | 2012-11-23 | 10:54 |  |  |  | 0.0090278 | 0 | 13 | [6 empty] | OMSU | 400kV Ramagundam-Bhadrawati 1&2 tripped due to reciept of DT from ramagundam side. Pole 1 & 2 tripped without any outgoing feeder. | .. | wr-11/1955,sr-11/527,nr-11/91
|  | Sub-Total= | [5 empty] | 4 | 126 |  | 0 | 13 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 6.1 |  |  | 0.21667 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 6.1 | 1525 | 719.7833 | 250 | 179945.8333 | 0.0084748 | 99.15%
2 | 711077 | HVDC pole # 2 at Bhadrawati | 2012-11-23 | 10:41 | 2012-11-23 | 11:45 |  |  |  | 0.044444 | 1 | 4 | [6 empty] | OMSU | 400kV Ramagundam-Bhadrawati 1&2 tripped due to reciept of DT from ramagundam side. Pole 1 & 2 tripped without any outgoing feeder. | .. | wr-11/1959,sr-11/528,nr-11/92
| 711019 | HVDC pole # 2 at Bhadrawati | 2012-11-07 | 13:49 | 2012-11-07 | 14:05 |  |  |  | 0.011111 | 0 | 16 | [6 empty] | OMSU | Pole # 2 tripped due to dip in Auxilary power supply | -- | WRLDC : 11/610 SR: 11/215 NLDC : 11/36
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 1 | 20 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 1.3333 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 0 | 0 | 718.6667 | 250 | 179666.6667 | 0 | 100%
|  | HVDC SYSTEM TOTAL= | [5 empty] | 4 | 126 |  | 1 | 33 | 0 | 0 | 0 |  | 0 | 0 | [7 empty] | 1525 |  |  | 359612.5
[9 empty] | 6.1 |  |  | 1.55 |  |  | 0 |  |  | 0 | [10 empty] | 0.0042407
[27 empty] | HVDC SYSTEM AVAILABILITY= |  | 99.58%
Formulas:
Attributed to sys conts. HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Outage deemed available HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
OUTAGE HOURS (HRS.MIN) = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Attributed to Other HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]

## ANX-II
MONTH : NOV-2012
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : NOV-2012
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
NIL
Total=

## ANX-V
MONTH : NOV-2012
V. Data to be complied by the inter-State Transmission Licensees
Sl. No. | Type of failures | Restoration Time (Days) |  |  | Remarks
A | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 | Insualtor Failure | Terrain Type
|  | Plain | River bed | Hilly
i | Insualtor Failure in single phase
ii | Insualtor Failure in two phases
ii | Insualtor Failure in three phases
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 | Tower Damage ( not collapse)
i | One arm damage
ii | Two arm damage
5 | Snapping of phase conductor
i | Conductor snapping in single phase
ii | Conductor snapping in two phases
iii | Conductor snapping in three phases
6 | Failure of Earth wire
7 | Insulator failure with conductor snapping
8 | Any other combination of failures | 3 |  |  | Jumper rectification work carried out at Loc.No.147 (R-Ph) of Korba-Raipur # 3 with the help of PG Clamp and conductor piece on dtd. 08/11/12
B | Elements of sub-station for each KV class seperately
1 | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
| Other major failures in ICTs | Single phase Unit |  | Three phase Unit
| (i) Replacement of faulty bushings |  |  | 0.20833 | Bph bushing of IV winding ICT-1 at Boisar
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 | Failures of Reactors
Restoration of failed Reactors