## Index
WRTS-I SYSTEM AVAILABILITY DETAILS :
AVAILABILITY INDEX FOR OCT-2012
|  | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element | Target
SN | Element Name |  |  |  |  | attr. to | attr. to | Individual |  | NSC1 | OH1*NSC1*CktKm1 | Cktkm1 * NSC1 | THM X | NAFM | Availability | wise | Availability
[6 empty] | POWERGRID | OTHERS | THM | Ckrkm1 |  |  |  | Cktkm1 X |  | =100-100*O | Availability | as per
|  | Hrs | Mints | Hrs | Mints | OH1 | OH2 | =31*24-OH2 |  |  |  |  | NSC1 |  |  | Achieved | SOP
1 | 220kV Tarapur - Boisar |  |  |  |  | 0 | 0 | 744 | 20.56 | 1 | 0 | 20.56 | 15296.64 | 0 | 100 | 100% | 90%
2 | 400kV Korba-Korba (W) |  |  |  |  | 0 | 0 | 744 | 14 | 2 | 0 | 28 | 20832 | 0 | 100 | 100% | 90%
3 | 400kV Korba-Bhilai # 1 |  |  |  |  | 0 | 0 | 744 | 197 | 2 | 0 | 394 | 293136 | 0 | 100 | 100% | 90%
4 | 400kV Korba-Bhilai # 2 |  |  |  |  | 0 | 0 | 744 | 192 | 2 | 0 | 384 | 285696 | 0 | 100 | 100% | 90%
5 | 400kV Bhilai-Koradi |  |  |  |  | 0 | 0 | 744 | 272 | 2 | 0 | 544 | 404736 | 0 | 100 | 100% | 90%
6 | 400kV Koradi-Satpura |  |  | 0 | 24 | 0 | 0.4 | 743.6 | 149 | 2 | 0 | 298 | 221592.8 | 0 | 100 | 100% | 90%
7 | 400kV Bhilai - Raipur # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 0 | 100 | 100% | 90%
8 | 400 KV Bhilai - Bhadrawati |  |  | 0 | 49 | 0 | 0.81667 | 743.1833 | 322 | 2 | 0 | 644 | 478610.0667 | 0 | 100 | 100% | 90%
9 | 400 kV Raipur - Bhadrawati # 1 |  |  |  |  | 0 | 0 | 744 | 333 | 2 | 0 | 666 | 495504 | 0 | 100 | 100% | 90%
10 | 400kV Raipur - Bhadrawati # 2 |  |  |  |  | 0 | 0 | 744 | 345.55 | 2 | 0 | 691.1 | 514178.4 | 0 | 100 | 100% | 90%
11 | 400kV Raipur - Bhadrawati # 3 |  |  |  |  | 0 | 0 | 744 | 345.55 | 2 | 0 | 691.1 | 514178.4 | 0 | 100 | 100% | 90%
12 | 400kV B'vati-Chandrapur # 1 |  |  |  |  | 0 | 0 | 744 | 20 | 2 | 0 | 40 | 29760 | 0 | 100 | 100% | 90%
13 | 400kV B'vati-Chandrapur # 2 |  |  |  |  | 0 | 0 | 744 | 20 | 2 | 0 | 40 | 29760 | 0 | 100 | 100% | 90%
14 | 400kV B'vati-Chandrapur # 3 |  |  |  |  | 0 | 0 | 744 | 22.42 | 2 | 0 | 44.84 | 33360.96 | 0 | 100 | 100% | 90%
15 | 400kV B'vati-Chandrapur # 4 |  |  |  |  | 0 | 0 | 744 | 22.42 | 2 | 0 | 44.84 | 33360.96 | 0 | 100 | 100% | 90%
16 | 400kV Kolhapur - Mapusa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 150 | 2 | 0 | 300 | 223150 | 0 | 100 | 100% | 90%
17 | 400kV Kolhapur - Mapusa # 2 |  |  | 0 | 5 | 0 | 0.083333 | 743.9167 | 150 | 2 | 0 | 300 | 223175 | 0 | 100 | 100% | 90%
18 | 400kV Tarapur - Padghe # 1 | 0 | 36 |  |  | 0.6 | 0 | 744 | 91.119 | 2 | 109.3428 | 182.238 | 135585.072 | 0.00080645 | 99.9194 | 99.92% | 90%
19 | 400kV Tarapur - Padghe # 2 |  |  | 3 | 25 | 0 | 3.4167 | 740.5833 | 91.119 | 2 | 0 | 182.238 | 134962.4255 | 0 | 100 | 100% | 90%
20 | 400 KV BOISAR - Padge |  |  |  |  | 0 | 0 | 744 | 101 | 2 | 0 | 202 | 150288 | 0 | 100 | 100% | 90%
21 | 400kV Tarapur - Boisar #1 |  |  |  |  | 0 | 0 | 744 | 20.881 | 2 | 0 | 41.762 | 31070.928 | 0 | 100 | 100% | 90%
22 | 400kV Tarapur - Boisar #2 |  |  | 0 | 57 | 0 | 0.95 | 743.05 | 20.881 | 2 | 0 | 41.762 | 31031.2541 | 0 | 100 | 100% | 90%
23 | 400 KV Vapi - Boisar |  |  |  |  | 0 | 0 | 744 | 91 | 2 | 0 | 182 | 135408 | 0 | 100 | 100% | 90%
24 | 400kV Vindhyachal - Mahan ( Essar) |  |  |  |  | 0 | 0 | 744 | 19 | 2 | 0 | 38 | 28272 | 0 | 100 | 100% | 90%
25 | 400kV Mahan ( Essar) - Korba |  |  |  |  | 0 | 0 | 744 | 196 | 2 | 0 | 392 | 291648 |  |  | 100% | 90%
26 | 400 kV Vindyanchal-Korba #2 |  |  |  |  | 0 | 0 | 744 | 288.994 | 2 | 0 | 577.988 | 430023.072 | 0 | 100 | 100% | 90%
27 | 400 KV Satpura - Seoni (LILO portion) |  |  |  |  | 0 | 0 | 744 | 1.507 | 2 | 0 | 3.014 | 2242.416 | 0 | 100 | 100% | 90%
28 | 400 KV Seoni - Bhilai (LILO portion) |  |  | 3 | 45 | 0 | 3.75 | 740.25 | 1.498 | 2 | 0 | 2.996 | 2217.789 | 0 | 100 | 100% | 90%
29 | 400KV Korba - Bhatapara |  |  |  |  | 0 | 0 | 744 | 123.73 | 2 | 0 | 247.46 | 184110.24 | 0 | 100 | 100% | 90%
30 | 400KV Bhilai- Bhatapara |  |  |  |  | 0 | 0 | 744 | 90.453 | 2 | 0 | 180.906 | 134594.064 | 0 | 100 | 100% | 90%
31 | 400kV Korba - Pathadi |  |  |  |  | 0 | 0 | 744 | 39.536 | 2 | 0 | 79.072 | 58829.568 | 0 | 100 | 100% | 90%
32 | 400kV Pathadi - Sipat |  |  |  |  | 0 | 0 | 744 | 29.117 | 2 | 0 | 58.234 | 43326.096 | 0 | 100 | 100% | 90%
33 | 400 KV D/C Raipur-Sipat # 1 |  |  |  |  | 0 | 0 | 744 | 149.12 | 2 | 0 | 298.24 | 221890.56 | 0 | 100 | 100% | 90%
34 | 400 KV D/C Raipur-Sipat # 2 |  |  |  |  | 0 | 0 | 744 | 149.12 | 2 | 0 | 298.24 | 221890.56 | 0 | 100 | 100% | 90%
35 | 400 kV S/C Raipur-Sipat # 3 |  |  |  |  | 0 | 0 | 744 | 160 | 2 | 0 | 320 | 238080 | 0 | 100 | 100% | 90%
36 | 765 KV S/C Sipat - Bilaspur # 1 |  |  |  |  | 0 | 0 | 744 | 21.507 | 4 | 0 | 86.028 | 64004.832 | 0 | 100 | 100% | 90%
37 | 765 KV S/C Bilaspur - Seoni # 1 |  |  |  |  | 0 | 0 | 744 | 337.046 | 4 | 0 | 1348.184 | 1003048.896 | 0 | 100 | 100% | 90%
38 | 765 KV S/C Sipat - Bilaspur # 2 |  |  |  |  | 0 | 0 | 744 | 22.216 | 4 | 0 | 88.864 | 66114.816 | 0 | 100 | 100% | 90%
39 | 765 KV S/C Bilaspur - Seoni # 2 | 3 | 48 |  |  | 3.8 | 0 | 744 | 338.33 | 4 | 5142.616 | 1353.32 | 1006870.08 | 0.0051075 | 99.4892 | 99.49% | 90%
40 | 765 KV S/C Seoni-Wardha # 1 |  |  |  |  | 0 | 0 | 744 | 267.894 | 4 | 0 | 1071.576 | 797252.544 | 0 | 100 | 100% | 90%
41 | 400 KV D/C Wardha-Akola # 1 |  |  | 0 | 30 | 0 | 0.5 | 743.5 | 161.865 | 2 | 0 | 323.73 | 240693.255 | 0 | 100 | 100% | 90%
42 | 400 KV D/C Wardha-Akola # 2 |  |  |  |  | 0 | 0 | 744 | 161.865 | 2 | 0 | 323.73 | 240855.12 | 0 | 100 | 100% | 90%
43 | 400 KV D/C Akola-Aurangabad # 1 |  |  |  |  | 0 | 0 | 744 | 241.23 | 2 | 0 | 482.46 | 358950.24 | 0 | 100 | 100% | 90%
44 | 400 KV D/C Akola-Aurangabad # 2 |  |  |  |  | 0 | 0 | 744 | 241.23 | 2 | 0 | 482.46 | 358950.24 | 0 | 100 | 100% | 90%
45 | 400KV Bhadrawati-Parli # 1 |  |  |  |  | 0 | 0 | 744 | 378.667 | 2 | 0 | 757.334 | 563456.496 |  |  | 100% | 90%
46 | 400KV Bhadrawati-Parli # 2 |  |  |  |  | 0 | 0 | 744 | 378.667 | 2 | 0 | 757.334 | 563456.496 |  |  | 100% | 90%
47 | 400KV Parli-Parli # 1 |  |  |  |  | 0 | 0 | 744 | 4.958 | 2 | 0 | 9.916 | 7377.504 |  |  | 100% | 90%
48 | 400KV Parli-Parli # 2 |  |  |  |  | 0 | 0 | 744 | 4.958 | 2 | 0 | 9.916 | 7377.504 |  |  | 100% | 90%
49 | 400KV Korba-Raipur # 3 |  |  |  |  | 0 | 0 | 744 | 212.83 | 2 | 0 | 425.66 | 316691.04 |  |  | 100% | 90%
50 | 400KV Korba-Raipur # 4 |  |  |  |  | 0 | 0 | 744 | 212.83 | 2 | 0 | 425.66 | 316691.04 |  |  | 100% | 90%
51 | 400KV Wardha-Parli # 1 |  |  |  |  | 0 | 0 | 744 | 336.939 | 4 | 0 | 1347.756 | 1002730.464 |  |  | 100% | 90%
52 | 400KV Wardha-Parli # 2 |  |  |  |  | 0 | 0 | 744 | 336.939 | 4 | 0 | 1347.756 | 1002730.464 |  |  | 100% | 90%
53 | 400KV Korba-Balco ( Portion of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 744 | 7.454 | 2 | 0 | 14.908 | 11091.552 |  |  | 100% | 90%
54 | 400KV D/C Balco-Birsinghpur ( Portion of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 744 | 219.188 | 2 | 0 | 438.376 | 326151.744 |  |  | 100% | 90%
55 | 400KV D/C Vandana-Birsingpur (Portion of Korba-Birsingpur # 1) |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 211.874 | 2 | 0 | 423.748 | 315197.8873 |  |  | 100% | 90%
56 | 765 KV S/C Seoni-Wardha # 2 |  |  |  |  | 0 | 0 | 744 | 260.763 | 4 | 0 | 1043.052 | 776030.688 | 0 | 100 | 100% | 90%
57 | 400KV Mouda-Wardha # 1 |  |  | 0 | 5 | 0 | 0.083333 | 743.9167 | 123.45 | 4 | 0 | 493.8 | 367346.05 |  |  | 100% | 90%
58 | 400KV Mouda-Wardha # 2 |  |  |  |  | 0 | 0 | 744 | 123.45 | 4 | 0 | 493.8 | 367387.2 |  |  | 100% | 90%
59 | 400KV Korba-Vandana ( Portion of Korba-Birsingpur # 1) |  |  |  |  | 0 | 0 | 744 | 14.768 | 2 | 0 | 29.536 | 21974.784 |  |  | 100% | 90%
60 | 400KV Raipur - Raigarh # 1 |  |  |  |  | 0 | 0 | 744 | 217.02 | 2 | 0 | 434.04 | 322925.76 |  |  | 100% | 90%
61 | 400KV Raipur - Raigarh # 2 |  |  |  |  | 0 | 0 | 744 | 217.02 | 2 | 0 | 434.04 | 322925.76 |  |  | 100% | 90%
62 | 400kV Raigarh - Rourkela # 1 |  |  |  |  | 0 | 0 | 744 | 212.46 | 2 | 0 | 424.92 | 316140.48 |  |  | 100% | 90%
63 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 744 | 99.46 | 2 | 0 | 198.92 | 147996.48 |  |  | 100% | 90%
64 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 744 | 113 | 2 | 0 | 226 | 168144 |  |  | 100% | 90%
65 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] |  |  |  |  | 0 | 0 | 744 | 134.74 | 2 | 0 | 269.48 | 200493.12 |  |  | 100% | 90%
66 | 400KV KSK (Mahanadi) - Raigarh [lilo of Raipur - Raigarh # 3] |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 86.14 | 2 | 0 | 172.28 | 128147.6067 |  |  | 100% | 90%
67 | 400KV Raipur - Raigarh # 4 |  |  |  |  | 0 | 0 | 744 | 220.884 | 2 | 0 | 441.768 | 328675.392 |  |  | 100% | 90%
68 | 400KV Raigarh-Rourkela # 3 |  |  | 497 | 25 | 0 | 497.4167 | 246.5833 | 209.283 | 2 | 0 | 418.566 | 103211.3995 |  |  | 100% | 90%
69 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] |  |  | 61 | 28 | 0 | 61.4667 | 682.5333 | 105 | 2 | 0 | 210 | 143332 |  |  | 100% | 90%
70 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] |  |  |  |  | 0 | 0 | 744 | 104.28 | 2 | 0 | 208.56 | 155168.64 |  |  | 100% | 90%
71 | 400KV D/C Sipat-Ranchi # 1 |  |  |  |  | 0 | 0 | 744 | 405.772 | 2 | 0 | 811.544 | 603788.736 |  |  | 100% | 90%
72 | 400KV D/C Sipat-Ranchi # 2 |  |  |  |  | 0 | 0 | 744 | 405.772 | 2 | 0 | 811.544 | 603788.736 |  |  | 100% | 90%
73 | 220KV Korba-Bhudhipadar # 3 |  |  |  |  | 0 | 0 | 744 | 184 | 1 | 0 | 184 | 136896 |  |  | 100% | 90%
74 | [16 empty] | 90%
75 | [16 empty] | 90%
76 |  | 3 | 84 | 564 | 323 | 4.4 | 569.3833 |  | 11588.324 |  | 5251.9588 |  | 20095206.3178 | 0.005914 | 4299.4086 |  | 90%
77 | [6 empty] | 573.7833 | 25.8 | [8 empty] | 90%
78 | [16 empty] | 90%
79 | [6 empty] | NAFM = |  | 0.00026135 | [7 empty] | 90%
80 | Availability of transmission lines = | [5 empty] | TAFM= (100-100*NAFM) = |  | 99.9739 | [7 empty] | 90%
81 | [16 empty] | 90%
82 | [16 empty] | 90%
83 | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | [6 empty] | Element | 90%
84 | [5 empty] | attr. to | attr. to | Individual | Capacity |  |  |  |  | NAFM | Availability | wise | 90%
85 | [5 empty] | POWERGRID | OTHERS | THM | MVAt | =2.5 | = Oht * MVAt * 2.5 | =MVAt * 2.5 | =MVAt * 2.5 * THM | =O/(THM*P) | =100-100*Q | Availability | 90%
86 |  | Hrs | Mints |  |  | OHt1 | OHt2 | [9 empty] | 90%
87 | [5 empty] | Hours | Hours | [9 empty] | 90%
88 | [16 empty] | 90%
1 | 400/220kV ICT # 1 / Raipur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
2 | 400/220kV ICT # 2 / Raipur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
3 | 400/220kV ICT # 1 / Mapusa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
4 | 400/220kV ICT # 2 / Mapusa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
5 | 400/220kV ICT # 1 / Boisar |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
6 | 400/220kV ICT # 2 / Boisar |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
7 | 400/220kV ICT # 1 / Bhatapara |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
8 | 400/220kV ICT # 1 / Raigarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
9 | 400/220kV ICT # 2 / Raigarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
10 | 765/400kV AT # 1 / Seoni |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
11 | 765/400kV AT # 2 / Seoni |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
12 | 765/400kV AT # 3 / Seoni |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
13 | 400/220kV ICT # 1 / Seoni |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
14 | 765/220kV AT # 1 / Wardha |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 |  |  | 100% | 90%
15 | 765/220kV AT # 2 / Wardha |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 |  |  | 100% | 90%
16 | 765/220kV AT # 3 / Wardha |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 |  |  | 100% | 90%
17 | 765/220kV AT # 1 / Bilaspur |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 |  |  | 100% | 90%
18 | 765/220kV AT # 2 / Bilaspur |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 |  |  | 100% | 90%
19 | 400/220kV ICT # 2 / Bhatapara |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
20 | 400/220kV ICT # 2 / Seoni |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
21 | 400/220kV ICT # 3 / Raipur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
22 | 400/220kV ICT # 1 / Wardha |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
23 | 400/220kV ICT # 2 / Wardha |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
24 | 400/220kV ICT # 3 / Wardha |  |  |  |  | 0 | 0 | 744 | 500 | 2.5 | 0 | 1250 | 930000 |  |  | 100% | 90%
25 | 400/220kV ICT # 1 / Solapur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
26 | 400/220kV ICT # 2 / Solapur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
27 | 400/220kV ICT # 1 / Pune |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
28 | 400/220kV ICT # 2 / Pune |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
29 | 400/220kV ICT # 3 / Pune |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 |  |  | 100% | 90%
30 | 765/220kV AT # 3 / Bilaspur |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 |  |  | 100% | 90%
31 | [16 empty] | 90%
32 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 20300 |  | 0 |  | 37758000 |  |  |  | 90%
33 | [16 empty] | 90%
34 | [16 empty] | 90%
35 | [16 empty] | 90%
36 | [5 empty] | NAFM = |  |  | 0 | [7 empty] | 90%
37 | Availability of ICTs = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 100 | [7 empty] | 90%
38 | [16 empty] | 90%
39 | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | BR | [6 empty] | Element | 90%
40 | [5 empty] | attr. to | attr. to | Individual | Capacity |  |  |  |  | NAFM | Availability | wise | 90%
41 | [5 empty] | POWERGRID | OTHERS | THM | MVARr | =4 | = OHr*MVARr*4 | =MVARr * 4 | THM*MVARr * 4 | =O/(THM*P) | =100-100*Q | Availability | 90%
42 |  | Hrs | Mints | Hrs | Mints | OHr | OHr2 | [9 empty] | 90%
43 | [5 empty] | Hours | Hours | [9 empty] | 90%
44 | [16 empty] | 90%
1 | Bus reactor / B'vati |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
2 | Bus Reactor / Raipur |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 0 | 100 | 100% | 90%
3 | Bus Reactor / Mapusa |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
4 | Bus Reactor / Kolhapur |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 0 | 100 | 100% | 90%
5 | Bus Reactor / Raigarh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
6 | Bus Reactor / Seoni (3 x 80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
7 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 |  |  | 100% | 90%
8 | Bus Reactor / Wardha |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
9 | Bus Reactor / Solapur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 |  |  | 100% | 90%
10 | Bus Reactor / Parli |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 |  |  | 100% | 90%
11 | Bus Reactor / Pune |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 |  |  | 100% | 90%
12 | 765KV Bus Reactor / Wardha(3x80) | 0 | 44 |  |  | 0.73333 | 0 | 744 | 240 | 4 | 704 | 960 | 714240 |  |  | 99.9% | 90%
13 | 765KV Bus Reactor / Bilaspur(3x80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 |  |  | 100% | 90%
1 | 500 MW HVDC B'vati Pole # 1 | [14 empty] | 100% | 85%
2 | 500 MW HVDC B'vati Pole # 2 | [14 empty] | 100% | 85%
|  | 0 | 44 | 0 | 0 | 0.73333 | 0 |  | 1319 |  | 704 |  | 3925344
5.1333
5.1333
[6 empty] | NAFM = |  |  | 0.00017935
| Availability Bus Reactors = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.9821
| System Availability :- |  |  |  | System Availability :-
[11 empty] | 5955.9588 |  | 61778550.3178
[6 empty] | NAFM = |  |  | 9.6408e-05
[6 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9904
0.25
|  |  | 101 | 134
|  | DOCO |  | 2.2333
103.2333
`
163
173

## details calculation-Oct-12
ANNEXURE-I
OUTAGE DETAILS FOR THE MONTH OF : OCTOBER-2012
AC TRANSMISSION LINE
SN | EVENT No. | ELEMENTS NAME | TRIPPING |  | RESTORATION |  | OUTAGE HOURS (HRS.MIN) | [11 empty] | CAT. CODE | DETAILED REASONS OF TRIPPING | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | TAFM (in Percentage)
|  |  | DATE | TIME | DATE | TIME | Attributed to PGCIL HRS:MIN | Attributed to PGCIL |  | Attributed to Other HRS:MIN | Attributed to Other |  | Attributed to sys conts. HRS:MIN | Attributed to sys conts. |  | Outage deemed available HRS:MIN | Outage deemed available |  |  |  | TRIPPING | CHARGING | A | B | C | D=A*B*C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN | [8 empty] | 744
1 |  | 220kV Tarapur-Boisar
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20.56 | 1 | 0 | 0 | 744 | 20.56 | 15296.64 | 0 | 100%
2 |  | 400KV Korba-Korba(W)
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 14 | 2 | 0 | 0 | 744 | 28 | 20832 | 0 | 100%
3 |  | 400KV Korba-Bhilai # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 197 | 2 | 0 | 0 | 744 | 394 | 293136 | 0 | 100%
4 |  | 400KV Korba - Bhilai # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 192 | 2 | 0 | 0 | 744 | 384 | 285696 | 0 | 100%
5 |  | 400KV Bhilai- Koradi
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 272 | 2 | 0 | 0 | 744 | 544 | 404736 | 0 | 100%
6 | 710067 | 400KV Koradi - Satpura | 2012-10-26 | 13:54 | 2012-10-26 | 14:18 |  |  |  | 0.016667 | 0 | 24 | [6 empty] | OMSU | Line autoreclosed sucessfully from Koradi end Yph E fault . Fault location 95Km from Koradi. But tripped at Satpura end due to A/R problem. | -- | 10/2001
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 24 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.4 |  |  | 0 |  |  | 0 |  |  |  |  | 149 | 2 | 0 | 0 | 743.6 | 298 | 221592.8 | 0 | 100%
7 |  | 400KV Raipur-Bhilai#1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 2 | 0 | 0 | 744 | 26 | 19344 | 0 | 100%
8 | 710079 | 400KV Bhilai-Bhadrawati | 2012-10-30 | 12:22 | 2012-10-30 | 13:11 |  |  |  | 0.034028 | 0 | 49 | [6 empty] | SBBU | Line tripped only at Bhadrawati end on receipt of DT from bhilai due to bus fault at Bhilai end . | -- | 10/2343
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 49 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.81667 |  |  | 0 |  |  | 0 |  |  |  |  | 322 | 2 | 0 | 0 | 743.1833 | 644 | 478610.0667 | 0 | 100%
9 |  | 400KV Raipur - Bhadrawati # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 333 | 2 | 0 | 0 | 744 | 666 | 495504 | 0 | 100%
10 |  | 400KV Bhadrawati - Raipur # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 345.55 | 2 | 0 | 0 | 744 | 691.1 | 514178.4 | 0 | 100%
11 |  | 400KV Raipur-Bhadrawati # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 345.55 | 2 | 0 | 0 | 744 | 691.1 | 514178.4 | 0 | 100%
12 |  | 400KV Bhadrawati- Chandrapur # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20 | 2 | 0 | 0 | 744 | 40 | 29760 | 0 | 100%
13 | 702004 | 400KV Bhadrawati- Chandrapur # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20 | 2 | 0 | 0 | 744 | 40 | 29760 | 0 | 100%
14 | 710033 | 400KV Bhadrawati-Chandrapur # 3 | 2012-10-13 | 10:48 | 2012-10-14 | 16:24 | [9 empty] | 1899-12-31 05:36 | 29 | 36 | OSPD | Outage availed by M/S GMR ltd for construction activity of upcoming EMCO-Bhadrwati D/C line | 10/993 | 10/1064
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 29 | 36
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 29.6 |  |  |  |  | 22.42 | 2 | 0 | 0 | 744 | 44.84 | 33360.96 | 0 | 100%
15 | 710034 | 400KV Bhadrawati-Chandrapur # 4 | 2012-10-13 | 10:48 | 2012-10-14 | 17:23 | [9 empty] | 1899-12-31 06:35 | 30 | 35 | OSPD | Outage availed by M/S GMR ltd for construction activity of upcoming EMCO-Bhadrwati D/C line | 10/994 | 10/1068
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 30 | 35
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 30.5833 |  |  |  |  | 22.42 | 2 | 0 | 0 | 744 | 44.84 | 33360.96 | 0 | 100%
16 | 710018 | 400KV Kolhapur-Mapusa # 1 | 2012-10-08 | 4:05 | 2012-10-08 | 4:15 | [6 empty] | 0.0069444 | 0 | 10 |  | 0 | 0 | GOVC | Line tripped due to overvoltage at Kolhapur end.DT received at Mapusa. | -- | --
| 710019 | 400KV Kolhapur-Mapusa # 1 | 2012-10-08 | 4:15 | 2012-10-08 | 6:36 | [9 empty] | 0.097917 | 2 | 21 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 10/521
| 710045 | 400KV Kolhapur-Mapusa # 1 | 2012-10-16 | 16:42 | 2012-10-20 | 9:38 | [9 empty] | 1900-01-02 16:56 | 88 | 56 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1220 | 10/1517
| 710052 | 400KV Kolhapur-Mapusa # 1 | 2012-10-20 | 16:16 | 2012-10-25 | 9:30 | [9 empty] | 1900-01-03 17:14 | 113 | 14 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1551 | 10/1882
| 710063 | 400KV Kolhapur-Mapusa # 1 | 2012-10-26 | 16:36 | 2012-10-29 | 10:05 | [10 empty] | 0 | 0 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/2019 | 10/2242
| 710076 | 400KV Kolhapur-Mapusa # 1 | 2012-10-30 | 16:36 | 2012-10-31 | 24:00 | [9 empty] | 11:32 | 11 | 32 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/2363 | 11/50
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 10 |  | 214 | 123
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 216.05 |  |  |  |  | 150 | 2 | 0 | 0 | 743.8333 | 300 | 223150 | 0 | 100%
17 | 709119 | 400KV Kolhapur - Mapusa # 2 | 2012-10-01 | 0:00 | 2012-10-15 | 9:23 | [9 empty] | 1900-01-13 09:23 | 345 | 23 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 09/2109 | 10/1098
| 710042 | 400KV Kolhapur - Mapusa # 2 | 2012-10-15 | 13:55 | 2012-10-16 | 11:00 | [9 empty] | 0.87847 | 21 | 5 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1129 | 10/1191
| 710055 | 400KV Kolhapur - Mapusa # 2 | 2012-10-24 | 17:05 | 2012-10-24 | 17:10 | [6 empty] | 0.0034722 | 0 | 5 |  | 0 | 0 | GOVC | Line tripped due to overvoltage at Kolhapur end . | -- | 10/1844
| 710056 | 400KV Kolhapur - Mapusa # 2 | 2012-10-24 | 17:10 | 2012-10-24 | 17:56 | [9 empty] | 0.031944 | 0 | 46 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | -- | 10/1844
| 710058 | 400KV Kolhapur - Mapusa # 2 | 2012-10-25 | 16:34 | 2012-10-26 | 10:44 | [9 empty] | 0.75694 | 18 | 10 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1921 | 10/1980
| 710076 | 400KV Kolhapur - Mapusa # 2 | 2012-10-29 | 16:29 | 2012-10-30 | 9:35 | [9 empty] | 0.7125 | 17 | 6 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/2273 | 10/2319
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 401 | 90
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 402.5 |  |  |  |  | 150 | 2 | 0 | 0 | 743.9167 | 300 | 223175 | 0 | 100%
18 | 710015 | 400KV Tarapur - Padghe # 1 | 2012-10-07 | 16:26 | 2012-10-07 | 17:02 | 0.025 | 0 | 36 | [9 empty] | LEFT | Line tripped only at Tarapur end due to A/R kept off at tarapur generating station end , A/R successful at padghe end on Bph-E fault (F.L. 14 KM from Padge and 72 KM from Tarapur ) | -- | 10/491
|  | Sub-Total= | [5 empty] | 0 | 36 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0.6 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 91.119 | 2 | 0.6 | 109.3428 | 744 | 182.238 | 135585.072 | 0.00080645 | 99.92%
19 | 710004 | 400KV Tarapur - Padghe # 2 | 2012-10-02 | 14:19 | 2012-10-02 | 17:44 |  |  |  | 0.14236 | 3 | 25 | [6 empty] | OMSU | Line tripped on Bph-Earth fault, at Tarapur end due to A/R in non-auto-mode. Line charging delayed by Tarapur due to CB problem . | -- | 10/117
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 3 | 25 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 3.4167 |  |  | 0 |  |  | 0 |  |  |  |  | 91.119 | 2 | 0 | 0 | 740.5833 | 182.238 | 134962.4255 | 0 | 100%
20 | 710038 | 400KV Boisar - Padghe | 2012-10-14 | 13:58 | 2012-10-14 | 13:58 | 0 | 0 | 0 | [9 empty] | LART | Line was Auto Reclosure successful on Rph-E fault . F.L: 28.2 KM from Boisar end . | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 101 | 2 | 0 | 0 | 744 | 202 | 150288 | 0 | 100%
21 |  | 400kV Tarapur-Boisar # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20.881 | 2 | 0 | 0 | 744 | 41.762 | 31070.928 | 0 | 100%
22 | 710014 | 400kV Tarapur-Boisar # 2 | 2012-10-06 | 18:24 | 2012-10-06 | 19:21 |  |  |  | 0.039583 | 0 | 57 | [6 empty] | OMSU | Line tripped on fault only at Tarapur end .A/R successful at Boisar end. | -- | 10/437
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 57 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.95 |  |  | 0 |  |  | 0 |  |  |  |  | 20.881 | 2 | 0 | 0 | 743.05 | 41.762 | 31031.2541 | 0 | 100%
23 | 710061 | 400KV Boisar - Vapi | 2012-10-26 | 9:03 | 2012-10-26 | 20:04 | [9 empty] | 0.45903 | 11 | 1 | LCSD | Outage availed to faciliate stringing work of up-coming 400KV Vapi- Navi-mumbai line. | 10/1970 | 10/2038
| 710069 | 400KV Boisar - Vapi | 2012-10-27 | 7:32 | 2012-10-27 | 17:30 | [9 empty] | 0.41528 | 9 | 58 | LCSD | Outage availed to faciliate stringing work of upcoming 400KV Vapi- Navi-mumbai line | 10/2073 | 10/2113
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 20 | 59
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 20.9833 |  |  |  |  | 91 | 2 | 0 | 0 | 744 | 182 | 135408 | 0 | 100%
24 |  | 400KV Vindhyachal - Mahan
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 19 | 2 | 0 | 0 | 744 | 38 | 28272 | 0 | 100%
25 | 710024 | 400KV Korba - Mahan | 2012-10-08 | 11:02 | 2012-10-10 | 16:11 | [9 empty] | 1900-01-01 05:09 | 53 | 9 | OSPD | OCC approved outage availed by NTPC for relay retrofitting works. | 10/555 | 10/750
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 53 | 9
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 53.15 |  |  |  |  | 196 | 2 | 0 | 0 | 744 | 392 | 291648 | 0 | 100%
26 |  | 400KV Korba - Vindhyachal # 2 | [11 empty] | 0 | 0 | [5 empty] | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 288.99 | 2 | 0 | 0 | 744 | 577.98 | 430017.12 | 0 | 100%
27 | 710068 | 400KV Seoni-Satpura | 2012-10-26 | 13:55 | 2012-10-26 | 13:55 |  |  |  | 0 | 0 | 0 | [6 empty] | OMSU | Autoreclosed sucessfully from both ends at 13:55hrs. Yph E fault . Fault location from seoni 33.6Km. Fault section belongs to MPPTCL. | -- | --
| 710075 | 400KV Seoni-Satpura | 2012-10-29 | 11:01 | 2012-10-29 | 18:29 | [9 empty] | 0.31111 | 7 | 28 | OSPD | Outage availed by MPPTCL for line maintenance works | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 7 | 28
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.4667 |  |  |  |  | 1.507 | 2 | 0 | 0 | 744 | 3.014 | 2242.416 | 0 | 100%
28 | 710028 | 400KV Seoni-Bhilai | 2012-10-10 | 10:20 | 2012-10-10 | 18:04 | [9 empty] | 0.32222 | 7 | 44 | OSPD | Line outage availed by MPEB for Maintenance works. | 10/719 | 10/761
| 710078 | 400KV Seoni-Bhilai | 2012-10-30 | 12:22 | 2012-10-30 | 16:07 |  |  |  | 0.15625 | 3 | 45 | [6 empty] | SBBU | Line tripped on receipt of DT at seoni end from bhilai due to bus fault at Bhilai end . | -- | 10/2357
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 3 | 45 |  | 0 | 0 |  | 7 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 3.75 |  |  | 0 |  |  | 7.7333 |  |  |  |  | 1.498 | 2 | 0 | 0 | 740.25 | 2.996 | 2217.789 | 0 | 100%
29 |  | 400KV Korba-Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 123.73 | 2 | 0 | 0 | 744 | 247.46 | 184110.24 | 0 | 100%
30 |  | 400KV Bhilai -Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 90.453 | 2 | 0 | 0 | 744 | 180.906 | 134594.064 | 0 | 100%
31 | 710009 | 400kv Korba- Pathadi | 2012-10-04 | 11:48 | 2012-10-16 | 19:50 | [9 empty] | 1900-01-11 08:02 | 296 | 2 | OSPD | Outage availed by NTPC for maintenance activities & relay repalcement at NTPC end. | 10/269 | 10/1237
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 296 | 2
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 296.0333 |  |  |  |  | 39.536 | 2 | 0 | 0 | 744 | 79.072 | 58829.568 | 0 | 100%
[17 empty] | 0 | 0
32 |  | 400KV Sipat-Pathadi
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.117 | 2 | 0 | 0 | 744 | 58.234 | 43326.096 | 0 | 100%
33 |  | 400KV Raipur-Sipat # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 149.12 | 2 | 0 | 0 | 744 | 298.24 | 221890.56 | 0 | 100%
34 | 710035 | 400KV Raipur-Sipat # 2 | 2012-10-13 | 11:28 | 2012-10-13 | 12:16 | [9 empty] | 0.033333 | 0 | 48 | OSPD | Outage availed by M/S NTPC for attending CB problems | 10/998 | 10/1001
| 710062 | 400KV Raipur-Sipat # 2 | 2012-10-26 | 9:42 | 2012-10-26 | 19:48 | [9 empty] | 0.42083 | 10 | 6 | OSPD | Outage availed by NTPC for line CT replacement at Sipat . | 10/1972 | 10/2024
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 10 | 54
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.9 |  |  |  |  | 149.12 | 2 | 0 | 0 | 744 | 298.24 | 221890.56 | 0 | 100%
35 |  | 400KV Raipur - Sipat # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 160 | 2 | 0 | 0 | 744 | 320 | 238080 | 0 | 100%
[17 empty] | 0 | 0
36 | 710026 | 765KV Sipat- Bilaspur# 1 | 2012-10-08 | 12:28 | 2012-10-08 | 15:34 | [9 empty] | 0.12917 | 3 | 6 | LPRD | Line H/T as per WRLDC instruction for power regulation | 10/560 | 10/569
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 3 | 6
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 3.1 |  |  |  |  | 21.507 | 4 | 0 | 0 | 744 | 86.028 | 64004.832 | 0 | 100%
37 |  | 765KV Seoni-Bilaspur # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337.046 | 4 | 0 | 0 | 744 | 1348.184 | 1003048.896 | 0 | 100%
38 |  | 765KV Sipat- Bilaspur# 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 22.216 | 4 | 0 | 0 | 744 | 88.864 | 66114.816 | 0 | 100%
39 | 710025 | 765KV Seoni - Bilaspur# 2 | 2012-10-08 | 12:06 | 2012-10-08 | 15:54 | 0.15833 | 3 | 48 | [9 empty] | OSPT | Outage availed for maintenance of line isolator at Bilaspur end. | 10/557 | 10/569
|  | Sub-Total= | [5 empty] | 3 | 48 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 3.8 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 338.33 | 4 | 3.8 | 5142.616 | 744 | 1353.32 | 1006870.08 | 0.0051075 | 99.49%
40 | 710010 | 765KV Seoni - Wardha # 1 | 2012-10-04 | 22:03 | 2012-10-10 | 15:24 | [9 empty] | 1900-01-04 17:21 | 137 | 21 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 01/34 | 01/82
| 710031 | 765KV Seoni - Wardha # 1 | 2012-10-10 | 16:16 | 2012-10-12 | 16:53 | [9 empty] | 1900-01-01 00:37 | 48 | 37 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 01/127 | 01/179
| 710037 | 765KV Seoni - Wardha # 1 | 2012-10-13 | 17:45 | 2012-10-16 | 6:37 | [9 empty] | 1900-01-01 12:52 | 60 | 52 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | WR- 01/754 ,NLDC-01/56 | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 245 | 110
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 246.8333 |  |  |  |  | 267.894 | 4 | 0 | 0 | 744 | 1071.576 | 797252.544 | 0 | 100%
41 | 710003 | 400KV Wardha-Akola # 1 | 2012-10-02 | 6:14 | 2012-10-02 | 6:39 | [6 empty] | 0.017361 | 0 | 25 |  |  |  | GOVC | Line tripped on Overvoltage at Akola end. DT received at Wardha. | -- | 10/92
| 710020 | 400KV Wardha-Akola # 1 | 2012-10-08 | 9:54 | 2012-10-08 | 9:59 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to o/v at wardha end.while charging 765 kv seoni wardha#1 voltage rised at wardha and line tripped on o/v. | -- | --
| 710021 | 400KV Wardha-Akola # 1 | 2012-10-08 | 9:59 | 2012-10-08 | 10:20 | [9 empty] | 0.014583 | 0 | 21 | LVRD | Line kept out of service as per WRLDC instructions for Voltage regulation | -- | 10/545
| 710040 | 400KV Wardha-Akola # 1 | 2012-10-14 | 21:48 | 2012-10-15 | 12:56 | [9 empty] | 0.63056 | 15 | 8 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1081 | 10/1125
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 30 |  | 15 | 29
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.5 |  |  | 15.4833 |  |  |  |  | 161.865 | 2 | 0 | 0 | 743.5 | 323.73 | 240693.255 | 0 | 100%
42 |  | 400kv Wardha-Akola # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 161.865 | 2 | 0 | 0 | 744 | 323.73 | 240855.12 | 0 | 100%
43 | 710051 | 400KV Akola - Aurangabad # 1 | 2012-10-19 | 12:24 | 2012-10-19 | 15:14 | [9 empty] | 0.11806 | 2 | 50 | OSPD | Outage availed by MSETCL to attend hot spots in Line isolator at Aurangabad end and taking out Line reactor at Akola end for Reactor Header pipe modification and works | 10/1447 | 10/1456
| 710077 | 400KV Akola - Aurangabad # 1 | 2012-10-30 | 12:20 | 2012-10-30 | 17:03 | [9 empty] | 0.19653 | 4 | 43 | OSPD | Outage availed by MSETCL for attending hotspot at akola end. | 10/2332 | 10/2358
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 6 | 93
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.55 |  |  |  |  | 241.23 | 2 | 0 | 0 | 744 | 482.46 | 358950.24 | 0 | 100%
44 |  | 400KV Akola - Aurangabad # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 241.23 | 2 | 0 | 0 | 744 | 482.46 | 358950.24 | 0 | 100%
45 | 709116 | 400KV Bhadrawati - Parli # 1 | 2012-10-01 | 0:00 | 2012-10-15 | 11:42 | [9 empty] | 1900-01-13 11:42 | 347 | 42 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 09/1932 | 10/1110
| 710047 | 400KV Bhadrawati - Parli # 1 | 2012-10-17 | 16:04 | 2012-10-29 | 7:26 | [9 empty] | 1900-01-10 15:22 | 279 | 22 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1291 | 10/2224
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 626 | 64
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 627.0667 |  |  |  |  | 378.667 | 2 | 0 | 0 | 744 | 757.334 | 563456.496 | 0 | 100%
46 | 710041 | 400KV Bhadrawati - Parli # 2 | 2012-10-15 | 11:53 | 2012-10-17 | 16:02 | [9 empty] | 1900-01-01 04:09 | 52 | 9 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1122 | 10/1290
| 710073 | 400KV Bhadrawati - Parli # 2 | 2012-10-29 | 7:33 | 2012-10-31 | 24:00 | [9 empty] | 1900-01-01 16:27 | 64 | 27 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation. | 10/2225 | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 116 | 36
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 116.6 |  |  |  |  | 378.667 | 2 | 0 | 0 | 744 | 757.334 | 563456.496 | 0 | 100%
47 | 710008 | 400KV Parli -Parli # 1 | 2012-10-03 | 13:51 | 2012-10-04 | 9:56 | [9 empty] | 0.83681 | 20 | 5 | LPRD | Line hand tripped as per wrldc instructions for power regulation to control line loading problem in lonikhand-Parli line of MSETCL. | 10/206 | 10/249
| 710017 | 400KV Parli -Parli # 1 | 2012-10-08 | 0:40 | 2012-10-15 | 12:32 | [9 empty] | 1900-01-06 11:52 | 179 | 52 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/518 | 10/1111
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 199 | 57
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 199.95 |  |  |  |  | 4.958 | 2 | 0 | 0 | 744 | 9.916 | 7377.504 | 0 | 100%
48 |  | 400KV Parli- Parli # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 4.958 | 2 | 0 | 0 | 744 | 9.916 | 7377.504 | 0 | 100%
49 |  | 400KV Korba- Raipur # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.83 | 2 | 0 | 0 | 744 | 425.66 | 316691.04 | 0 | 100%
50 |  | 400KV Korba-Raipur # 4
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.83 | 2 | 0 | 0 | 744 | 425.66 | 316691.04 | 0 | 100%
51 | 709126 | 400KV Wardha- Parli # 1 | 2012-10-01 | 0:00 | 2012-10-01 | 12:22 | [9 empty] | 0.51528 | 12 | 22 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 9/2283 | 10/26
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 12 | 22
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 12.3667 |  |  |  |  | 336.939 | 4 | 0 | 0 | 744 | 1347.756 | 1002730.464 | 0 | 100%
52 | 710011 | 400KV Wardha-Parli # 2 | 2012-10-05 | 0:56 | 2012-10-05 | 9:14 | [9 empty] | 0.34583 | 8 | 18 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/313 | 10/322
| 710016 | 400KV Wardha-Parli # 2 | 2012-10-07 | 23:58 | 2012-10-13 | 12:49 | [9 empty] | 1900-01-04 12:51 | 132 | 51 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/514 | 10/1003
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 140 | 69
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 141.15 |  |  |  |  | 336.939 | 4 | 0 | 0 | 744 | 1347.756 | 1002730.464 | 0 | 100%
53 | 710060 | 400KV Korba - Balco | 2012-10-26 | 7:25 | 2012-10-26 | 18:40 | [9 empty] | 0.46875 | 11 | 15 | OSPD | Outage availed for LBB modification & testing by NTPC. | 10/1965 | 10/2027
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 11 | 15
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.25 |  |  |  |  | 7.454 | 2 | 0 | 0 | 744 | 14.908 | 11091.552 | 0 | 100%
54 | 709103 | 400KV Balco- Birsinghpur | 2012-10-01 | 0:00 | 2012-10-08 | 17:57 | [9 empty] | 1900-01-06 17:57 | 185 | 57 | OSPD | Line outage availed for attending PLCC problem at both ends. PLCC system of both ends belongs to M/s Balco. | -- | 10/582
| 710039 | 400KV Balco- Birsinghpur | 2012-10-14 | 14:26 | 2012-10-19 | 17:30 | [9 empty] | 1900-01-04 03:04 | 123 | 4 | OSPD | Outage availed by BALCO for Line rectification works | 10/1070 | 10/1466
| 710057 | 400KV Balco- Birsinghpur | 2012-10-25 | 13:15 | 2012-10-26 | 21:02 | [9 empty] | 1899-12-31 07:47 | 31 | 47 | OSPD | Outage availed By BALCO for maintenance works | 10/1905 | 10/2044
| 710064 | 400KV Balco- Birsinghpur | 2012-10-26 | 21:02 | 2012-10-29 | 14:00 | [12 empty] | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/2044 | 10/2259
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 339 | 108
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 340.8 |  |  |  |  | 219.188 | 2 | 0 | 0 | 744 | 438.376 | 326151.744 | 0 | 100%
55 | 710048 | 400KV Vandana - Bhirsingpur | 2012-10-01 | 0:00 | 2012-10-25 | 13:00 | [9 empty] | 1900-01-23 13:00 | 589 | 0 | GOMD | Line unable to restore due to over-voltage. Lilo of Korba- Bhirshingpur # 1 carried out on 29/09/12 - 16:31 hrs at M/s Vandana. | 08/813 | 10/1897
| 710070 | 400KV Vandana - Bhirsingpur | 2012-10-27 | 10:31 | 2012-10-27 | 10:41 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on over voltage at Birsingpur end | -- | --
| 710071 | 400KV Vandana - Bhirsingpur | 2012-10-27 | 10:41 | 2012-10-31 | 24:00 | [9 empty] | 1900-01-03 13:19 | 109 | 19 | GOMD | Line unable to restore after line tripped on ovar-voltage due to Relay problem at M/s Vandana end. | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 10 |  | 698 | 19
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 698.3167 |  |  |  |  | 211.874 | 2 | 0 | 0 | 743.8333 | 423.748 | 315197.8873 | 0 | 100%
56 | 710002 | 765KV Seoni - Wardha # 2 | 2012-10-01 | 13:34 | 2012-10-04 | 11:10 | [9 empty] | 1900-01-01 21:36 | 69 | 36 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 10/36 | 10/261
| 710032 | 765KV Seoni - Wardha # 2 | 2012-10-12 | 17:12 | 2012-10-13 | 15:46 | [9 empty] | 0.94028 | 22 | 34 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/944 | 10/1012
| 710046 | 765KV Seoni - Wardha # 2 | 2012-10-17 | 0:07 | 2012-10-17 | 18:59 | [9 empty] | 0.78611 | 18 | 52 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1250 | 10/1311
| 710049 | 765KV Seoni - Wardha # 2 | 2012-10-18 | 0:37 | 2012-10-18 | 11:58 | [9 empty] | 0.47292 | 11 | 21 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1347 | 10/1376
| 710054 | 765KV Seoni - Wardha # 2 | 2012-10-23 | 3:16 | 2012-10-25 | 7:58 | [9 empty] | 1900-01-01 04:42 | 52 | 42 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1790 | 10/1875
| 710059 | 765KV Seoni - Wardha # 2 | 2012-10-25 | 22:05 | 2012-10-26 | 7:25 | [9 empty] | 0.38889 | 9 | 20 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1945 | 10/1964
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 181 | 205
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 184.4167 |  |  |  |  | 260.763 | 4 | 0 | 0 | 744 | 1043.052 | 776030.688 | 0 | 100%
57 | 710012 | 400KV Wardha - Mauda #1 | 2012-10-05 | 1:04 | 2012-10-05 | 17:24 | [9 empty] | 0.68056 | 16 | 20 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/314 | 10/366
| 710022 | 400KV Wardha - Mauda #1 | 2012-10-08 | 9:54 | 2012-10-08 | 9:59 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to o/v at wardha end.while charging 765 kv seoni wardha#1 voltage rised at wardha and line tripped on o/v. | -- | --
| 710023 | 400KV Wardha - Mauda #1 | 2012-10-08 | 9:59 | 2012-10-08 | 12:00 | [9 empty] | 0.084028 | 2 | 1 | LVRD | Line kept out of service as per WRLDC instructions for Voltage regulation | -- | 10/546
| 710050 | 400KV Wardha - Mauda #1 | 2012-10-18 | 10:53 | 2012-10-25 | 15:13 | [9 empty] | 1900-01-06 04:20 | 172 | 20 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1374 | 10/1910
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 190 | 41
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 190.6833 |  |  |  |  | 123.45 | 4 | 0 | 0 | 743.9167 | 493.8 | 367346.05 | 0 | 100%
58 | 710030 | 400KV Wardha-Mouda # 2 | 2012-10-10 | 15:20 | 2012-10-17 | 11:25 | [9 empty] | 1900-01-05 20:05 | 164 | 5 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/743 | 10/1278
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 164 | 5
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 164.0833 |  |  |  |  | 123.45 | 4 | 0 | 0 | 744 | 493.8 | 367387.2 | 0 | 100%
59 |  | 400KV Korba-Vandana
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 14.768 | 2 | 0 | 0 | 744 | 29.536 | 21974.784 | 0 | 100%
[9 empty] | 4.4 |  |  | 9.3333 |  |  | 1 |  |  | 3850.2333 | [7 empty] | 5251.9588 |  |  | 16413566.2556
0.00031998
[27 empty] | LINE AVAILABILITY= |  | 99.97%
60 | 709120 | 400KV Raipur-Raigarh # 1 | 2012-10-01 | 0:00 | 2012-10-05 | 19:40 | [9 empty] | 1900-01-03 19:40 | 115 | 40 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 09/2112 | 10/374
| 710053 | 400KV Raipur-Raigarh # 1 | 2012-10-23 | 11:19 | 2012-10-31 | 24:00 | [9 empty] | 1900-01-07 12:41 | 204 | 41 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1715 | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 319 | 81
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 320.35 |  |  |  |  | 217.02 | 2 | 0 | 0 | 744 | 434.04 | 322925.76 | 0 | 100%
61 | 710043 | 400KV Raipur-Raigarh # 2 | 2012-10-15 | 17:13 | 2012-10-23 | 11:11 | [9 empty] | 1900-01-06 17:58 | 185 | 58 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1140 | 10/1714
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 185 | 58
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 185.9667 |  |  |  |  | 217.02 | 2 | 0 | 0 | 744 | 434.04 | 322925.76 | 0 | 100%
62 |  | 400KV Raigarh-Rourkela # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.46 | 2 | 0 | 0 | 744 | 424.92 | 316140.48 | 0 | 100%
63 |  | 400KV Raigarh-SEL # 1
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 99.46 | 2 | 0 | 0 | 744 | 198.92 | 147996.48 | 0 | 100%
64 |  | 400KV SEL -Rourkela #1 | [18 empty] | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 113 | 2 | 0 | 0 | 744 | 226 | 168144 | 0 | 100%
65 | 710065 | 400KV Raipur-KSK | 2012-10-26 | 21:48 | 2012-10-26 | 21:58 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on Overvoltage | -- | --
| 710066 | 400KV Raipur-KSK | 2012-10-26 | 21:58 | 2012-10-31 | 24:00 | [9 empty] | 122:02 | 122 | 2 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | -- | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 10 |  | 122 | 2
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 122.0333 |  |  |  |  | 134.74 | 2 | 0 | 0 | 743.8333 | 269.48 | 200448.2067 | 0 | 100%
66 |  | 400KV Raigarh - KSK
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 86.14 | 2 | 0 | 0 | 744 | 172.28 | 128176.32 | 0 | 100%
67 | 710013 | 400KV Raipur-Raigarh # 4 | 2012-10-05 | 19:54 | 2012-10-13 | 17:10 | [9 empty] | 1900-01-06 21:16 | 189 | 16 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/378 | 10/1017
| 710036 | 400KV Raipur-Raigarh # 4 | 2012-10-13 | 17:34 | 2012-10-15 | 16:04 | [9 empty] | 1899-12-31 22:30 | 46 | 30 | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | 10/1023 | 10/1135
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 235 | 46
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 235.7667 |  |  |  |  | 220.884 | 2 | 0 | 0 | 744 | 441.768 | 328675.392 | 0 | 100%
68 | 709091 | 400KV Raigarh-Rourkela # 3 | 2012-10-01 | 0:00 | 2012-10-21 | 17:25 | [6 empty] | 1900-01-19 17:25 | 497 | 25 |  |  |  | LNCC | Due to heavy rain line tripped on Yph-Bph fault (Tower collapse ) in Rourkela (ER) portion .FL - 135 KM from Raigarh end. Locations No. 364 , 365. | -- | --
| 710072 | 400KV Raigarh-Rourkela # 3 | 2012-10-28 | 9:40 | 2012-10-29 | 13:19 | [12 empty] | LVRD | Line handtripped as per WRLDC instructions for Voltage regulation | WR : 10/2179 ER: 10/237 NLDC : 10/188 | WR : 10/2253 ER: 10/669 NLDC : 10/196
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 497 | 25 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 497.4167 |  |  | 0 |  |  |  |  | 209.283 | 2 | 0 | 0 | 246.5833 | 418.566 | 103211.3995 | 0 | 100%
69 | 709069 | 400KV Raigarh - SEL # 2 | 2012-10-01 | 0:00 | 2012-10-02 | 17:02 | [9 empty] | 1899-12-31 17:02 | 41 | 2 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation. | -- | WR-10/122 ER-10/21 NLDC-10/12
| 710006 | 400KV Raigarh - SEL # 2 | 2012-10-02 | 18:02 | 2012-10-02 | 18:12 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to overvoltage at Raigarh end. | -- | --
| 710007 | 400KV Raigarh - SEL # 2 | 2012-10-02 | 18:12 | 2012-10-02 | 21:02 | [9 empty] | 0.11806 | 2 | 50 | LVRD | Line kept uncharged as per wrldc instrucitons for voltage regualtion. | -- | WR-10/138 ER-10/23 NLDC-10/14
| 710074 | 400KV Raigarh - SEL # 2 | 2012-10-29 | 10:42 | 2012-10-31 | 24:00 | [6 empty] | 1900-01-01 13:18 | 61 | 18 |  |  |  | LNCC | Outage availed to restore line on new towers and remove ERS system (Which was put inplace of collapsed tower. | WR: 10/2244 ER:10/663 NLDC :10/195 | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 61 | 28 |  | 43 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 61.4667 |  |  | 43.8667 |  |  |  |  | 105 | 2 | 0 | 0 | 682.5333 | 210 | 143332 | 0 | 100%
70 |  | 400KV SEL -Rourkela #2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 104.28 | 2 | 0 | 0 | 744 | 208.56 | 155168.64 | 0 | 100%
71 | 710029 | 400KV Ranchi - Sipat # 1 | 2012-10-10 | 11:55 | 2012-10-31 | 24:00 | [9 empty] | 1900-01-20 12:05 | 516 | 5 | OSPD | Outage availed by NTPC Sipat for CB replacement at NTPC Sipat end. | WRLDC :10/743 ER: 10/229 NLDC : 10/63 | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 516 | 5
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 516.0833 |  |  |  |  | 405.772 | 2 | 0 | 0 | 744 | 811.544 | 603788.736 | 0 | 100%
72 |  | 400KV Ranchi- Sipat # 2
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 405.772 | 2 | 0 | 0 | 744 | 811.544 | 603788.736 | 0 | 100%
73 |  | 220KV Korba( e) -Budipadar # 3
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 184 | 1 | 0 | 0 | 744 | 184 | 136896 | 0 | 100%
[8 empty] | 3 | 84 | 0 | 6 | 200 | 0 | 558 | 123 | 0 | 5432 | 1603
[9 empty] | 4.4 |  |  | 9.3333 |  |  | 560.05 |  |  | 5458.7167
1 |  | ICT # 1 400/220KV at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
2 |  | ICT # 2 400/220KV at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
3 |  | ICT # 1 400/220KV at Mapusa
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
4 |  | ICT # 2 400/220KV at Mapusa
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
5 |  | ICT# 1 400/220KV at Boisar
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
6 |  | ICT# 2 400/220KV at Boisar
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
7 |  | ICT # 1 400/220kV at Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
8 |  | ICT # 1 400/220kV at Raigarh
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
9 |  | ICT # 2 400/220kV at Raigarh
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
10 |  | AT-1 765/400KV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
11 |  | AT-2 765/400KV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
12 |  | AT-3 765/400KV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
13 |  | ICT # 1 400/220kV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
14 | 710001 | AT -I 765/400 KV at Wardha | 2012-10-01 | 10:45 | 2012-10-01 | 18:08 | [9 empty] | 0.30764 | 7 | 23 | SCSD | Outage availed to faciliate erection of 400kv Spare reactor bushing. | 10/17 | 10/58
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 7 | 23
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.3833 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
15 |  | AT - 2 765/400 KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
16 |  | AT - 3 765/400 KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
17 |  | AT-1 765/400KV at Bilaspur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
18 |  | AT-2 765/400KV at Bilaspur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
19 |  | ICT # 2 400/220kV at Bhatapara
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
20 |  | ICT # 2 400/220kV at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
21 |  | ICT- 3 400/220KVat Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
22 |  | ICT-1 400/220KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
23 |  | ICT-2 400/220KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
24 |  | ICT-3 400/220KV at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 500 | 2.5 | 0 | 0 | 744 | 1250 | 930000 | 0 | 100%
25 |  | ICT-1 400/220KV at Solapur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
26 |  | ICT-2 400/220KV at Solapur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
27 |  | ICT-1 400/220KV at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
28 |  | ICT-2 400/220KV at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
29 |  | ICT-3 400/220KV at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
30 |  | AT-3 765/400KV at Bilaspur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 23 | [7 empty] | 0 |  |  | 37758000
[9 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.3833 | [10 empty] | 0
[27 empty] | ICT AVAILABILITY= |  | 100%
1 |  | 400 KV Bus reactor at Bhadrawati
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
2 |  | 400 KV Bus reactor at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 744 | 320 | 238080 | 0 | 100%
3 |  | Bus reactor at Mapusa
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
4 |  | Bus reactor at Kolhapur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 744 | 320 | 238080 | 0 | 100%
5 |  | 400 KV Bus reactor at Raigarh
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
6 |  | 765 KV Bus reactor at Seoni
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
7 |  | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
8 |  | 400 KV Bus reactor at Wardha
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
9 |  | Bus Reactor at Solapur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
10 |  | 400 KV Bus reactor at Parli
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
11 |  | 400 KV Bus reactor at Pune
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
12 | 710027 | 765KV Bus reactor at Wardha | 2012-10-09 | 16:58 | 2012-10-09 | 17:42 | 0.030556 | 0 | 44 | [9 empty] | OSPT | Ouatge availed to for maintenance work at Wardha. | 10/659 | 10/666
|  | Sub-Total= | [5 empty] | 0 | 44 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0.73333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0.73333 | 704 | 744 | 960 | 714240 | 0.00098566 | 99.9%
13 |  | 765KV Bus reactor at Bilapsur
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
[8 empty] | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 704 |  |  | 3925344
[9 empty] | 0.73333 |  |  | 0 |  |  | 0 |  |  | 0 | [10 empty] | 0.00017935
[27 empty] | BUS REACTOR AVAILABILITY= |  | 99.98%
[26 empty] | 5955.9588 |  |  | 58096910.2556
0.00010252
[27 empty] | SYSTEM AVAILABILITY= |  | 99.99%
SN | EVENT No. | HVDC POLE | TRIPPING |  | RESTORATION |  | OUTAGE HOURS (HRS.MIN) | [11 empty] | CAT. CODE | DETAILED REASONS OF TRIPPING | WRLDC CODE FOR |  | TCR Pole Capacity ( 50:50%) WR & SR | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | =TCR X OH | THM | RC ( Rated Capacity) Pole Capacity ( 50:50%) WR & SR | =THM X RC | NAFM | TAFM (in Percentage)
|  |  | DATE | TIME | DATE | TIME | Attributed to PGCIL HRS:MIN | Attributed to PGCIL |  | Attributed to Other HRS:MIN | Attributed to Other |  | Attributed to sys conts. HRS:MIN | Attributed to sys conts. |  | Outage deemed available HRS:MIN | Outage deemed available |  |  |  | TRIPPING | CHARGING | A | B | C | D=A X C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 | 710005 | HVDC Pole-1 at Bhadrawati | 2012-10-02 | 16:28 | 2012-10-02 | 16:44 |  | 0 | 0 | 0.011111 | 0 | 16 | [6 empty] | OMSU | Pole tripped due to dip in the 33kv Auxiliary supply provided by MSEDCL. | -- | WR-10/126 SR-10/42 NLDC-10/13
|  | Sub-Total= | [5 empty] | 0 | 0 | 0.011111 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.26667 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 0 | 0 | 743.7333 | 250 | 185933.3333 | 0 | 100%
2 | 710044 | HVDC Pole # 2 at Bhadrawati | 2012-10-16 | 15:34 | 2012-10-16 | 16:58 |  | 0 | 0 | 0.058333 | 1 | 24 | [6 empty] | OMSU | Pole tripped due to dip in the 33KV Auxiliary supply provided by MSEDCL. | -- | WR: 10/1224 SR: 10/417 NLDC: 10/108
|  | Sub-Total= | [5 empty] | 0 | 0 | 0.058333 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 1.4 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 0 | 0 | 742.6 | 250 | 185650 | 0 | 100%
|  | HVDC SYSTEM TOTAL= | [5 empty] | 0 | 0 | 0.069444 | 1 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  | 371583.3333
[9 empty] | 0 |  |  | 1.6667 |  |  | 0 |  |  | 0 | [10 empty] | 0
[27 empty] | HVDC SYSTEM AVAILABILITY= |  | 100%
Formulas:
Attributed to Other HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Outage deemed available HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Attributed to sys conts. HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
OUTAGE HOURS (HRS.MIN) = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]

## ANX-II
MONTH : OCT-2012
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : OCT-2012
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
NIL
Total=

## ANX-V
MONTH : OCT-2012
V. Data to be complied by the inter-State Transmission Licensees
Sl. No. | Type of failures | Restoration Time (Days) |  |  | Remarks
A | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 | Insualtor Failure | Terrain Type
|  | Plain | River bed | Hilly
i | Insualtor Failure in single phase
ii | Insualtor Failure in two phases
ii | Insualtor Failure in three phases
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately. |  |  | 35.1942 | Tower collapse at loc. no. 364-365 of Raigarh-Rourkela # 3
4 | Tower Damage ( not collapse)
i | One arm damage
ii | Two arm damage
5 | Snapping of phase conductor
i | Conductor snapping in single phase
ii | Conductor snapping in two phases
iii | Conductor snapping in three phases
6 | Failure of Earth wire
7 | Insulator failure with conductor snapping
8 | Any other combination of failures
B | Elements of sub-station for each KV class seperately
1 | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
| Other major failures in ICTs | Single phase Unit |  | Three phase Unit
(i) Replacement of faulty bushings
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 | Failures of Reactors
Restoration of failed Reactors