## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-I) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-I) Transmission System in Western Region for the month of NOV- 2013 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 220kV Tarapur - Boisar | 100 | 37 | 765 KV S/C Bilaspur - Seoni # 1 | 100
2 | 400kV Korba-Korba (W) | 100 | 38 | 765 KV S/C Sipat - Bilaspur # 2 | 100
3 | 400kV Korba-Bhilai # 1 | 100 | 39 | 765 KV S/C Bilaspur - Seoni # 2 | 100
4 | 400kV Korba-Bhilai # 2 | 100 | 40 | 765 KV S/C Seoni-Wardha # 1 | 100
5 | 400kV Bhilai-Koradi | 100 | 41 | 765 KV S/C Seoni-Wardha # 2 | 100
6 | 400kV Koradi-Satpura | 100 | 42 | 400 KV D/C Wardha-Akola # 1 | 99.287
7 | 400kV Bhilai - Raipur # 1 | 100 | 43 | 400 KV D/C Wardha-Akola # 2 | 100
8 | 400 KV Bhilai - Bhadrawati | 100 | 44 | 400 KV D/C Akola-Aurangabad # 1 | 100
9 | 400 kV Raipur - Bhadrawati # 1 | 100 | 45 | 400 KV D/C Akola-Aurangabad # 2 | 100
10 | 400kV Raipur - Bhadrawati # 2 | 100 | 46 | 400KV Bhadrawati-Parli # 1 | 100
11 | 400kV Raipur - Bhadrawati # 3 | 100 | 47 | 400KV Bhadrawati-Parli # 2 | 100
12 | 400kV B'vati-Chandrapur # 1 | 100 | 48 | 400KV Parli-Parli # 1 | 100
13 | 400kV B'vati-Chandrapur # 2 | 100 | 49 | 400KV Parli-Parli # 2 | 100
14 | 400kV B'vati-Chandrapur # 3 | 100 | 50 | 400KV Korba-Raipur-3 | 100
15 | 400kV B'vati-Chandrapur # 4 | 100 | 51 | 400KV Korba-Raipur-4 | 100
16 | 400kV Kolhapur - Mapusa # 1 | 100 | 52 | 400KV Wardha-Parli # 1 | 100
17 | 400kV Kolhapur - Mapusa # 2 | 100 | 53 | 400KV Wardha-Parli # 2 | 100
18 | 400kV Tarapur - Padghe # 1 | 100 | 54 | 400KV Korba-Balco (lilo of Korba-Biringsinghpur # 2) | 100
19 | 400kV Tarapur - Padghe # 2 | 100 | 55 | 400KV Balco-Birsinghpur (lilo of Korba-Biringsinghpur # 2) | 100
20 | 400 KV BOISAR - Padge | 100 | 56 | 400KV Mouda-Wardha # 2 | 100
21 | 400kV Tarapur - Boisar #1 | 100 | 57 | 400KV Korba-Vandana (lilo of Korba-Birsinghpur # 1) | 100
22 | 400kV Tarapur - Boisar #2 | 100 | 58 | 400KV Vandana-Bhirshingpur- (lilo of Korba-Birsinghpur # 1) | 100
23 | 400 KV Vapi - Boisar | 100 | 59 | 400KV Raipur-Wardha # 1 | 100
24 | 400kV Vindhyachal - Mahan ( Essar) | 100 | 60 | 400KV Raipur-Wardha # 2 | 100
25 | 400kV Mahan ( Essar) - Korba | 100 | 61 | 400KV Wardha-IEPL (Lilo of Mouda- Wardha # 1 ) | 100
26 | 400 kV Vindyanchal-Korba #2 | 100 | 62 | 400KV IEPL -Mouda (Lilo of Mouda- Wardha # 1 ) | 100
27 | 400 KV Satpura - Seoni (LILO portion) | 100 | 63 | 400KV D/C Raipur-Raipur PS (Durg) # 1 | 100
28 | 400 KV Seoni - Bhilai (LILO portion) | 100 | 64 | 400KV D/C Raipur-Raipur PS (Durg) # 2 | 100
29 | 400KV Bhilai- Bhatapara | 98.8385 | 65 | 400KV Raigarh -Kotra PS # 1 | 100
30 | 400KV Korba - Bhatapara | 100 | 66 | 400KV Raigarh -Kotra PS # 2 | 100
31 | 400kV Korba - Pathadi | 100 | 67 | 765KV D/C Tamnar PS - Kotra PS # 1 | 100
32 | 400kV Pathadi - Sipat | 100 | 68 | 765KV D/C Tamnar PS - Kotra PS # 2 | 100
33 | 400 KV D/C Raipur-Sipat # 1 | 100 | 69 | 400KV Raipur - Raigarh # 1 | 100
34 | 400 KV D/C Raipur-Sipat # 2 | 100 | 70 | D/C Raipur-KWPCL (lilo of Raipur - Raigarh # 2 ) | 100
35 | 400 kV S/C Raipur-Sipat # 3 | 100 | 71 | D/C KWPCL- Raigarh (lilo of Raipur - Raigarh # 2 ) | 100
36 | 765 KV S/C Sipat - Bilaspur # 1 | 100 | 72 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] | 100
73 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] | 100 | 109 | 400/220kV ICT # 2 / Wardha | 100
74 | 400KV Raigarh - Jharsuguda # 1 (lilo of Raigarh - Rourkela#1) | 100 | 110 | 400/220kV ICT # 3 / Wardha | 100
75 | 400KV Jharsuguda- Rourkela # 1 (lilo of Raigarh - Rourkela#1) | 100 | 111 | 400/220kV ICT # 1 / Solapur | 100
76 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] | 100 | 112 | 400/220kV ICT # 2 / Solpaur | 100
77 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] | 100 | 113 | 400/220kV ICT # 1 / Pune | 100
78 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] | 100 | 114 | 400/220kV ICT # 2 / Pune | 100
79 | 400KV Raipur - Raigarh # 4 | 100 | 115 | 400/220kV ICT # 3 / Pune | 100
80 | 400KV Raigarh - Jharsuguda # 2 ( lilo of Raigarh-Rourkela # 3) | 100 | 116 | 765/400kV AT # 3 / Bilaspur | 99.8611
81 | 400KV Jharsuguda-Rourkela # 2 ( lilo of Raigarh-Rourkela # 3) | 100 | 117 | 765/400kV AT # 1 /Kotra PS | 100
82 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] | 100 | 118 | 765/400kV AT # 2 / Kotra PS | 100
83 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] | 100 | 119 | 765/400kV AT # 4 / Kotra PS | 100
84 | 400KV D/C Sipat-Ranchi # 1 | 99.7211 | 120 | 400/220kV ICT # 3 / Mapusa | 100
85 | 400KV D/C Sipat-Ranchi # 2 | 100 | 121 | 765/400kV AT # 1 /Tamnar PS | 100
86 | 220KV Korba-Bhudhipadar # 3 | 100 | 122 | Bus reactor / B'vati | 100
87 | 400/220kV ICT # 1 / Raipur | 100 | 123 | Bus Reactor / Raipur | 100
88 | 400/220kV ICT # 2 / Raipur | 100 | 124 | Bus Reactor / Mapusa | 100
89 | 400/220kV ICT # 1 / Mapusa | 100 | 125 | Bus Reactor / Kolhapur | 100
90 | 400/220kV ICT # 2 / Mapusa | 100 | 126 | Bus Reactor / Raigarh | 100
91 | 400/220kV ICT # 1 / Boisar | 100 | 127 | Bus Reactor / Seoni (3 x 80) | 100
92 | 400/220kV ICT # 2 / Boisar | 100 | 128 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur | 100
93 | 400/220kV ICT # 1 / Bhatapara | 99.1134 | 129 | Bus Reactor / Wardha | 100
94 | 400/220kV ICT # 1 / Raigarh | 100 | 130 | Bus Reactor / Solapur | 100
95 | 400/220kV ICT # 2 / Raigarh | 100 | 131 | Bus Reactor / Parli | 100
96 | 765/400kV AT # 1 / Seoni | 100 | 132 | Bus Reactor / Pune | 100
97 | 765/400kV AT # 2 / Seoni | 100 | 133 | 765KV Bus Reactor / Wardha(3x80) | 99.7431
98 | 765/400kV AT # 3 / Seoni | 100 | 134 | 765KV Bus Reactor / Bilaspur(3x80) | 100
99 | 400/220kV ICT # 1 / Seoni | 100 | 135 | 765KV Bina line Switchable Line Reactor at Seoni (3x80) | 100
100 | 765/220kV AT # 1 / Wardha | 100 | 136 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80) | 100
101 | 765/220kV AT # 2 / Wardha | 100 | 137 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80) | 100
102 | 765/220kV AT # 3 / Wardha | 100 | 138 | 765KV Ranchi # 1 Switchable line Reactor charged as Bus Reactor at Bilaspur | 100
103 | 765/220kV AT # 1 / Bilaspur | 99.7222 | 139 | 765KV Bus Reactor at Kotra PS | 100
104 | 765/220kV AT # 2 / Bilaspur | 99.7222 | 140 | 400KV Bus Reactor / Kotra PS | 100
105 | 400/220kV ICT # 2 / Bhatapara | 100 | 141 | 765KV Raipur # 1 Switchable Line Reactor charged as Bus Reactor at Kotra PS | 100
106 | 400/220kV ICT # 2 / Seoni | 100 | 142 | 765KV Raipur # 2 Switchable Line Reactor charged as Bus Reactor at Kotra PS | 100
107 | 400/220kV ICT # 3 / Raipur | 100 | 143 | 500 MW HVDC B'vati Pole # 1 | 100
108 | 400/220kV ICT # 1 / Wardha | 100 | 144 | 500 MW HVDC B'vati Pole # 2 | 99.9699
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
66
85
Availability Bus Reactors =
System Availability :-

## WRPC AVAIL
AVAILABILITY OF AC SYSTEM : NOV-2013
OUTAGE DATA FOR POWERGRID TRANSMISSION SYSTEM
|  | 2013-11-16 |  |  |  | Total Outage | Total Outage |  | Line length |  |  |  |  | Individual line Availability
[6 empty] | Hrs | Hrs | Individual |  | NSC1 | OH1* | Cktkm1 * NSC1 | THM
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | PGCIL | OTHERS | THM | Ckrkm1 |  | NSC1*CktKm1 |  | *Cktkm1 * NSC1
No. |  | Hrs | Mints | Hrs | Mints | OH1 | OH2
[6 empty] | Hrs | Hrs
WRTS-I
1 | 220kV Tarapur - Boisar |  |  |  |  | 0 | 0 | 720 | 20.56 | 1 | 0 | 20.56 | 14803.2 | 100
2 | 400kV Korba-Korba (W) |  |  |  |  | 0 | 0 | 720 | 14 | 2 | 0 | 28 | 20160 | 100
3 | 400kV Korba-Bhilai # 1 |  |  |  |  | 0 | 0 | 720 | 197 | 2 | 0 | 394 | 283680 | 100
4 | 400kV Korba-Bhilai # 2 |  |  |  |  | 0 | 0 | 720 | 192 | 2 | 0 | 384 | 276480 | 100
5 | 400kV Bhilai-Koradi |  |  |  |  | 0 | 0 | 720 | 272 | 2 | 0 | 544 | 391680 | 100
6 | 400kV Koradi-Satpura |  |  |  |  | 0 | 0 | 720 | 149 | 2 | 0 | 298 | 214560 | 100
7 | 400kV Bhilai - Raipur # 1 |  |  |  |  | 0 | 0 | 720 | 13 | 2 | 0 | 26 | 18720 | 100
8 | 400 KV Bhilai - Bhadrawati |  |  |  |  | 0 | 0 | 720 | 322 | 2 | 0 | 644 | 463680 | 100
9 | 400 kV Raipur - Bhadrawati # 1 |  |  |  |  | 0 | 0 | 720 | 333 | 2 | 0 | 666 | 479520 | 100
10 | 400kV Raipur - Bhadrawati # 2 |  |  |  |  | 0 | 0 | 720 | 345.55 | 2 | 0 | 691.1 | 497592 | 100
11 | 400kV Raipur - Bhadrawati # 3 |  |  |  |  | 0 | 0 | 720 | 345.55 | 2 | 0 | 691.1 | 497592 | 100
12 | 400kV B'vati-Chandrapur # 1 |  |  |  |  | 0 | 0 | 720 | 20 | 2 | 0 | 40 | 28800 | 100
13 | 400kV B'vati-Chandrapur # 2 |  |  |  |  | 0 | 0 | 720 | 20 | 2 | 0 | 40 | 28800 | 100
14 | 400kV B'vati-Chandrapur # 3 |  |  |  |  | 0 | 0 | 720 | 22.42 | 2 | 0 | 44.84 | 32284.8 | 100
15 | 400kV B'vati-Chandrapur # 4 |  |  |  |  | 0 | 0 | 720 | 22.42 | 2 | 0 | 44.84 | 32284.8 | 100
16 | 400kV Kolhapur - Mapusa # 1 |  |  |  |  | 0 | 0 | 720 | 150 | 2 | 0 | 300 | 216000 | 100
17 | 400kV Kolhapur - Mapusa # 2 |  |  |  |  | 0 | 0 | 720 | 150 | 2 | 0 | 300 | 216000 | 100
18 | 400kV Tarapur - Padghe # 1 |  |  |  |  | 0 | 0 | 720 | 91.119 | 2 | 0 | 182.238 | 131211.36 | 100
19 | 400kV Tarapur - Padghe # 2 |  |  |  |  | 0 | 0 | 720 | 91.119 | 2 | 0 | 182.238 | 131211.36 | 100
20 | 400 KV BOISAR - Padge |  |  |  |  | 0 | 0 | 720 | 101 | 2 | 0 | 202 | 145440 | 100
21 | 400kV Tarapur - Boisar #1 |  |  |  |  | 0 | 0 | 720 | 20.881 | 2 | 0 | 41.762 | 30068.64 | 100
22 | 400kV Tarapur - Boisar #2 |  |  | 0 | 20 | 0 | 0.33333 | 719.6667 | 20.881 | 2 | 0 | 41.762 | 30054.7193 | 100
23 | 400 KV Vapi - Boisar |  |  |  |  | 0 | 0 | 720 | 91 | 2 | 0 | 182 | 131040 | 100
24 | 400kV Vindhyachal - Mahan ( Essar) |  |  |  |  | 0 | 0 | 720 | 19 | 2 | 0 | 38 | 27360 | 100
25 | 400kV Mahan ( Essar) - Korba |  |  |  |  | 0 | 0 | 720 | 196 | 2 | 0 | 392 | 282240 | 100
26 | 400 kV Vindyanchal-Korba #2 |  |  |  |  | 0 | 0 | 720 | 288.994 | 2 | 0 | 577.988 | 416151.36 | 100
27 | 400 KV Satpura - Seoni (LILO portion) |  |  |  |  | 0 | 0 | 720 | 1.507 | 2 | 0 | 3.014 | 2170.08 | 100
28 | 400 KV Seoni - Bhilai (LILO portion) |  |  |  |  | 0 | 0 | 720 | 1.498 | 2 | 0 | 2.996 | 2157.12 | 100
29 | 400KV Bhilai- Bhatapara | 8 | 0 | 31 | 14 | 8 | 31.2333 | 688.7667 | 90.453 | 2 | 1447.248 | 180.906 | 124602.0226 | 98.8385
30 | 400KV Korba - Bhatapara |  |  |  |  | 0 | 0 | 720 | 123.73 | 2 | 0 | 247.46 | 178171.2 | 100
31 | 400kV Korba - Pathadi |  |  |  |  | 0 | 0 | 720 | 39.536 | 2 | 0 | 79.072 | 56931.84 | 100
32 | 400kV Pathadi - Sipat |  |  |  |  | 0 | 0 | 720 | 29.117 | 2 | 0 | 58.234 | 41928.48 | 100
33 | 400 KV D/C Raipur-Sipat # 1 |  |  |  |  | 0 | 0 | 720 | 149.12 | 2 | 0 | 298.24 | 214732.8 | 100
34 | 400 KV D/C Raipur-Sipat # 2 |  |  |  |  | 0 | 0 | 720 | 149.12 | 2 | 0 | 298.24 | 214732.8 | 100
35 | 400 kV S/C Raipur-Sipat # 3 |  |  |  |  | 0 | 0 | 720 | 162.04 | 2 | 0 | 324.08 | 233337.6 | 100
36 | 765 KV S/C Sipat - Bilaspur # 1 |  |  |  |  | 0 | 0 | 720 | 21.507 | 4 | 0 | 86.028 | 61940.16 | 100
37 | 765 KV S/C Bilaspur - Seoni # 1 |  |  |  |  | 0 | 0 | 720 | 337.046 | 4 | 0 | 1348.184 | 970692.48 | 100
38 | 765 KV S/C Sipat - Bilaspur # 2 |  |  |  |  | 0 | 0 | 720 | 22.216 | 4 | 0 | 88.864 | 63982.08 | 100
39 | 765 KV S/C Bilaspur - Seoni # 2 |  |  |  |  | 0 | 0 | 720 | 338.33 | 4 | 0 | 1353.32 | 974390.4 | 100
40 | 765 KV S/C Seoni-Wardha # 1 |  |  |  |  | 0 | 0 | 720 | 267.894 | 4 | 0 | 1071.576 | 771534.72 | 100
41 | 765 KV S/C Seoni-Wardha # 2 |  |  | 0 | 30 | 0 | 0.5 | 719.5 | 260.763 | 4 | 0 | 1043.052 | 750475.914 | 100
42 | 400 KV D/C Wardha-Akola # 1 | 4 | 65 | 7 | 3 | 5.0833 | 7.05 | 712.95 | 161.865 | 2 | 1645.6275 | 323.73 | 230803.3035 | 99.287
43 | 400 KV D/C Wardha-Akola # 2 |  |  |  |  | 0 | 0 | 720 | 161.865 | 2 | 0 | 323.73 | 233085.6 | 100
44 | 400 KV D/C Akola-Aurangabad # 1 |  |  |  |  | 0 | 0 | 720 | 241.23 | 2 | 0 | 482.46 | 347371.2 | 100
45 | 400 KV D/C Akola-Aurangabad # 2 |  |  |  |  | 0 | 0 | 720 | 241.23 | 2 | 0 | 482.46 | 347371.2 | 100
46 | 400KV Bhadrawati-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 378.667 | 2 | 0 | 757.334 | 545280.48 | 100
47 | 400KV Bhadrawati-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 378.667 | 2 | 0 | 757.334 | 545280.48 | 100
48 | 400KV Parli-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 4.958 | 2 | 0 | 9.916 | 7139.52 | 100
49 | 400KV Parli-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 4.958 | 2 | 0 | 9.916 | 7139.52 | 100
50 | 400KV Korba-Raipur-3 |  |  |  |  | 0 | 0 | 720 | 212.83 | 2 | 0 | 425.66 | 306475.2 | 100
51 | 400KV Korba-Raipur-4 |  |  |  |  | 0 | 0 | 720 | 212.83 | 2 | 0 | 425.66 | 306475.2 | 100
52 | 400KV Wardha-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 336.939 | 4 | 0 | 1347.756 | 970384.32 | 100
53 | 400KV Wardha-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 336.939 | 4 | 0 | 1347.756 | 970384.32 | 100
54 | 400KV Korba-Balco (lilo of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 720 | 7.454 | 2 | 0 | 14.908 | 10733.76 | 100
55 | 400KV Balco-Birsinghpur (lilo of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 720 | 219.188 | 2 | 0 | 438.376 | 315630.72 | 100
56 | 400KV Mouda-Wardha # 2 |  |  |  |  | 0 | 0 | 720 | 123.45 | 4 | 0 | 493.8 | 355536 | 100
57 | 400KV Korba-Vandana (lilo of Korba-Birsinghpur # 1) |  |  |  |  | 0 | 0 | 720 | 14.768 | 2 | 0 | 29.536 | 21265.92 | 100
58 | 400KV Vandana-Bhirshingpur- (lilo of Korba-Birsinghpur # 1) |  |  |  |  | 0 | 0 | 720 | 211.874 | 2 | 0 | 423.748 | 305098.56 | 100
59 | 400KV Raipur-Wardha # 1 |  |  |  |  | 0 | 0 | 720 | 370.565 | 4 | 0 | 1482.26 | 1067227.2 | 100
60 | 400KV Raipur-Wardha # 2 |  |  |  |  | 0 | 0 | 720 | 370.565 | 4 | 0 | 1482.26 | 1067227.2 | 100
61 | 400KV Wardha-IEPL (Lilo of Mouda- Wardha # 1 ) |  |  |  |  | 0 | 0 | 720 | 52.62 | 4 | 0 | 210.48 | 151545.6 | 100
62 | 400KV IEPL -Mouda (Lilo of Mouda- Wardha # 1 ) |  |  |  |  | 0 | 0 | 720 | 70.83 | 4 | 0 | 283.32 | 203990.4 | 100
63 | 400KV D/C Raipur-Raipur PS (Durg) # 1 |  |  |  |  | 0 | 0 | 720 | 21.43 | 2 | 0 | 42.86 | 30859.2 | 100
64 | 400KV D/C Raipur-Raipur PS (Durg) # 2 |  |  |  |  | 0 | 0 | 720 | 21.43 | 2 | 0 | 42.86 | 30859.2 | 100
65 | 400KV Raigarh -Kotra PS # 1 |  |  |  |  | 0 | 0 | 720 | 6.288 | 2 | 0 | 12.576 | 9054.72 | 100
66 | 400KV Raigarh -Kotra PS # 2 |  |  |  |  | 0 | 0 | 720 | 6.288 | 2 | 0 | 12.576 | 9054.72 | 100
67 | 765KV D/C Tamnar PS - Kotra PS # 1 |  |  |  |  | 0 | 0 | 720 | 47.986 | 6 | 0 | 287.916 | 207299.52 | 100
68 | 765KV D/C Tamnar PS - Kotra PS # 2 |  |  |  |  | 0 | 0 | 720 | 47.986 | 6 | 0 | 287.916 | 207299.52 | 100
69 | 400KV Raipur - Raigarh # 1 |  |  |  |  | 0 | 0 | 720 | 217.02 | 2 | 0 | 434.04 | 312508.8 | 100
70 | D/C Raipur-KWPCL (lilo of Raipur - Raigarh # 2 ) |  |  |  |  | 0 | 0 | 720 | 208.29 | 2 | 0 | 416.58 | 299937.6 | 100
71 | D/C KWPCL- Raigarh (lilo of Raipur - Raigarh # 2 ) |  |  |  |  | 0 | 0 | 720 | 8.73 | 2 | 0 | 17.46 | 12571.2 | 100
72 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 720 | 99.46 | 2 | 0 | 198.92 | 143222.4 | 100
73 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 720 | 113 | 2 | 0 | 226 | 162720 | 100
74 | 400KV Raigarh - Jharsuguda # 1 (lilo of Raigarh - Rourkela#1) |  |  | 11 | 39 | 0 | 11.65 | 708.35 | 114.46 | 2 | 0 | 228.92 | 162155.482 | 100 | 100
75 | 400KV Jharsuguda- Rourkela # 1 (lilo of Raigarh - Rourkela#1) |  |  |  |  | 0 | 0 | 720 | 142.448 | 2 | 0 | 284.896 | 205125.12 | 100 | 100
76 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] |  |  |  |  | 0 | 0 | 720 | 134.74 | 2 | 0 | 269.48 | 194025.6 | 100
77 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] |  |  |  |  | 0 | 0 | 720 | 85.01 | 2 | 0 | 170.02 | 122414.4 | 100 |  | 108
78 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] |  |  |  |  | 0 | 0 | 720 | 1.129 | 2 | 0 | 2.258 | 1625.76 | 100
79 | 400KV Raipur - Raigarh # 4 |  |  |  |  | 0 | 0 | 720 | 220.884 | 2 | 0 | 441.768 | 318072.96 | 100
80 | 400KV Raigarh - Jharsuguda # 2 ( lilo of Raigarh-Rourkela # 3) |  |  | 10 | 9 | 0 | 10.15 | 709.85 | 110.98 | 2 | 0 | 221.96 | 157558.306 | 100
81 | 400KV Jharsuguda-Rourkela # 2 ( lilo of Raigarh-Rourkela # 3) |  |  |  |  | 0 | 0 | 720 | 143.06 | 2 | 0 | 286.12 | 206006.4 | 100
82 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] |  |  |  |  | 0 | 0 | 720 | 105 | 2 | 0 | 210 | 151200 | 100
83 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] |  |  |  |  | 0 | 0 | 720 | 104.28 | 2 | 0 | 208.56 | 150163.2 | 100
84 | 400KV D/C Sipat-Ranchi # 1 | 2 | 0 | 2 | 57 | 2 | 2.95 | 717.05 | 405.772 | 2 | 1623.088 | 811.544 | 581917.6252 | 99.7211
85 | 400KV D/C Sipat-Ranchi # 2 |  |  |  |  | 0 | 0 | 720 | 405.772 | 2 | 0 | 811.544 | 584311.68 | 100
86 | 220KV Korba-Bhudhipadar # 3 |  |  |  |  | 0 | 0 | 720 | 184 | 1 | 0 | 184 | 132480 | 100
87 | 400/220kV ICT # 1 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
88 | 400/220kV ICT # 2 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
89 | 400/220kV ICT # 1 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
90 | 400/220kV ICT # 2 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
91 | 400/220kV ICT # 1 / Boisar |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
92 | 400/220kV ICT # 2 / Boisar |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
93 | 400/220kV ICT # 1 / Bhatapara | 6 | 23 |  |  | 6.3833 | 0 | 720 | 315 | 2.5 | 5026.875 | 787.5 | 567000 | 99.1134
94 | 400/220kV ICT # 1 / Raigarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
95 | 400/220kV ICT # 2 / Raigarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
96 | 765/400kV AT # 1 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
97 | 765/400kV AT # 2 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
98 | 765/400kV AT # 3 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
99 | 400/220kV ICT # 1 / Seoni |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
100 | 765/220kV AT # 1 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
101 | 765/220kV AT # 2 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
102 | 765/220kV AT # 3 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
103 | 765/220kV AT # 1 / Bilaspur | 2 | 0 |  |  | 2 | 0 | 720 | 1500 | 2.5 | 7500 | 3750 | 2700000 | 99.7222
104 | 765/220kV AT # 2 / Bilaspur | 2 | 0 |  |  | 2 | 0 | 720 | 1500 | 2.5 | 7500 | 3750 | 2700000 | 99.7222
105 | 400/220kV ICT # 2 / Bhatapara |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
106 | 400/220kV ICT # 2 / Seoni |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
107 | 400/220kV ICT # 3 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
108 | 400/220kV ICT # 1 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
109 | 400/220kV ICT # 2 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
110 | 400/220kV ICT # 3 / Wardha |  |  |  |  | 0 | 0 | 720 | 500 | 2.5 | 0 | 1250 | 900000 | 100
111 | 400/220kV ICT # 1 / Solapur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
112 | 400/220kV ICT # 2 / Solpaur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
113 | 400/220kV ICT # 1 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
114 | 400/220kV ICT # 2 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
115 | 400/220kV ICT # 3 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
116 | 765/400kV AT # 3 / Bilaspur | 1 | 0 |  |  | 1 | 0 | 720 | 1500 | 2.5 | 3750 | 3750 | 2700000 | 99.8611
117 | 765/400kV AT # 1 /Kotra PS |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
118 | 765/400kV AT # 2 / Kotra PS |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
119 | 765/400kV AT # 4 / Kotra PS |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
120 | 400/220kV ICT # 3 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 100
121 | 765/400kV AT # 1 /Tamnar PS |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 100
122 | Bus reactor / B'vati |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 100
123 | Bus Reactor / Raipur |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 100
124 | Bus Reactor / Mapusa |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 100
125 | Bus Reactor / Kolhapur |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 100
126 | Bus Reactor / Raigarh |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 100
127 | Bus Reactor / Seoni (3 x 80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
128 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 100
129 | Bus Reactor / Wardha |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 100
130 | Bus Reactor / Solapur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 100
131 | Bus Reactor / Parli |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 100
132 | Bus Reactor / Pune |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 100
133 | 765KV Bus Reactor / Wardha(3x80) | 1 | 51 |  |  | 1.85 | 0 | 720 | 240 | 4 | 1776 | 960 | 691200 | 99.7431
134 | 765KV Bus Reactor / Bilaspur(3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
135 | 765KV Bina line Switchable Line Reactor at Seoni (3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
136 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
137 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
138 | 765KV Ranchi # 1 Switchable line Reactor charged as Bus Reactor at Bilaspur |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
139 | 765KV Bus Reactor at Kotra PS |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
140 | 400KV Bus Reactor / Kotra PS |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 100
141 | 765KV Raipur # 1 Switchable Line Reactor charged as Bus Reactor at Kotra PS |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
142 | 765KV Raipur # 2 Switchable Line Reactor charged as Bus Reactor at Kotra PS |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 100
143 | 500 MW HVDC B'vati Pole # 1 |  |  |  | 10 | 0 | 0.16667 | 719.8333 | 250 | 0 | 250 | 179958.3333 |  | 100
144 | 500 MW HVDC B'vati Pole # 2 | 0 | 13 |  |  | 0.21667 | 0 | 720 | 250 | 54.1667 | 250 | 180000 |  | 99.9699

## Tripping
POWERGRID CORPORATION OF INDIA LIMITED
LINE TRIPPING DETAILS OF WRTS - 1 NOV-2013
TOTAL NUMBER OF ELEMENTS :144
SN | Event No. | Voltage KV | Element Name | Tripping Date | Tripping Time | Resto-ration Date | Resto-ration Time | Attributed to PGCIL | Attributed to PGCIL |  |  | Attributed to Other |  |  | Attributed to sys conts. |  |  | Outage deemed available |  | Cat. Code | Reason of Tripping | Tripping Code | Charging Code
[9 empty] | HRS | MIN | Attributed to Other | HRS | MIN | Attributed to sys conts. | HRS | MIN | Outage deemed available | HRS | MIN
1 | 710007 | 400 | Raigarh-Raipur # 4 | 2013-10-02 | 11:35 | 2013-11-15 | 17:57 | [9 empty] | 353:57 | 353 | 57 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/103 | 11/1261
2 | 701028 | 400/220 | ICT-3:315MVA:PUNE | 2013-10-11 | 10:40 | 2013-11-09 | 11:31 | [9 empty] | 203:31 | 203 | 31 | SPRD | H/T as per WRLDC instructions for power regulation | 10/752 | 11/670
3 | 701062 | 400 | Bus Reactor / Pune (50) | 2013-10-21 | 11:59 | 2013-11-03 | 17:05 | [9 empty] | 65:05 | 65 | 5 | SVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1412 | 11/204
4 | 701078 | 400 | Jharsuguda-Raigarh # 2 | 2013-10-28 | 2:50 | 2013-11-08 | 10:17 | [9 empty] | 178:17 | 178 | 17 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/2105 | WR-'11/577, ER-11/171 ,NL-11/66
5 | 701080 | 400 | Bhilai -Korba # 1 | 2013-10-29 | 12:03 | 2013-11-01 | 12:11 | [9 empty] | 12:11 | 12 | 11 | LVRD | Line kept uncharged due to outage taken by NTPC for maintenance works | 10/2047 | 11/30
6 | 701084 | 400 | Kolhapur - Mapusa # 1 | 2013-10-30 | 21:27 | 2013-11-08 | 10:55 | [9 empty] | 178:55 | 178 | 55 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/2187 | 11/582
7 | 711001 | 765 | Seoni-Wardha # 2 | 2013-11-02 | 21:28 | 2013-11-02 | 21:38 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on over voltage at Wardha.
8 | 711002 | 765 | Seoni-Wardha # 2 | 2013-11-02 | 21:38 | 2013-11-06 | 8:53 | [9 empty] | 1900-01-02 11:15 | 83 | 15 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | WR -11/423, NL-11/47
9 | 711003 | 400 | Boisar-Tarapur # 2 | 2013-11-03 | 9:02 | 2013-11-03 | 9:12 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on over voltage at Boisar | -- | --
10 | 711004 | 400 | Boisar-Tarapur # 2 | 2013-11-03 | 9:12 | 2013-11-03 | 10:35 | [9 empty] | 0.057639 | 1 | 23 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/176
11 | 711005 | 400 | Bhadrawati-Parli # 1 | 2013-11-03 | 17:44 | 2013-11-04 | 9:33 | [9 empty] | 0.65903 | 15 | 49 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/214 | 11/262
12 | 711006 | 400 | Boisar-Tarapur # 2 | 2013-11-04 | 0:52 | 2013-11-04 | 1:02 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped on over voltage at Boisar | -- | --
13 | 711007 | 400 | Boisar-Tarapur # 2 | 2013-11-04 | 1:02 | 2013-11-04 | 6:28 | [9 empty] | 0.22639 | 5 | 26 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 11/246
14 | 711008 | 400 | Bhadrawati-Parli # 1 | 2013-11-04 | 16:51 | 2013-11-05 | 9:30 | [9 empty] | 0.69375 | 16 | 39 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/288 | 11/332
15 | 711009 | 765/400 | ICT-2:1500MVA: BILASPUR | 2013-11-05 | 11:21 | 2013-11-05 | 17:15 | [9 empty] | 5:54 | 5 | 54 | SCSD | ICT outage availed for construction warranty test. | 11/349, NL-11/34 | 11/368 NL-11/40
16 | 711010 | 400 | Bhadrawati-Parli # 1 | 2013-11-05 | 21:39 | 2013-11-06 | 15:37 | [9 empty] | 0.74861 | 17 | 58 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/386
17 | 711011 | 765/400 | ICT-2:1500MVA: BILASPUR | 2013-11-06 | 10:15 | 2013-11-06 | 15:05 | [9 empty] | 4:50 | 4 | 50 | SCSD | ICT outage availed for construction warranty test. | 11/429 | 11/442
18 | 711012 | 400 | Bhadrawati-Parli # 2 | 2013-11-06 | 17:46 | 2013-11-07 | 14:51 | [9 empty] | 0.87847 | 21 | 5 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/456 | 11/523
19 | 711013 | 400 | Boisar - Padhge | 2013-11-06 | 22:37 | 2013-11-07 | 8:05 | [9 empty] | 0.39444 | 9 | 28 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/478 | 11/505
20 | 711014 | 765/400 | ICT-2:1500MVA: BILASPUR | 2013-11-07 | 11:40 | 2013-11-07 | 20:15 | [9 empty] | 8:35 | 8 | 35 | SCSD | ICT outage availed for construction warranty test. | WR:11/518, NLDC:11/60 | WR:11/541, NLDC:11/62
21 | 711015 | 765 | Seoni-Wardha # 2 | 2013-11-07 | 20:06 | 2013-11-07 | 20:16 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to O/V at Seoni S/S. | -- | --
22 | 711016 | 765 | Seoni-Wardha # 2 | 2013-11-07 | 20:16 | 2013-11-12 | 10:20 | [9 empty] | 1900-01-03 14:04 | 110 | 4 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | WR:11/542 | WR-11/917, NL-11/104
23 | 711017 | 400 | Bus Reactor / Solapur (63) | 2013-11-08 | 9:26 | 2013-11-09 | 16:57 | [9 empty] | 1899-12-31 07:31 | 31 | 31 | SVRD | H/T as per WRLDC instructions for Voltage regulation | 11/575 | 11/690
24 | 711018 | 765/400 | ICT-2:1500MVA: BILASPUR | 2013-11-08 | 10:10 | 2013-11-08 | 14:15 | [9 empty] | 4:05 | 4 | 5 | SCSD | ICT outage availed for construction warranty test. | 11/580, NL-11/67 | 11/595, NL-11/69
25 | 711019 | 400 | Kolhapur - Mapusa # 1 | 2013-11-08 | 16:45 | 2013-11-10 | 11:01 | [9 empty] | 1899-12-31 18:16 | 42 | 16 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/606 | 11/742
26 | 711020 | 400 | Jharsuguda-Raigarh # 2 | 2013-11-09 | 9:16 | 2013-11-09 | 19:25 | [6 empty] | 0.42292 | 10 | 9 |  |  |  | LMAC | Replacement of Insulator string damaged due to Militant activity . | WR-658, ER-11/186, NL-11/73 | WR-706, ER-11/197, NL-11/78
27 | 711021 | 400/220 | ICT-1:315MVA :BHATAPARA | 2013-11-09 | 9:50 | 2013-11-09 | 16:13 | 6:23 | 6 | 23 | [9 empty] | OSPT | ICT outage availed for AMP works and DGA of bushing oil. | 11/662 | 11/696
28 | 711022 | 400/220 | ICT-1:315MVA:PUNE | 2013-11-09 | 13:05 | 2013-11-10 | 19:22 | [9 empty] | 1899-12-31 06:17 | 30 | 17 | SPRD | H/T for power regulation as per WRLDC instructions | 11/678 | 11/769
29 | 711023 | HVDC | POLE # 1 : BHADRAWATI | 2013-11-09 | 14:50 | 2013-11-09 | 15:00 |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | OMSU | Pole tripped due to voltage dip in auxillary power supply |  | WR-682, SR-11/306, NL-11/76
30 | 711024 | 400 | Jharsuguda-Raigarh # 1 | 2013-11-10 | 9:31 | 2013-11-10 | 21:10 | [6 empty] | 0.48542 | 11 | 39 |  |  |  | LMAC | Replacement of Insulator string damaged due to Militant activity . | WR-734, ER-11/205, NL-11/84 | WR-776, ER-11/218, NL-11/86
31 | 711025 | 400 | Kolhapur - Mapusa # 2 | 2013-11-10 | 16:33 | 2013-11-12 | 10:33 | [9 empty] | 1899-12-31 18:00 | 42 | 0 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/761 | 11/919
32 | 711026 | 400/220 | ICT-2:315MVA:PUNE | 2013-11-11 | 8:08 | 2013-11-12 | 13:44 | [9 empty] | 1899-12-31 05:36 | 29 | 36 | SPRD | H/T for power regulation as per WRLDC instructions | 11/801 | 11/939
33 | 711027 | 400 | Korba-Vindhyachal # 2 | 2013-11-11 | 9:15 | 2013-11-13 | 17:37 | [9 empty] | 1900-01-01 08:22 | 56 | 22 | OSPD | Outage availed by NTPC for maintenance works | 11/811 | 11/1049
34 | 711028 | 765/400 | ICT-1:1500MVA: BILASPUR | 2013-11-11 | 10:35 | 2013-11-11 | 15:20 | [9 empty] | 4:45 | 4 | 45 | SCSD | ICT outage availed for construction warranty test. | WR-11/821, NL-11/93 | WR-11/844, NL-11/96
35 | 711029 | 400 | Bus Reactor / Parli (63) | 2013-11-11 | 14:33 | 2013-11-11 | 17:10 | [9 empty] | 0.10903 | 2 | 37 | SVRD | Busreactor H/T as per WRLDC instructions for Voltage regulation | 11/841 | 11/859
36 | 711030 | 400 | Bus Reactor / Solapur (63) | 2013-11-11 | 14:52 | 2013-11-11 | 16:38 | [9 empty] | 0.073611 | 1 | 46 | SVRD | Busreactor H/T as per WRLDC instructions for Voltage regulation | 11/843 | 11/855
37 | 711031 | 400 | Bus Reactor / Solapur (63) | 2013-11-12 | 9:44 | 2013-11-12 | 15:33 | [9 empty] | 0.24236 | 5 | 49 | SVRD | Busreactor H/T as per WRLDC instructions for Voltage regulation | 11/914 | 11/951
38 | 711032 | 765/400 | ICT-1:1500MVA: BILASPUR | 2013-11-12 | 10:36 | 2013-11-12 | 14:40 | [9 empty] | 4:04 | 4 | 4 | SCSD | ICT outage availed for construction warranty test. | WR-11/921, NL-11/105 | WR-11/942, NL-11/107
39 | 711033 | 400/220 | ICT-1:315MVA:PUNE | 2013-11-12 | 13:43 | 2013-11-12 | 15:22 | [9 empty] | 0.06875 | 1 | 39 | SPRD | H/T for power regulation as per WRLDC instructions | 11/940 | 11/945
40 | 711034 | 400/220 | ICT-2:315MVA:PUNE | 2013-11-12 | 15:20 | 2013-11-30 | 24:00 | [9 empty] | 1900-01-17 08:40 | 440 | 40 | SPRD | H/T for power regulation as per WRLDC instructions | 11/946 | --
41 | 711035 | 400 | Kolhapur - Mapusa # 1 | 2013-11-12 | 16:30 | 2013-11-13 | 8:44 | [9 empty] | 0.67639 | 16 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/955 | 11/994
42 | 711036 | 765 | Seoni-Wardha # 1 | 2013-11-12 | 22:12 | 2013-11-21 | 12:05 | [9 empty] | 1900-01-07 13:53 | 205 | 53 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | WR-11/979, NL-11/118 | WR-11/1964, NL-11/225
43 | 711037 | 765/400 | ICT-1:1500MVA: BILASPUR | 2013-11-13 | 12:08 | 2013-11-13 | 15:10 | [9 empty] | 3:02 | 3 | 2 | SCSD | ICT outage availed for construction warranty test. | WR-11/1020, NL-11/127 | WR-11/1034, NL-11/128
44 | 711038 | 400 | Akola-Wardha # 1 | 2013-11-13 | 12:50 | 2013-11-13 | 14:31 | 1:41 | 1 | 41 | [9 empty] | LHWT | Line tripped on Y-E fault at F.L.77.5km from Wardha and 82.3km from Akola. F.C.=4.5KA. Yph Insulator D-capped at loc. no. 206. | - | - |  | 1.1333
45 | 711039 | 400 | Akola-Wardha # 1 | 2013-11-13 | 14:31 | 2013-11-13 | 21:34 | [6 empty] | 7:03 | 7 | 3 |  |  |  | LMAC | Line rectification works affected terribly due to villagers miscreants activities as bullock died due to Y-E phase fault in line. | - | - | 11 | 68
46 | 711040 | 400 | Akola-Wardha # 1 | 2013-11-13 | 21:34 | 2013-11-14 | 0:58 | 3:24 | 3 | 24 | [9 empty] | OSPT | Outage availed for line rectification work after discontinue of villagers miscreants activities. | - | 11/1072 |  | 12.1333
47 | 711041 | 400 | Akola-Aurangabad # 1 | 2013-11-13 | 14:32 | 2013-11-14 | 1:21 | [9 empty] | 0.45069 | 10 | 49 | LPRD | Line H/T as per WRLDC instructions for Power regulation | 11/1035 | 11/1074
48 | 711042 | 400 | Kolhapur - Mapusa # 1 | 2013-11-13 | 16:11 | 2013-11-14 | 9:02 | [9 empty] | 0.70208 | 16 | 51 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1040 | 11/1104
49 | 711043 | 400 | Bus Reactor / Solapur (63) | 2013-11-14 | 9:47 | 2013-11-14 | 17:12 | [9 empty] | 0.30903 | 7 | 25 | SVRD | H/T as per WRLDC instructions for Voltage regulation | 11/1115 | 11/1161
50 | 711044 | 765/400 | ICT-1:1500MVA: BILASPUR | 2013-11-14 | 10:05 | 2013-11-14 | 13:50 | [9 empty] | 3:45 | 3 | 45 | SCSD | ICT outage availed for construction warranty test. | 11/1116 | 11/1141, NL-11/143
51 | 711045 | 400 | Jharsuguda-Raigarh # 1 | 2013-11-14 | 10:36 | 2013-11-14 | 19:08 | [9 empty] | 8:32 | 8 | 32 | LCSD | Line outage availled for construction works at Jarsuguda. | WR-11/1121, NL-11/137, EL-11/334 | WR-11/1173, NL-11/147, EL-11/349
52 | 711046 | 400 | Padhge -Tarapur # 2 | 2013-11-14 | 12:24 | 2013-11-14 | 18:37 | [9 empty] | 0.25903 | 6 | 13 | OSPD | OCC approved outage availed by MSETCL for quarterly maintenance work at Padghe end | 11/1134 | 11/1168
53 | 711047 | 400 | Kolhapur - Mapusa # 2 | 2013-11-14 | 16:14 | 2013-11-15 | 11:08 | [9 empty] | 0.7875 | 18 | 54 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1152 | 11/1238
54 | 711048 | 400 | Jharsuguda-Raigarh # 2 | 2013-11-15 | 8:32 | 2013-11-16 | 20:14 | [9 empty] | 1899-12-31 11:42 | 35 | 42 | LCSD | Outage availed by ER-2 for construction/stringing activity of upcoming line. | WR-11/1217 ,NL-11/150, EL-11/355 | WR-11/1396 ER-11/409 NL- 11/
55 | 711049 | 765/400 | ICT-3:1500MVA: BILASPUR | 2013-11-15 | 11:45 | 2013-11-15 | 14:40 | [9 empty] | 2:55 | 2 | 55 | SCSD | ICT outage availed for construction warranty test. | 11/1240, NL-11/158 | 11/1247, NL-11/159
56 | 711050 | 400 | Kolhapur - Mapusa # 1 | 2013-11-15 | 16:16 | 2013-11-16 | 8:17 | [9 empty] | 0.66736 | 16 | 1 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1256 | 11/1321
57 | 711051 | 765 | Seoni-Wardha # 2 | 2013-11-15 | 20:58 | 2013-11-15 | 21:08 | [6 empty] | 0.0069444 | 0 | 10 |  |  |  | GOVC | Line tripped due to Over voltage at wardha
58 | 711052 | 765 | Seoni-Wardha # 2 | 2013-11-15 | 21:08 | 2013-11-16 | 6:48 | [9 empty] | 0.40278 | 9 | 40 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/1289 | 11/1309, NL-11/164
59 | 711053 | 765/400 | ICT-3:1500MVA: BILASPUR | 2013-11-16 | 11:08 | 2013-11-16 | 14:26 | [9 empty] | 3:18 | 3 | 18 | SCSD | ICT outage availed for construction warranty test. | 11/1343 | 11/1356
60 | 711054 | 400 | Kolhapur - Mapusa # 2 | 2013-11-16 | 16:40 | 2013-11-17 | 9:47 | [9 empty] | 0.71319 | 17 | 7 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1378 | 11/1442
61 | 711055 | 400 | KWPCL-Raipur | 2013-11-16 | 9:32 | 2013-11-17 | 19:36 | [9 empty] | 1899-12-31 10:04 | 34 | 4 | SCSD | Line outage availed by KWPCL for line construction work | 11/1327 | 11/1480
62 | 711056 | 400 | KWPCL- Raigarh | 2013-11-16 | 9:33 | 2013-11-17 | 19:36 | [9 empty] | 1899-12-31 10:03 | 34 | 3 | SCSD | Line outage availed by KWPCL for line construction work | 11/1328 | 11/1481
63 | 711057 | 400 | Kolhapur - Mapusa # 1 | 2013-11-17 | 16:15 | 2013-11-18 | 9:32 | [9 empty] | 0.72014 | 17 | 17 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1462 | 11/1530
64 | 711058 | 400 | Kolhapur - Mapusa # 2 | 2013-11-18 | 16:32 | 2013-11-18 | 22:33 | [9 empty] | 0.25069 | 6 | 1 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1663 | 11/1690
65 | 711059 | 400 | Kolhapur - Mapusa # 1 | 2013-11-18 | 22:36 | 2013-11-19 | 9:28 | [9 empty] | 0.45278 | 10 | 52 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1690 | 11/1723
66 | 711060 | 400 | Kolhapur - Mapusa # 1 | 2013-11-19 | 17:10 | 2013-11-20 | 8:57 | [9 empty] | 0.65764 | 15 | 47 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1769 | 11/1812
67 | 711061 | 400 | Bus Reactor / Kolhapur (80) | 2013-11-19 | 8:15 | 2013-11-19 | 17:34 | [9 empty] | 0.38819 | 9 | 19 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1724 | 11/1772
68 | 711062 | 400 | Bus Reactor / Kolhapur (80) | 2013-11-20 | 8:54 | 2013-11-20 | 18:18 | [9 empty] | 0.39167 | 9 | 24 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1838 | 11/1885
69 | 711063 | 400 | Bus Reactor / Pune (50) | 2013-11-20 | 10:42 | 2013-11-20 | 17:20 | [9 empty] | 0.27639 | 6 | 38 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1838 | 11/1880
70 | 711064 | 400 | Bus Reactor / Mapusa (50) | 2013-11-20 | 10:37 | 2013-11-20 | 16:20 | [9 empty] | 0.23819 | 5 | 43 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1839 | 11/1873
71 | 711065 | 400 | Bus Reactor / Parli (63) | 2013-11-20 | 11:06 | 2013-11-20 | 17:06 | [9 empty] | 0.25 | 6 | 0 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1843 | 11/1881
72 | 711066 | 400 | Bus Reactor / Solapur (63) | 2013-11-20 | 11:16 | 2013-11-20 | 17:05 | [9 empty] | 0.24236 | 5 | 49 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1844 | 11/1879
73 | 711067 | 400 | Kolhapur - Mapusa # 1 | 2013-11-20 | 14:52 | 2013-11-20 | 16:40 | [9 empty] | 0.075 | 1 | 48 | OSFD | Emergency outage for replacing spring of Bph isolator at Kolhapur (MSETCL) end. | 11/1864 | 11/1878
74 | 711068 | 400 | Kolhapur - Mapusa # 1 | 2013-11-20 | 16:40 | 2013-11-21 | 9:27 | [9 empty] | 0.69931 | 16 | 47 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 11/1878 | 11/1940
75 | 711069 | 400 | Bus Reactor / Kolhapur (80) | 2013-11-21 | 9:16 | 2013-11-27 | 20:06 | [9 empty] | 1900-01-05 10:50 | 154 | 50 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/1939 | 11/2602
76 | 711070 | 400 | Kolhapur - Mapusa # 1 | 2013-11-21 | 16:20 | 2013-11-22 | 11:36 | [9 empty] | 0.80278 | 19 | 16 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/1985 | 11/2081
77 | 711071 | 765 | Seoni-Wardha # 2 | 2013-11-21 | 16:53 | 2013-11-30 | 24:00 | [9 empty] | 1900-01-08 07:07 | 223 | 7 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | WR-11/1988, NL-11/227
78 | 711072 | 400 | Bus Reactor / Solapur (63) | 2013-11-22 | 9:23 | 2013-11-22 | 16:38 | [9 empty] | 0.30208 | 7 | 15 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/2057 | 11/2108
79 | 711073 | HVDC | POLE # 2 : BHADRAWATI | 2013-11-22 | 15:26 | 2013-11-22 | 15:39 | 0:13 | 0 | 13 | [9 empty] | OMST | Pole tripped due to Pole control system Watch dog alarm. |  | WR-11/2100, NL-11/235, SR-11/699
80 | 711074 | 400 | Kolhapur - Mapusa # 1 | 2013-11-22 | 16:03 | 2013-11-23 | 10:45 | [9 empty] | 0.77917 | 18 | 42 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2104 | 11/2198
81 | 711075 | 400 | Kolhapur - Mapusa # 2 | 2013-11-23 | 16:39 | 2013-11-24 | 9:08 | [9 empty] | 0.68681 | 16 | 29 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2233 | 11/2292
82 | 711076 | 400 | Bus Reactor / Solapur (63) | 2013-11-24 | 9:41 | 2013-11-24 | 16:24 | [9 empty] | 0.27986 | 6 | 43 | SVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2297 | 11/2330
83 | 711077 | 400 | Kolhapur - Mapusa # 2 | 2013-11-24 | 4:21 | 2013-11-25 | 10:23 | [9 empty] | 1899-12-31 06:02 | 30 | 2 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2329 | 11/2373
84 | 711078 | 400 | Ranchi- Sipat # 1 | 2013-11-24 | 13:30 | 2013-11-24 | 15:30 | 2:00 | 2 | 0 | [9 empty] | OSPT | Line outage availed line rectification work. | WR-'11/2316 Er- 11/673 NL :- 11/245
85 | 711079 | 400 | Ranchi- Sipat # 1 | 2013-11-24 | 15:30 | 2013-11-24 | 18:27 |  |  |  | 0.12292 | 2 | 57 | [6 empty] | OMSU | Delay in charging due to problem at NTPC Sipat end. |  | WR-11/2326 Er- 11/675 NL: 11/246
86 | 711080 | 400 | Bhilai -Korba # 2 | 2013-11-25 | 8:15 | 2013-11-25 | 19:57 | [9 empty] | 0.4875 | 11 | 42 | LCSD | OCC approved outage availed for line crossing works of D/C 765 KV Raipur - Champa. | 11/2360 | 11/2413
87 | 711081 | 400 | Jharsuguda-Raigarh # 2 | 2013-11-25 | 13:04 | 2013-11-30 | 24:00 | [9 empty] | 1900-01-04 10:56 | 130 | 46 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | WR-11/2385, NL-11/255, ER-11/708 | --
88 | 711082 | 400 | Kolhapur - Mapusa # 2 | 2013-11-25 | 16:02 | 2013-11-26 | 09:27 | [9 empty] | 0.72569 | 17 | 25 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2397 | 11/2447
89 | 711083 | 765 | Bus Reactor / Wardha (3 X 80 MVAR) | 2013-11-25 | 16:31 | 2013-11-25 | 18:22 | 1:51 | 1 | 51 | [9 empty] | OSPT | Outage availed for maintenance of bay Isolator at Wardha. | WR- 11/2376 , NLDC-11/255 | WR-11/2404 NL-11/256
90 | 711084 | 400 | Kolhapur - Mapusa # 2 | 2013-11-26 | 17:03 | 2013-11-27 | 8:59 | [9 empty] | 0.66389 | 15 | 56 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2482
91 | 711085 | 400 | Kolhapur - Mapusa # 2 | 2013-11-27 | 16:38 | 2013-11-28 | 09:01 | [9 empty] | 0.68264 | 16 | 23 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2581 | 11/2628
92 | 711086 | 400 | Bus Reactor / Kolhapur (80) | 2013-11-27 | 9:25 | 2013-11-30 | 24:00 | [9 empty] | 1900-01-02 14:35 | 86 | 35 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/2548
93 | 711087 | 400 | Bus Reactor / Solapur (63) | 2013-11-28 | 11:24 | 2013-11-28 | 16:22 | [9 empty] | 0.20694 | 4 | 58 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/2643 | 11/2673
94 | 711088 | 400 | Bus Reactor / Parli (63) | 2013-11-28 | 11:41 | 2013-11-28 | 18:06 | [9 empty] | 0.26736 | 6 | 25 | SVRD | B/R H/T as per WRLDC instructions for Voltage regulation | 11/2645 | 11/2678
95 | 711089 | 400 | Kolhapur - Mapusa # 2 | 2013-11-28 | 16:16 | 2013-11-29 | 09:43 | [9 empty] | 0.72708 | 17 | 27 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2672 | 11/2738
96 | 711090 | 400 | Bhatapara-Bhilai | 2013-11-29 | 08:46 | 2013-11-30 | 24:00 | [6 empty] | 1899-12-31 15:14 | 39 | 14 |  |  |  | LNCC | Outage availed for restoration of line work from ERS to normal (Permament) towers which was collapsed due to heavy wind & thunder in Jun-13. | 11/2729
97 | 711091 | 400 | Kolhapur - Mapusa # 1 | 2013-11-29 | 16:21 | 2013-11-30 | 11:32 | [9 empty] | 0.79931 | 19 | 11 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2775 | 11/2843
98 | 711092 | 400 | Kolhapur - Mapusa # 2 | 2013-11-30 | 15:50 | 2013-11-30 | 24:00 | [9 empty] | 0.34028 | 8 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 11/2863
GRAND TOTAL HRS:MIN= | [8 empty] | 13 | 152 |  | 2 | 67 |  | 67 | 115 |  | 3323 | 2404
GRAND TOTAL HRS= | [8 empty] | 15.5333 |  |  | 3.1167 |  |  | 68.9167 |  |  | 3363.0667
|  | Voltage | Elements Name
|  | 765 | Akola-Aurangabad # 1
|  | 400 | Akola-Aurangabad # 2
|  | 220 | Akola-Wardha # 1
|  | 132 | Akola-Wardha # 2
|  | 765/400 | Balco-Birsinghpur
|  | 400/220 | Balco-Korba
|  | HVDC | Bhadrawati - Chandrapur # 1
Bhadrawati - Chandrapur # 2
Bhadrawati - Chandrapur # 3
Bhadrawati - Chandrapur # 4
Bhadrawati -Raipur # 1
Bhadrawati-Parli # 1
Bhadrawati-Parli # 2
Bhadrawati-Raipur # 2
Bhadrawati-Raipur # 3
Bhatapara -Korba
Bhatapara-Bhilai
Bhilai - Raipur # 1
Bhilai - Seoni
Bhilai -Bhadrawati
Bhilai -Korba # 1
Bhilai -Korba # 2
Bhilai-Koradi
Bilaspur-Seoni # 1
Bilaspur-Seoni # 2
Bilaspur-Sipat # 1
Bilaspur-Sipat # 2
Birsinghpur -Vandana
Boisar - Padhge
Boisar-Tarapur
Boisar-Tarapur # 1
Boisar-Tarapur # 2
Boisar-Vapi
Budhipadar- Korba (E)
DB Power-KSK
DB Power-Raigarh
IEPL -Mouda
IEPL-Wardha
Jharsuguda-Raigarh # 1
Jharsuguda-Rourkela # 1
Jharsuguda-Raigarh # 2
Jharsuguda-Rourkela # 2
Kolhapur - Mapusa # 1
Kolhapur - Mapusa # 2
Koradi - Satpura
Korba - Korba (W)
Korba-Mahan ( Essar)
Korba-Pathadi
Korba-Raipur # 3
Korba-Raipur # 4
Korba-Vandana
Korba-Vindhyachal # 2
KSK - Raigarh
KSK-Raipur
KWPCL- Raigarh
KWPCL-Raipur
Mahan ( Essar)-Vindhyachal
Mouda-Wardha # 2
Padhge -Tarapur # 1
Padhge -Tarapur # 2
Parli (PGCIL)-Parli(MSETCL) # 1
Parli (PGCIL)-Parli(MSETCL) # 2
Parli-Wardha # 1
Parli-Wardha # 2
Pathadi-Sipat
Raigarh - Rourkela # 1
Raigarh - SEL # 1
Raigarh - SEL # 2
Raigarh-Raipur # 4
Raigarh-Raipur # 1
Raipur-Sipat # 1
Raipur-Sipat # 2
Raipur-Sipat # 3
Raipur-Wardha # 1
Raipur-Wardha # 2
Ranchi- Sipat # 1
Ranchi- Sipat # 2
Satpura - Seoni
SEL-Rourkela-SEL # 1
SEL-Rourkela-SEL # 2
Seoni-Wardha # 1
Seoni-Wardha # 2
ICT-1:315MVA : RAIPUR
ICT-2:315MVA : RAIPUR
ICT-3:315MVA : RAIPUR
ICT-1:315MVA : MAPUSA
ICT-2:315MVA : MAPUSA
ICT-1:315MVA :BOISAR
ICT-2:315MVA :BOISAR
ICT-1:315MVA :BHATAPARA
ICT-2:315MVA :BHATAPARA
ICT-1:315MVA :RAIGARH
ICT-2:315MVA :RAIGARH
ICT-1:1500MVA: SEONI
ICT-2:1500MVA: SEONI
ICT-3:1500MVA: SEONI
ICT-1:315MVA: SEONI
ICT-2:315MVA: SEONI
ICT-1:315MVA: WARDHA
ICT-2:315MVA: WARDHA
ICT-3:315MVA: WARDHA
ICT-1:1500MVA: WARDHA
ICT-2:1500MVA: WARDHA
ICT-3:1500MVA: WARDHA
ICT-1:315MVA:SOLAPUR
ICT-2:315MVA:SOLAPUR
ICT-1:315MVA:PUNE
ICT-2:315MVA:PUNE
ICT-3:315MVA:PUNE
ICT-1:1500MVA: BILASPUR
ICT-2:1500MVA: BILASPUR
ICT-3:1500MVA: BILASPUR
POLE # 1 : BHADRAWATI
POLE # 2 : BHADRAWATI
Bus Reactor / Bhadrawati (50)
Bus Reactor / Raipur (80)
Bus Reactor / Mapusa (50)
Bus Reactor / Kolhapur (80)
Bus Reactor / Raigarh (63)
Bus Reactor / Seoni (3 X 80 MVAR)
Bus Reactor /(SLR) in Raipur-Sipat # 3 at Raipur
Bus Reactor / Wardha (50)
Bus Reactor / Solapur (63)
Bus Reactor / Parli (63)
Bus Reactor / Pune (50)
Bus Reactor / Wardha (3 X 80 MVAR)
Bus Reactor / Bilaspur (3 X 80 MVAR)
Bus Reactor / Bilaspur (3 X 80 MVAR): Ranchi-1
Formulas:
Attributed to sys conts. = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Outage deemed available = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to PGCIL = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to Other = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]

## ANX-II
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
| NIL |  | NIL
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
Sl. No. | Type of failures | Restoration Time (Days) |  |  | Remarks
A | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 | Insualtor Failure | Terrain Type
|  | Plain | River bed | Hilly
i | Insualtor Failure in single phase
ii | Insualtor Failure in two phases
ii | Insualtor Failure in three phases
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 | Tower Damage ( not collapse)
i | One arm damage
ii | Two arm damage
5 | Snapping of phase conductor
i | Conductor snapping in single phase
ii | Conductor snapping in two phases
iii | Conductor snapping in three phases
6 | Failure of Earth wire
7 | Insulator failure with conductor snapping | 0.50542 |  |  | 400kv Akola-Wardha # 1 on 13.11.13.
8 | Any other combination of failures
B | Elements of sub-station for each KV class seperately
1 | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
| Other major failures in ICTs | Single phase Unit |  | Three phase Unit
(i) Replacement of faulty bushings
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 | Failures of Reactors
Restoration of failed Reactors