## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-I) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-I) Transmission System in Western Region for the month of OCT- 2013 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 220kV Tarapur - Boisar | 100 | 34 | 400 KV D/C Raipur-Sipat # 2 | 100
2 | 400kV Korba-Korba (W) | 100 | 35 | 400 kV S/C Raipur-Sipat # 3 | 99.5811
3 | 400kV Korba-Bhilai # 1 | 100 | 36 | 765 KV S/C Sipat - Bilaspur # 1 | 100
4 | 400kV Korba-Bhilai # 2 | 100 | 37 | 765 KV S/C Bilaspur - Seoni # 1 | 100
5 | 400kV Bhilai-Koradi | 99.9888 | 38 | 765 KV S/C Sipat - Bilaspur # 2 | 100
6 | 400kV Koradi-Satpura | 100 | 39 | 765 KV S/C Bilaspur - Seoni # 2 | 100
7 | 400kV Bhilai - Raipur # 1 | 100 | 40 | 765 KV S/C Seoni-Wardha # 1 | 99.9149
8 | 400 KV Bhilai - Bhadrawati | 99.4347 | 41 | 765 KV S/C Seoni-Wardha # 2 | 100
9 | 400 kV Raipur - Bhadrawati # 1 | 99.9776 | 42 | 400 KV D/C Wardha-Akola # 1 | 100
10 | 400kV Raipur - Bhadrawati # 2 | 100 | 43 | 400 KV D/C Wardha-Akola # 2 | 100
11 | 400kV Raipur - Bhadrawati # 3 | 100 | 44 | 400 KV D/C Akola-Aurangabad # 1 | 100
12 | 400kV B'vati-Chandrapur # 1 | 100 | 45 | 400 KV D/C Akola-Aurangabad # 2 | 100
13 | 400kV B'vati-Chandrapur # 2 | 100 | 46 | 400KV Bhadrawati-Parli # 1 | 99.5452
14 | 400kV B'vati-Chandrapur # 3 | 100 | 47 | 400KV Bhadrawati-Parli # 2 | 100
15 | 400kV B'vati-Chandrapur # 4 | 100 | 48 | 400KV Parli-Parli # 1 | 100
16 | 400kV Kolhapur - Mapusa # 1 | 100 | 49 | 400KV Parli-Parli # 2 | 100
17 | 400kV Kolhapur - Mapusa # 2 | 100 | 50 | 400KV Korba-Raipur-3 | 100
18 | 400kV Tarapur - Padghe # 1 | 100 | 51 | 400KV Korba-Raipur-4 | 100
19 | 400kV Tarapur - Padghe # 2 | 100 | 52 | 400KV Wardha-Parli # 1 | 100
20 | 400 KV BOISAR - Padge | 100 | 53 | 400KV Wardha-Parli # 2 | 100
21 | 400kV Tarapur - Boisar #1 | 100 | 54 | 400KV Korba-Balco (lilo of Korba-Biringsinghpur # 2) | 100
22 | 400kV Tarapur - Boisar #2 | 100 | 55 | 400KV Balco-Birsinghpur (lilo of Korba-Biringsinghpur # 2) | 100
23 | 400 KV Vapi - Boisar | 100 | 56 | 400KV Mouda-Wardha # 2 | 100
24 | 400kV Vindhyachal - Mahan ( Essar) | 100 | 57 | 400KV Korba-Vandana (lilo of Korba-Birsinghpur # 1) | 100
25 | 400kV Mahan ( Essar) - Korba | 100 | 58 | 400KV Vandana-Bhirshingpur- (lilo of Korba-Birsinghpur # 1) | 100
26 | 400 kV Vindyanchal-Korba #2 | 100 | 59 | 400KV Raipur-Wardha # 1 | 100
27 | 400 KV Satpura - Seoni (LILO portion) | 100 | 60 | 400KV Raipur-Wardha # 2 | 100
28 | 400 KV Seoni - Bhilai (LILO portion) | 100 | 61 | 400KV Wardha-IEPL (Lilo of Mouda- Wardha # 1 ) | 100
29 | 400KV Bhilai- Bhatapara | 100 | 62 | 400KV IEPL -Mouda (Lilo of Mouda- Wardha # 1 ) | 100
30 | 400KV Korba - Bhatapara | 99.4456 | 63 | D/C Raipur-Raipur (pooling/Durg) # 1 | 100
31 | 400kV Korba - Pathadi | 100 | 64 | D/C Raipur-Raipur (pooling/Durg) # 2 | 100
32 | 400kV Pathadi - Sipat | 100 | 65 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 1 | 100
33 | 400 KV D/C Raipur-Sipat # 1 | 100 | 66 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 2 | 100
67 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 2 | 100 | 103 | 400/220kV ICT # 2 / Bhatapara | 100
68 | 400KV Raipur - Raigarh # 1 | 100 | 104 | 400/220kV ICT # 2 / Seoni | 100
69 | D/C Raipur-KWPCL (lilo of Raipur - Raigarh # 2 ) | 100 | 105 | 400/220kV ICT # 3 / Raipur | 100
70 | D/C KWPCL- Raigarh (lilo of Raipur - Raigarh # 2 ) | 100 | 106 | 400/220kV ICT # 1 / Wardha | 100
71 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] | 100 | 107 | 400/220kV ICT # 2 / Wardha | 100
72 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] | 100 | 108 | 400/220kV ICT # 3 / Wardha | 100
73 | 400KV Raigarh - Jharsuguda # 1 (lilo of Raigarh - Rourkela#1) | 100 | 109 | 400/220kV ICT # 1 / Solapur | 100
74 | 400KV Jharsuguda- Rourkela # 1 (lilo of Raigarh - Rourkela#1) | 100 | 110 | 400/220kV ICT # 2 / Solpaur | 100
75 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] | 100 | 111 | 400/220kV ICT # 1 / Pune | 100
76 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] | 100 | 112 | 400/220kV ICT # 2 / Pune | 100
77 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] | 100 | 113 | 400/220kV ICT # 3 / Pune | 100
78 | 400KV Raipur - Raigarh # 4 | 100 | 114 | 765/400kV AT # 3 / Bilaspur | 100
79 | 400KV Raigarh - Jharsuguda # 2 ( lilo of Raigarh-Rourkela # 3) | 100 | 115 | 765/400kV AT # 1 / Raigarh PS (Kotra) | 100
80 | 400KV Jharsuguda-Rourkela # 2 ( lilo of Raigarh-Rourkela # 3) | 100 | 116 | 765/400kV AT # 2 / Raigarh PS (Kotra) | 100
81 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] | 100 | 117 | Bus reactor / B'vati | 100
82 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] | 100 | 118 | Bus Reactor / Raipur | 100
83 | 400KV D/C Sipat-Ranchi # 1 | 100 | 119 | Bus Reactor / Mapusa | 100
84 | 400KV D/C Sipat-Ranchi # 2 | 100 | 120 | Bus Reactor / Kolhapur | 100
85 | 220KV Korba-Bhudhipadar # 3 | 100 | 121 | Bus Reactor / Raigarh | 100
85 | 400/220kV ICT # 1 / Raipur | 100 | 122 | Bus Reactor / Seoni (3 x 80) | 100
86 | 400/220kV ICT # 2 / Raipur | 100 | 123 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur | 100
87 | 400/220kV ICT # 1 / Mapusa | 100 | 124 | Bus Reactor / Wardha | 100
88 | 400/220kV ICT # 2 / Mapusa | 100 | 125 | Bus Reactor / Solapur | 100
89 | 400/220kV ICT # 1 / Boisar | 100 | 126 | Bus Reactor / Parli | 100
90 | 400/220kV ICT # 2 / Boisar | 100 | 127 | Bus Reactor / Pune | 100
91 | 400/220kV ICT # 1 / Bhatapara | 100 | 128 | 765KV Bus Reactor / Wardha(3x80) | 100
92 | 400/220kV ICT # 1 / Raigarh | 100 | 129 | 765KV Bus Reactor / Bilaspur(3x80) | 100
93 | 400/220kV ICT # 2 / Raigarh | 100 | 130 | 765KV Bina line Switchable Line Reactor at Seoni (3x80) | 100
94 | 765/400kV AT # 1 / Seoni | 100 | 131 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80) | 100
95 | 765/400kV AT # 2 / Seoni | 100 | 132 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80) | 100
96 | 765/400kV AT # 3 / Seoni | 100 | 133 | 765KV Ranchi # 1 Switchable line Reactor charged as Bus Reactor at Bilaspur | 100
97 | 400/220kV ICT # 1 / Seoni | 100 | 134 | 765KV Bus Reactor at Kotra PS | 100
98 | 765/220kV AT # 1 / Wardha | 100 | 135 | 400KV Bus Reactor /Kotra PS | 100
99 | 765/220kV AT # 2 / Wardha | 100 | 136 | 765KV Raipur # 1 Switchable Line Reactor charged as Bus Reactor at Kotra PS | 100
100 | 765/220kV AT # 3 / Wardha | 100 | 137 | 500 MW HVDC Bhadrawati Pole # 1 | 100
101 | 765/220kV AT # 1 / Bilaspur | 100 | 138 | 500 MW HVDC Bhadrawati Pole # 2 | 100
102 | 765/220kV AT # 2 / Bilaspur | 100
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
66
85
Availability Bus Reactors =
System Availability :-

## wrpc Aval
AVAILABILITY OF AC SYSTEM : OCT-2013
OUTAGE DATA FOR POWERGRID TRANSMISSION SYSTEM
|  | 2013-10-16 |  |  |  | Total Outage | Total Outage |  | Line length |  |  |  |  | Individual line Availability
[6 empty] | Hrs | Hrs | Individual |  | NSC1 | OH1* | Cktkm1 * NSC1 | THM
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | PGCIL | OTHERS | THM | Ckrkm1 |  | NSC1*CktKm1 |  | *Cktkm1 * NSC1
No. |  | Hrs | Mints | Hrs | Mints | OH1 | OH2
[6 empty] | Hrs | Hrs
WRTS-I
1 | 220kV Tarapur - Boisar |  |  |  |  | 0 | 0 | 744 | 20.56 | 1 | 0 | 20.56 | 15296.64 | 100
2 | 400kV Korba-Korba (W) |  |  |  |  | 0 | 0 | 744 | 14 | 2 | 0 | 28 | 20832 | 100
3 | 400kV Korba-Bhilai # 1 |  |  | 0 | 15 | 0 | 0.25 | 743.75 | 197 | 2 | 0 | 394 | 293037.5 | 100
4 | 400kV Korba-Bhilai # 2 |  |  |  |  | 0 | 0 | 744 | 192 | 2 | 0 | 384 | 285696 | 100
5 | 400kV Bhilai-Koradi | 0 | 5 |  |  | 0.083333 | 0 | 744 | 272 | 2 | 45.3333 | 544 | 404736 | 99.9888
6 | 400kV Koradi-Satpura |  |  |  |  | 0 | 0 | 744 | 149 | 2 | 0 | 298 | 221712 | 100
7 | 400kV Bhilai - Raipur # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 100
8 | 400 KV Bhilai - Bhadrawati | 3 | 72 | 1 | 0 | 4.2 | 1 | 743 | 322 | 2 | 2704.8 | 644 | 478492 | 99.4347
9 | 400 kV Raipur - Bhadrawati # 1 | 0 | 10 | 0 | 38 | 0.16667 | 0.63333 | 743.3667 | 333 | 2 | 111 | 666 | 495082.2 | 99.9776
10 | 400kV Raipur - Bhadrawati # 2 |  |  |  |  | 0 | 0 | 744 | 345.55 | 2 | 0 | 691.1 | 514178.4 | 100
11 | 400kV Raipur - Bhadrawati # 3 |  |  |  |  | 0 | 0 | 744 | 345.55 | 2 | 0 | 691.1 | 514178.4 | 100
12 | 400kV B'vati-Chandrapur # 1 |  |  | 2 | 29 | 0 | 2.4833 | 741.5167 | 20 | 2 | 0 | 40 | 29660.6667 | 100
13 | 400kV B'vati-Chandrapur # 2 |  |  | 3 | 7 | 0 | 3.1167 | 740.8833 | 20 | 2 | 0 | 40 | 29635.3333 | 100
14 | 400kV B'vati-Chandrapur # 3 |  |  |  |  | 0 | 0 | 744 | 22.42 | 2 | 0 | 44.84 | 33360.96 | 100
15 | 400kV B'vati-Chandrapur # 4 |  |  |  |  | 0 | 0 | 744 | 22.42 | 2 | 0 | 44.84 | 33360.96 | 100
16 | 400kV Kolhapur - Mapusa # 1 |  |  |  |  | 0 | 0 | 744 | 150 | 2 | 0 | 300 | 223200 | 100
17 | 400kV Kolhapur - Mapusa # 2 |  |  |  |  | 0 | 0 | 744 | 150 | 2 | 0 | 300 | 223200 | 100
18 | 400kV Tarapur - Padghe # 1 |  |  | 0 | 5 | 0 | 0.083333 | 743.9167 | 91.119 | 2 | 0 | 182.238 | 135569.8855 | 100
19 | 400kV Tarapur - Padghe # 2 |  |  |  |  | 0 | 0 | 744 | 91.119 | 2 | 0 | 182.238 | 135585.072 | 100
20 | 400 KV BOISAR - Padge |  |  |  |  | 0 | 0 | 744 | 101 | 2 | 0 | 202 | 150288 | 100
21 | 400kV Tarapur - Boisar #1 |  |  |  |  | 0 | 0 | 744 | 20.881 | 2 | 0 | 41.762 | 31070.928 | 100
22 | 400kV Tarapur - Boisar #2 |  |  | 0 | 27 | 0 | 0.45 | 743.55 | 20.881 | 2 | 0 | 41.762 | 31052.1351 | 100
23 | 400 KV Vapi - Boisar |  |  |  |  | 0 | 0 | 744 | 91 | 2 | 0 | 182 | 135408 | 100
24 | 400kV Vindhyachal - Mahan ( Essar) |  |  |  |  | 0 | 0 | 744 | 19 | 2 | 0 | 38 | 28272 | 100
25 | 400kV Mahan ( Essar) - Korba |  |  |  |  | 0 | 0 | 744 | 196 | 2 | 0 | 392 | 291648 | 100
26 | 400 kV Vindyanchal-Korba #2 |  |  |  |  | 0 | 0 | 744 | 288.994 | 2 | 0 | 577.988 | 430023.072 | 100
27 | 400 KV Satpura - Seoni (LILO portion) |  |  |  |  | 0 | 0 | 744 | 1.507 | 2 | 0 | 3.014 | 2242.416 | 100
28 | 400 KV Seoni - Bhilai (LILO portion) |  |  |  |  | 0 | 0 | 744 | 1.498 | 2 | 0 | 2.996 | 2229.024 | 100
29 | 400KV Bhilai- Bhatapara |  |  |  |  | 0 | 0 | 744 | 90.453 | 2 | 0 | 180.906 | 134594.064 | 100
30 | 400KV Korba - Bhatapara | 3 | 61 | 19 | 32 | 4.0167 | 19.5333 | 724.4667 | 123.73 | 2 | 993.9643 | 247.46 | 179276.5213 | 99.4456
31 | 400kV Korba - Pathadi |  |  |  |  | 0 | 0 | 744 | 39.536 | 2 | 0 | 79.072 | 58829.568 | 100
32 | 400kV Pathadi - Sipat |  |  |  |  | 0 | 0 | 744 | 29.117 | 2 | 0 | 58.234 | 43326.096 | 100
33 | 400 KV D/C Raipur-Sipat # 1 |  |  |  |  | 0 | 0 | 744 | 149.12 | 2 | 0 | 298.24 | 221890.56 | 100
34 | 400 KV D/C Raipur-Sipat # 2 |  |  |  |  | 0 | 0 | 744 | 149.12 | 2 | 0 | 298.24 | 221890.56 | 100
35 | 400 kV S/C Raipur-Sipat # 3 | 3 | 7 |  |  | 3.1167 | 0 | 744 | 162.04 | 2 | 1010.0493 | 324.08 | 241115.52 | 99.5811
36 | 765 KV S/C Sipat - Bilaspur # 1 |  |  |  |  | 0 | 0 | 744 | 21.507 | 4 | 0 | 86.028 | 64004.832 | 100
37 | 765 KV S/C Bilaspur - Seoni # 1 |  |  |  |  | 0 | 0 | 744 | 337.046 | 4 | 0 | 1348.184 | 1003048.896 | 100
38 | 765 KV S/C Sipat - Bilaspur # 2 |  |  |  |  | 0 | 0 | 744 | 22.216 | 4 | 0 | 88.864 | 66114.816 | 100
39 | 765 KV S/C Bilaspur - Seoni # 2 |  |  |  |  | 0 | 0 | 744 | 338.33 | 4 | 0 | 1353.32 | 1006870.08 | 100
40 | 765 KV S/C Seoni-Wardha # 1 | 0 | 38 |  |  | 0.63333 | 0 | 744 | 267.894 | 4 | 678.6648 | 1071.576 | 797252.544 | 99.9149
41 | 765 KV S/C Seoni-Wardha # 2 |  |  |  |  | 0 | 0 | 744 | 260.763 | 4 | 0 | 1043.052 | 776030.688 | 100
42 | 400 KV D/C Wardha-Akola # 1 |  |  |  |  | 0 | 0 | 744 | 161.865 | 2 | 0 | 323.73 | 240855.12 | 100
43 | 400 KV D/C Wardha-Akola # 2 |  |  |  |  | 0 | 0 | 744 | 161.865 | 2 | 0 | 323.73 | 240855.12 | 100
44 | 400 KV D/C Akola-Aurangabad # 1 |  |  |  |  | 0 | 0 | 744 | 241.23 | 2 | 0 | 482.46 | 358950.24 | 100
45 | 400 KV D/C Akola-Aurangabad # 2 |  |  |  |  | 0 | 0 | 744 | 241.23 | 2 | 0 | 482.46 | 358950.24 | 100
46 | 400KV Bhadrawati-Parli # 1 | 3 | 23 | 0 | 5 | 3.3833 | 0.083333 | 743.9167 | 378.667 | 2 | 2562.3134 | 757.334 | 563393.3848 | 99.5452
47 | 400KV Bhadrawati-Parli # 2 |  |  |  |  | 0 | 0 | 744 | 378.667 | 2 | 0 | 757.334 | 563456.496 | 100
48 | 400KV Parli-Parli # 1 |  |  |  |  | 0 | 0 | 744 | 4.958 | 2 | 0 | 9.916 | 7377.504 | 100
49 | 400KV Parli-Parli # 2 |  |  |  |  | 0 | 0 | 744 | 4.958 | 2 | 0 | 9.916 | 7377.504 | 100
50 | 400KV Korba-Raipur-3 |  |  |  |  | 0 | 0 | 744 | 212.83 | 2 | 0 | 425.66 | 316691.04 | 100
51 | 400KV Korba-Raipur-4 |  |  |  |  | 0 | 0 | 744 | 212.83 | 2 | 0 | 425.66 | 316691.04 | 100
52 | 400KV Wardha-Parli # 1 |  |  |  |  | 0 | 0 | 744 | 336.939 | 4 | 0 | 1347.756 | 1002730.464 | 100
53 | 400KV Wardha-Parli # 2 |  |  |  |  | 0 | 0 | 744 | 336.939 | 4 | 0 | 1347.756 | 1002730.464 | 100
54 | 400KV Korba-Balco (lilo of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 744 | 7.454 | 2 | 0 | 14.908 | 11091.552 | 100
55 | 400KV Balco-Birsinghpur (lilo of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 744 | 219.188 | 2 | 0 | 438.376 | 326151.744 | 100
56 | 400KV Mouda-Wardha # 2 |  |  |  |  | 0 | 0 | 744 | 123.45 | 4 | 0 | 493.8 | 367387.2 | 100
57 | 400KV Korba-Vandana (lilo of Korba-Birsinghpur # 1) |  |  |  |  | 0 | 0 | 744 | 14.768 | 2 | 0 | 29.536 | 21974.784 | 100
58 | 400KV Vandana-Bhirshingpur- (lilo of Korba-Birsinghpur # 1) |  |  |  |  | 0 | 0 | 744 | 211.874 | 2 | 0 | 423.748 | 315268.512 | 100
59 | 400KV Raipur-Wardha # 1 |  |  |  |  | 0 | 0 | 744 | 370.565 | 4 | 0 | 1482.26 | 1102801.44 | 100
60 | 400KV Raipur-Wardha # 2 |  |  |  |  | 0 | 0 | 744 | 370.565 | 4 | 0 | 1482.26 | 1102801.44 | 100
61 | 400KV Wardha-IEPL (Lilo of Mouda- Wardha # 1 ) |  |  |  |  | 0 | 0 | 744 | 52.62 | 4 | 0 | 210.48 | 156597.12 | 100
62 | 400KV IEPL -Mouda (Lilo of Mouda- Wardha # 1 ) |  |  |  |  | 0 | 0 | 744 | 70.83 | 4 | 0 | 283.32 | 210790.08 | 100
63 | D/C Raipur-Raipur (pooling/Durg) # 1 |  |  |  |  | 0 | 0 | 744 | 21.43 | 2 | 0 | 42.86 | 31887.84 | 100
64 | D/C Raipur-Raipur (pooling/Durg) # 2 |  |  |  |  | 0 | 0 | 744 | 21.43 | 2 | 0 | 42.86 | 31887.84 | 100
65 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 1 |  |  |  |  | 0 | 0 | 744 | 6.288 | 2 | 0 | 12.576 | 9356.544 | 100
66 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 2 |  |  |  |  | 0 | 0 | 744 | 6.288 | 2 | 0 | 12.576 | 9356.544 | 100
67 | 400KV Raipur - Raigarh # 1 |  |  |  |  | 0 | 0 | 744 | 217.02 | 2 | 0 | 434.04 | 322925.76 | 100
68 | D/C Raipur-KWPCL (lilo of Raipur - Raigarh # 2 ) |  |  |  |  | 0 | 0 | 744 | 208.29 | 2 | 0 | 416.58 | 309935.52 | 100
69 | D/C KWPCL- Raigarh (lilo of Raipur - Raigarh # 2 ) |  |  |  |  | 0 | 0 | 744 | 8.73 | 2 | 0 | 17.46 | 12990.24 | 100
70 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 744 | 99.46 | 2 | 0 | 198.92 | 147996.48 | 100
71 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 744 | 113 | 2 | 0 | 226 | 168144 | 100
72 | 400KV Raigarh - Jharsuguda # 1 (lilo of Raigarh - Rourkela#1) |  |  |  |  | 0 | 0 | 744 | 114.46 | 2 | 0 | 228.92 | 170316.48 | 100 | 100
73 | 400KV Jharsuguda- Rourkela # 1 (lilo of Raigarh - Rourkela#1) |  |  |  |  | 0 | 0 | 744 | 142.448 | 2 | 0 | 284.896 | 211962.624 | 100 | 100
74 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] |  |  |  |  | 0 | 0 | 744 | 134.74 | 2 | 0 | 269.48 | 200493.12 | 100
75 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] |  |  | 1 | 38 | 0 | 1.6333 | 742.3667 | 85.01 | 2 | 0 | 170.02 | 126217.1807 | 100
76 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] |  |  | 1 | 26 | 0 | 1.4333 | 742.5667 | 1.129 | 2 | 0 | 2.258 | 1676.7155 | 100
77 | 400KV Raipur - Raigarh # 4 |  |  |  |  | 0 | 0 | 744 | 220.884 | 2 | 0 | 441.768 | 328675.392 | 100 | 100
78 | 400KV Raigarh - Jharsuguda # 2 ( lilo of Raigarh-Rourkela # 3) |  |  |  |  | 0 | 0 | 744 | 110.98 | 2 | 0 | 221.96 | 165138.24 | 100 | 100
79 | 400KV Jharsuguda-Rourkela # 2 ( lilo of Raigarh-Rourkela # 3) |  |  |  |  | 0 | 0 | 744 | 143.06 | 2 | 0 | 286.12 | 212873.28 | 100
80 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] |  |  | 0 | 42 | 0 | 0.7 | 743.3 | 105 | 2 | 0 | 210 | 156093 | 100
81 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] |  |  |  |  | 0 | 0 | 744 | 104.28 | 2 | 0 | 208.56 | 155168.64 | 100
82 | 400KV D/C Sipat-Ranchi # 1 |  |  |  |  | 0 | 0 | 744 | 405.772 | 2 | 0 | 811.544 | 603788.736 | 100
83 | 400KV D/C Sipat-Ranchi # 2 |  |  |  |  | 0 | 0 | 744 | 405.772 | 2 | 0 | 811.544 | 603788.736 | 100
84 | 220KV Korba-Bhudhipadar # 3 |  |  | 0 | 15 | 0 | 0.25 | 743.75 | 184 | 1 | 0 | 184 | 136850 | 100
85 | 400/220kV ICT # 1 / Raipur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
86 | 400/220kV ICT # 2 / Raipur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
87 | 400/220kV ICT # 1 / Mapusa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
88 | 400/220kV ICT # 2 / Mapusa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
89 | 400/220kV ICT # 1 / Boisar |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
90 | 400/220kV ICT # 2 / Boisar |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
91 | 400/220kV ICT # 1 / Bhatapara |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
92 | 400/220kV ICT # 1 / Raigarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
93 | 400/220kV ICT # 2 / Raigarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
94 | 765/400kV AT # 1 / Seoni |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
95 | 765/400kV AT # 2 / Seoni |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
96 | 765/400kV AT # 3 / Seoni |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
97 | 400/220kV ICT # 1 / Seoni |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
98 | 765/220kV AT # 1 / Wardha |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
99 | 765/220kV AT # 2 / Wardha |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
100 | 765/220kV AT # 3 / Wardha |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
101 | 765/220kV AT # 1 / Bilaspur |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
102 | 765/220kV AT # 2 / Bilaspur |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
103 | 400/220kV ICT # 2 / Bhatapara |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
104 | 400/220kV ICT # 2 / Seoni |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
105 | 400/220kV ICT # 3 / Raipur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
106 | 400/220kV ICT # 1 / Wardha |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
107 | 400/220kV ICT # 2 / Wardha |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
108 | 400/220kV ICT # 3 / Wardha |  |  |  |  | 0 | 0 | 744 | 500 | 2.5 | 0 | 1250 | 930000 | 100
109 | 400/220kV ICT # 1 / Solapur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
110 | 400/220kV ICT # 2 / Solpaur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
111 | 400/220kV ICT # 1 / Pune |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
112 | 400/220kV ICT # 2 / Pune |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
113 | 400/220kV ICT # 3 / Pune |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
114 | 765/400kV AT # 3 / Bilaspur |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
115 | 765/400kV AT # 1 / Raigarh PS (Kotra) |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
116 | 765/400kV AT # 2 / Raigarh PS (Kotra) |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 100
117 | Bus reactor / B'vati |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
118 | Bus Reactor / Raipur |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 100
119 | Bus Reactor / Mapusa |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
120 | Bus Reactor / Kolhapur |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 100
121 | Bus Reactor / Raigarh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
122 | Bus Reactor / Seoni (3 x 80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
123 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
124 | Bus Reactor / Wardha |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
125 | Bus Reactor / Solapur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
126 | Bus Reactor / Parli |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
127 | Bus Reactor / Pune |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
128 | 765KV Bus Reactor / Wardha(3x80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
129 | 765KV Bus Reactor / Bilaspur(3x80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
130 | 765KV Bina line Switchable Line Reactor at Seoni (3x80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
131 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
132 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80) |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
133 | 765KV Ranchi # 1 Switchable line Reactor charged as Bus Reactor at Bilaspur |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
134 | 765KV Bus Reactor at Kotra PS |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
135 | 400KV Bus Reactor /Kotra PS |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 100
136 | 765KV Raipur # 1 Switchable Line Reactor charged as Bus Reactor at Kotra PS |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
137 | 500 MW HVDC B'vati Pole # 1 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 250 | 0 | 250 | 185941.6667 |  | 100%
138 | 500 MW HVDC B'vati Pole # 2 |  |  | 0 | 15 | 0 | 0.25 | 743.75 | 250 | 0 | 250 | 185937.5 |  | 100%

## Tripping
POWERGRID CORPORATION OF INDIA LIMITED
LINE TRIPPING DETAILS OF WRTS - 1 FOR OCTOBER-2013
TOTAL NUMBER OF ELEMENTS : 138
SN | Event No. | Voltage KV | Element Name | Tripping Date | Tripping Time | Resto-ration Date | Resto-ration Time | Attributed to PGCIL | Attributed to PGCIL |  | Attributed to Other | Attributed to Other |  | Attributed to sys conts. | Attributed to sys conts. |  | Outage deemed available | Outage deemed available |  | Cat. Code | Actual Detail Reason of Tripping | Tripping Code | Charging Code
[9 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN
1 | 709021 | 765 | Seoni-Wardha # 2 | 2013-09-10 | 13:03 | 2013-10-21 | 9:42 | [9 empty] | 489:42 | 489 | 42 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-'10/1404, NL-10/229
2 | 709047 | 400 | Bhadrawati-Parli # 2 | 2013-09-22 | 12:27 | 2013-10-05 | 10:56 | [9 empty] | 106:56 | 106 | 56 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 09/1636 | 09/332
3 | 709076 | 400 | Kolhapur - Mapusa # 1 | 2013-09-28 | 18:01 | 2013-10-01 | 9:05 | [9 empty] | 9:05 | 9 | 5 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 09/2194 | 10/16
4 | 709078 | 400 | Akola-Wardha # 1 | 2013-09-30 | 23:53 | 2013-10-01 | 6:38 | [9 empty] | 6:38 | 6 | 38 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 09/2333 | 10/05
5 | 701001 | 400 | Akola-Aurangabad # 1 | 2013-10-01 | 0:46 | 2013-10-01 | 6:10 | [9 empty] | 0.225 | 5 | 24 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/01 | 10/06
6 | 701002 | 400 | Korba - Korba (W) | 2013-10-01 | 10:29 | 2013-10-01 | 17:55 | [9 empty] | 0.30972 | 7 | 26 | OSPD | Outage availed by CSPTCL for maintenance work. | 10/29 | 10/56
7 | 701005 | 400 | Kolhapur - Mapusa # 1 | 2013-10-01 | 17:09 | 2013-10-03 | 9:35 | [9 empty] | 1899-12-31 16:26 | 40 | 26 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/50 | 10/159
8 | 701006 | 400 | Raipur-Sipat # 3 | 2013-10-02 | 11:19 | 2013-10-02 | 19:08 | [9 empty] | 0.32569 | 7 | 49 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/100 | 10/110
9 | 701007 | 400 | Raigarh-Raipur # 4 | 2013-10-02 | 11:35 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-28 12:25 | 708 | 25 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/103
10 | 701008 | 400 | Ranchi- Sipat # 2 | 2013-10-02 | 12:25 | 2013-10-02 | 13:55 | [9 empty] | 0.0625 | 1 | 30 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/105 | 10/110
11 | 701009 | 400 | Bhilai -Bhadrawati | 2013-10-03 | 10:44 | 2013-10-03 | 11:03 | 0:19 | 0 | 19 | [9 empty] | OSPT | Line H/T for isolating Line reactor for AMP works at Bhadrawati end. | 10/164 | 10/168
12 | 701010 | 400 | Bhatapara -Korba | 2013-10-03 | 12:58 | 2013-10-03 | 13:28 | 0:30 | 0 | 30 | [9 empty] | LEFT | Line tripped due to Yph- e fault F.L=103km from Bhatapara,F/L=13km from Korba. Insualtor string falshover at Loc. No.41, heavy raifall & lightning at site. | - | -
13 | 701011 | 400 | Bhatapara -Korba | 2013-10-03 | 13:28 | 2013-10-04 | 9:00 | [6 empty] | 19:32 | 19 | 32 |  |  |  | LNCC | Line rectification works affected due to heavy rainfall & lightning till 04/10/13-09:00 hrs. Affected site condition was not approachable due to continuous raining. | - | -
14 | 701012 | 400 | Bhatapara -Korba | 2013-10-04 | 9:00 | 2013-10-04 | 12:26 | 3:26 | 3 | 26 | [9 empty] | OSPT | Outage availed for line rectification work after stoppage of rain. | - | 10/238
15 | 701013 | 400 | Boisar-Tarapur # 1 | 2013-10-03 | 13:53 | 2013-10-03 | 21:35 | [9 empty] | 0.32083 | 7 | 42 | OSPD | Line outage availed by NPCIL for Jumper tightening works at NPCIL S/S end. | 10/176 | 10/197
16 | 701014 | 400 | Kolhapur - Mapusa # 1 | 2013-10-03 | 21:48 | 2013-10-04 | 9:26 | [9 empty] | 0.48472 | 11 | 38 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/204 | 10/225
17 | 701016 | 400 | Bhadrawati -Raipur # 1 | 2013-10-04 | 13:04 | 2013-10-04 | 13:14 | 0:10 | 0 | 10 | [9 empty] | OSPT | Line H/T for isolating line reactor for AMP works | 10/241
18 | 701017 | 400 | Bhadrawati -Raipur # 1 | 2013-10-04 | 13:14 | 2013-10-04 | 13:52 |  |  |  | 0.026389 | 0 | 38 | [6 empty] | OMSU | Line charging delayed due to delay in code received of code. | - | 10/246
19 | 701018 | 400 | Kolhapur - Mapusa # 2 | 2013-10-04 | 16:49 | 2013-10-08 | 10:26 | [9 empty] | 1900-01-02 17:37 | 89 | 37 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/262 | 10/538
20 | 701019 | 400 | Raigarh - SEL # 2 | 2013-10-05 | 13:06 | 2013-10-05 | 18:22 | [9 empty] | 0.21944 | 5 | 16 | OSPD | Line H/T to availed outage availed by Sterlite | WR-'10/347, NLDC 10/61, ER- 10/118 | WR- 10/373, NLDC-10 /67, ER-10/127
21 | 701020 | 400 | Bhadrawati-Parli # 2 | 2013-10-06 | 0:07 | 2013-10-07 | 19:24 | [9 empty] | 1899-12-31 19:17 | 43 | 17 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/393 | 10/495
22 | 701021 | 400 | Bhatapara -Korba | 2013-10-08 | 0:03 | 2013-10-08 | 0:08 | 0:05 | 0 | 5 | [9 empty] | LEFT | Line tripped due to R ph - E fault, F/L=24Km from Korba.
23 | 701022 | 400 | Bhatapara -Korba | 2013-10-08 | 0:08 | 2013-10-09 | 7:10 | [9 empty] | 1899-12-31 07:02 | 31 | 2 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | 10/524
24 | 701023 | 400 | Korba-Vindhyachal # 2 | 2013-10-08 | 11:48 | 2013-10-10 | 10:25 | [9 empty] | 1899-12-31 22:37 | 46 | 37 | OSPD | Line H/T to availed outage by NTPC for maintenance works | 10/545 | 10/666
25 | 701024 | 400 | Kolhapur - Mapusa # 1 | 2013-10-08 | 16:43 | 2013-10-09 | 9:58 | [9 empty] | 0.71875 | 17 | 15 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/554 | 10/602
26 | 701025 | 400 | Kolhapur - Mapusa # 2 | 2013-10-09 | 18:17 | 2013-10-10 | 9:31 | [9 empty] | 0.63472 | 15 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/632 | 10/660
27 | 701026 | 400 | Kolhapur - Mapusa # 2 | 2013-10-10 | 16:37 | 2013-10-11 | 10:57 | [9 empty] | 0.76389 | 18 | 20 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/687 | 10/755
28 | 701027 | 400 | Bhadrawati - Chandrapur # 1 | 2013-10-11 | 1:40 | 2013-10-12 | 16:54 | [9 empty] | 1899-12-31 15:14 | 39 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/728 | 10/852
29 | 701028 | 400 | ICT-3:315MVA:PUNE | 2013-10-11 | 10:40 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-19 13:20 | 493 | 20 | SPRD | H/T as per WRLDC instructions for power regulation | 10/752
30 | 701029 | 400 | Kolhapur - Mapusa # 1 | 2013-10-11 | 16:38 | 2013-10-12 | 9:11 | [9 empty] | 0.68958 | 16 | 33 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/771 | 10/819
31 | 701030 | 400 | Bhadrawati-Parli # 1 | 2013-10-12 | 10:07 | 2013-10-12 | 13:30 | 3:23 | 3 | 23 | [9 empty] | OSPT | Outage availed to line maintenance works | 10/821 | -
32 | 701031 | 400 | Bhadrawati-Parli # 1 | 2013-10-12 | 13:30 | 2013-10-12 | 17:30 | [9 empty] | 4:00 | 4 | 0 | GOMD | Line could not be taken into service due to system high voltage. | - | 10/853
33 | 701032 | 400 | Kolhapur - Mapusa # 1 | 2013-10-12 | 16:44 | 2013-10-15 | 9:15 | [9 empty] | 1900-01-01 16:31 | 16 | 31 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/851 | 10/1043
34 | 701033 | 220 | Budhipadar- Korba (E) | 2013-10-12 | 17:35 | 2013-10-12 | 18:24 | [9 empty] | 0.034028 | 0 | 49 | LPRD | Line tripped due to over loading of line. |  | WR-10/863, ER-10/344, NL-10/135
35 | 701034 | 400 | Raigarh - SEL # 2 | 2013-10-13 | 4:19 | 2013-10-13 | 5:01 |  |  |  | 0.029167 | 0 | 42 | [6 empty] | OMSU | Line tripped due to Bph-E. fault in LILO portion of M/S SEL ltd. Fl= 18km from SEL, 101km from Raigarh |  | 10/898
36 | 701035 | 400 | DB Power-KSK | 2013-10-13 | 8:09 | 2013-10-13 | 9:47 |  |  |  | 0.068056 | 1 | 38 | [6 empty] | OMSU | Line tripped due to DT sent from DBPL end |  | 10/914
37 | 701036 | 400 | DB Power-Raigarh | 2013-10-13 | 8:09 | 2013-10-13 | 9:35 |  |  |  | 0.059722 | 1 | 26 | [6 empty] | OMSU | Line tripped due to DT sent from DBPL end |  | 10/916
38 | 701037 | 400 | Raigarh-Raipur # 1 | 2013-10-13 | 17:10 | 2013-10-30 | 10:38 | [9 empty] | 401:28 | 17 | 28 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/945 | 10/2121
39 | 701038 | 400 | Bhadrawati-Parli # 1 | 2013-10-13 | 17:26 | 2013-10-14 | 9:29 | [9 empty] | 0.66875 | 16 | 3 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/946 | 10/987
40 | 701039 | 400 | Boisar-Tarapur # 2 | 2013-10-14 | 1:53 | 2013-10-14 | 2:20 | [6 empty] | 0.01875 | 0 | 27 |  |  |  | GOVC | Line tripped due to O/V at Boisar end.
41 | 701040 | 400 | Padhge -Tarapur # 1 | 2013-10-14 | 2:05 | 2013-10-14 | 2:10 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to O/V at Boisar end.
42 | 701041 | 400 | Padhge -Tarapur # 1 | 2013-10-14 | 2:10 | 2013-10-14 | 7:23 | [9 empty] | 0.21736 | 5 | 13 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | 10/979
43 | 701042 | 400 | Jharsuguda-Raigarh # 1 | 2013-10-14 | 12:18 | 2013-10-14 | 19:20 | [9 empty] | 7:02 | 7 | 2 | LCSD | Outage availed by ER-II for Line constrction Works | WR-1001, NL-161, ER-339 | WR-1012, NL-162, ER-351
44 | 701043 | 400 | Kolhapur - Mapusa # 2 | 2013-10-15 | 17:40 | 2013-10-16 | 9:27 | [9 empty] | 0.65764 | 15 | 47 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1072 | 10/1098
45 | 701044 | 400 | Kolhapur - Mapusa # 1 | 2013-10-16 | 21:39 | 2013-10-17 | 9:27 | [9 empty] | 0.49167 | 11 | 48 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1135 | 10/1154
46 | 701046 | 400 | Kolhapur - Mapusa # 2 | 2013-10-17 | 20:38 | 2013-10-18 | 9:48 | [9 empty] | 0.54861 | 13 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1186 | 10/1216
47 | 701047 | 400 | Bhadrawati-Parli # 1 | 2013-10-18 | 0:25 | 2013-10-18 | 0:30 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to O/V at Parli end. | -- | --
48 | 701048 | 400 | Bhadrawati-Parli # 1 | 2013-10-18 | 0:30 | 2013-10-19 | 11:05 | [9 empty] | 1899-12-31 10:35 | 34 | 35 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 10/1198 | 10/1287
49 | 701049 | 400 | Kolhapur - Mapusa # 1 | 2013-10-18 | 16:30 | 2013-10-19 | 9:39 | [9 empty] | 0.71458 | 17 | 9 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1244 | 10/1283
50 | 701050 | 400 | Raigarh - SEL # 2 | 2013-10-19 | 9:50 | 2013-10-19 | 16:02 | [9 empty] | 0.25833 | 6 | 12 | OSPD | Outage availed by SEL for maintenance work | WR-10/1284, NL-204 , ER- 10/461 | WR-10/1305, NL-10/205, ER-10/470
51 | 701052 | 400 | Korba - Korba (W) | 2013-10-19 | 11:51 | 2013-10-19 | 20:22 | [9 empty] | 0.35486 | 8 | 31 | OSPD | Line H/T for CT Replacement work at Korba (W) | 10/1295 | 10/1325
52 | 701053 | 400 | Bhilai-Koradi | 2013-10-19 | 12:21 | 2013-10-19 | 19:21 | [9 empty] | 7:00 | 7 | 0 | OSFD | Outage availed by MSETCL for replacing hanging IPS tube between Line CT and Line reactor at Koradi end. | 10/1296 | 10/1319
53 | 701054 | 400 | Kolhapur - Mapusa # 2 | 2013-10-19 | 16:46 | 2013-10-19 | 19:11 | [9 empty] | 0.10069 | 2 | 25 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1310 | 10/1322
54 | 701055 | 400 | Kolhapur - Mapusa # 2 | 2013-10-19 | 21:50 | 2013-10-20 | 8:04 | [9 empty] | 0.42639 | 10 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1326 | 10/1339
55 | 701056 | 400 | DB Power-KSK | 2013-10-20 | 9:35 | 2013-10-20 | 18:50 | [9 empty] | 0.38542 | 9 | 15 | OSFD | Emergency outage availed by DBPL to attend hotspot at DBPL end. | 10/1342 | 10/1361
56 | 701057 | 400 | DB Power-Raigarh | 2013-10-20 | 9:45 | 2013-10-20 | 18:44 | [9 empty] | 0.37431 | 8 | 59 | OSFD | Emergency outage availed by DBPL to attend hotspot at DBPL end. | 10/1343 | 10/1362
57 | 701058 | 400 | Vandana-Birsinghpur | 2013-10-20 | 15:38 | 2013-10-21 | 3:14 | [9 empty] | 0.48333 | 11 | 36 | OSPD | Line outage availed by Birsinghpur (MPPTCL) for attending broken SF6 gas pipe in MPPTCL switchyard damged by monkeys at Birsinghpur end. | 10/1354 | 10/1386
58 | 701059 | 400 | Kolhapur - Mapusa # 1 | 2013-10-20 | 17:06 | 2013-10-21 | 9:46 | [9 empty] | 0.69444 | 16 | 40 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1359 | 10/1406
59 | 701060 | 400 | Bhadrawati-Parli # 1 | 2013-10-20 | 23:26 | 2013-10-21 | 7:30 | [9 empty] | 0.33611 | 8 | 4 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1380 | 10/1393
60 | 701063 | 400 | Kolhapur - Mapusa # 2 | 2013-10-21 | 16:35 | 2013-10-22 | 19:32 | [9 empty] | 1899-12-31 02:57 | 26 | 57 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1427 | 10/1480
61 | 701064 | 765 | Seoni-Wardha # 1 | 2013-10-21 | 17:57 | 2013-10-30 | 14:54 | [9 empty] | 1900-01-07 20:57 | 212 | 57 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1430, NL-10/238 | 10/2156
62 |  | 765 | Seoni-Wardha # 1 | 2013-10-30 | 14:54 | 2013-10-30 | 15:32 | 0.026389 | 0 | 38 | [9 empty] | OMST | Line charging delay due to adjustment of PLCC AGC at Seoni end. | - | 10/2156
63 | 701065 | 400 | Boisar-Tarapur # 1 | 2013-10-22 | 8:19 | 2013-10-22 | 19:34 | [9 empty] | 0.46875 | 11 | 15 | OSPD | Outage availed by NPCIL for maintenance works | 10/1472 | 10/1533
64 | 701066 | 220 | Budhipadar- Korba (E) | 2013-10-22 | 10:03 | 2013-10-22 | 10:18 |  |  |  | 0.010417 | 0 | 15 | [6 empty] | SBBU | Line tripped due to Bus fault at Korba (east) end | - | -
65 | 701067 | 220 | Budhipadar- Korba (E) | 2013-10-22 | 10:18 | 2013-10-22 | 22:18 | [9 empty] | 0.5 | 12 | 0 | OSFD | Outage continue by CSEB after bus fault at Korba (east) end |  | 10/1543, ER-10/5353, NL-10/253
66 | 701069 | 400 | Kolhapur - Mapusa # 2 | 2013-10-22 | 21:28 | 2013-10-23 | 9:48 | [9 empty] | 0.51389 | 12 | 20 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1539 | 25477
67 | 701070 | 400 | Boisar-Tarapur # 1 | 2013-10-23 | 8:49 | 2013-10-23 | 19:56 | [9 empty] | 0.46319 | 11 | 7 | OSPD | OCC Outage availed by NPCIL for maintenance works | 10/1560 | 10/1621
68 | 701071 | 400 | Kolhapur - Mapusa # 2 | 2013-10-23 | 21:49 | 2013-10-24 | 10:24 | [9 empty] | 0.52431 | 12 | 35 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1632 | 10/1656
69 | 701072 | 400 | Kolhapur - Mapusa # 1 | 2013-10-24 | 21:58 | 2013-10-25 | 10:08 | [9 empty] | 0.50694 | 12 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1703 | 10/1728
70 | 701073 | 400 | Kolhapur - Mapusa # 1 | 2013-10-25 | 16:59 | 2013-10-26 | 10:53 | [9 empty] | 0.74583 | 17 | 54 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1752 | 10/1792
71 | 701074 | 400 | Kolhapur - Mapusa # 2 | 2013-10-25 | 17:32 | 2013-10-29 | 9:25 | [9 empty] | 1900-01-02 15:53 | 87 | 53 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1814
72 | 701075 | 400 | Bhilai -Bhadrawati | 2013-10-27 | 10:16 | 2013-10-27 | 14:09 | 3:53 | 3 | 53 | [9 empty] | OSPT | Line outage availed for line maintenance works. | 10/1860 | 10/1878
73 | 701076 | 400 | Bhilai -Bhadrawati | 2013-10-27 | 14:09 | 2013-10-27 | 15:09 |  |  |  | 1:00 | 1 | 0 | [6 empty] | OMSU | Line charging delayed due to delay at CSPTCL Bhilai end. | 10/1860 | 10/1878
74 | 701077 | 400 | Bhadrawati - Chandrapur # 1 | 2013-10-27 | 10:45 | 2013-10-27 | 13:14 |  |  |  | 0.10347 | 2 | 29 | [6 empty] | SBBU | Line tripped due to bus-bar protection operation at MSECTL Chandrapur. | - | 10/1868
75 | 701078 | 400 | Bhadrawati - Chandrapur # 2 | 2013-10-27 | 10:45 | 2013-10-27 | 13:52 |  |  |  | 0.12986 | 3 | 7 | [6 empty] | SBBU | Line tripped due to bus-bar protection operation at MSECTL Chandrapur. | - | 10/1874
76 | 701079 | 400 | Jharsuguda-Raigarh # 2 | 2013-10-28 | 2:50 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-02 21:10 | 93 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation
77 | 701080 | 400 | Bhilai -Korba # 1 | 2013-10-29 | 12:03 | 2013-10-29 | 12:18 |  |  |  | 0.010417 | 0 | 15 | [6 empty] | SBBU | Line tripped due to Busbar protection operated at Korba end. | -- | --
78 | 701081 | 400 | Bhilai -Korba # 1 | 2013-10-29 | 12:18 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-01 11:42 | 59 | 42 | GOMD | Line kept uncharged due to outage taken by NTPC for maintenance works | 10/2047 | --
79 | 701082 | 400 | Bhadrawati-Parli # 1 | 2013-10-29 | 17:31 | 2013-10-29 | 18:46 | [9 empty] | 0.052083 | 1 | 15 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/2053 | 10/2060
80 | 701083 | 400 | Bhilai-Koradi | 2013-10-30 | 3:21 | 2013-10-30 | 3:26 | 0:05 | 0 | 5 | [9 empty] | LEFT | Line A/R successful at Bhilai end but tripped at Koradi end on Y ph- E fault. F/L=40.24Km from Bhilai end. | -- | --
81 | 701084 | 400 | Bhilai-Koradi | 2013-10-30 | 3:26 | 2013-10-30 | 3:57 | [9 empty] | 0.021528 | 0 | 31 | LVRD | Line kept uncharged as per WRLDC instruction for voltage regulation | -- | 10/2090
82 | 701085 | 400 | Kolhapur - Mapusa # 1 | 2013-10-30 | 21:28 | 2013-10-31 | 24:00 | [9 empty] | 1899-12-31 02:32 | 26 | 32 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/2187
83 | 701086 | 400 | Raipur-Sipat # 3 | 2013-10-31 | 15:43 | 2013-10-31 | 18:50 | 3:07 | 3 | 7 | [9 empty] | OSPT | Line outage availed for maintenance work at loc. No.310 | 10/2252 | 10/2266
1 | 701015 | 400/220 | ICT-2:315MVA:PUNE | 2013-10-04 | 12:14 | 2013-10-10 | 10:24 | [9 empty] | 1900-01-04 22:10 | 142 | 10 | SPRD | H/T as per WRLDC instructions for power regulation | 10/240 | 10/670
2 | 701061 | 400/220 | ICT-2:315MVA: SEONI | 2013-10-21 | 10:02 | 2013-10-21 | 14:55 | [9 empty] | 4:53 | 4 | 53 | SCSD | ICT outage availed for faciliating civil works below/adjacent of bays. | 10/1407 | 10/1421
3 | 701068 | 400/220 | ICT-1:315MVA: SEONI | 2013-10-22 | 10:31 | 2013-10-22 | 15:02 | [9 empty] | 4:31 | 4 | 31 | SCSD | ICT outage availed for faciliating civil works below/adjacent of bays. | 10/1486 | 10/1510
1 | 701045 | 400 | Bus Reactor / Mapusa (50) | 2013-10-17 | 15:17 | 2013-10-18 | 0:03 | [9 empty] | 0.36528 | 8 | 46 | SVRD | Bus reactor H/T as per WRLDC instructions for Voltage regulation | 10/1171 | 10/1196
2 | 701051 | 400 | Bus Reactor / Mapusa (50) | 2013-10-19 | 11:32 | 2013-10-19 | 16:30 | [9 empty] | 0.20694 | 4 | 58 | SVRD | B/R H/T as per WRLDC instruction for voltage regulation | 10/1294 | 10/1309
3 | 701062 | 400 | Bus Reactor / Pune (50) | 2013-10-21 | 11:59 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-09 12:01 | 252 | 1 | SVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1412
1 | 701003 | HVDC | POLE # 1 : BHADRAWATI | 2013-10-01 | 16:26 | 2013-10-01 | 16:40 |  |  |  | 0.0097222 | 0 | 14 | [6 empty] | OMSU | HVDC pole tripped due to failure of MSEDCL auxillary power supply |  | 10/47, SR/20,NL/9
2 | 701004 | HVDC | POLE # 2 : BHADRAWATI | 2013-10-01 | 16:26 | 2013-10-01 | 16:41 |  |  |  | 0.010417 | 0 | 15 | [6 empty] | OMSU | HVDC pole tripped due to failure of MSEDCL auxillary power supply |  | 10/47, SR/20,NL/9
GRAND TOTAL HRS:MIN= | [8 empty] | 12 | 216 | 0.47917 | 8 | 210 | 0.83958 | 19 | 69 | 120.2042 | 3039 | 1575
GRAND TOTAL HRS= | [8 empty] | 15.6 |  |  | 11.5 |  |  | 20.15 |  |  | 3065.25
31.65
|  | Voltage | Elements Name
|  | 765 | Akola-Aurangabad # 1
|  | 400 | Akola-Aurangabad # 2
|  | 220 | Akola-Wardha # 1
|  | 132 | Akola-Wardha # 2
|  | 765/400 | Balco-Birsinghpur
|  | 400/220 | Balco-Korba
|  | HVDC | Bhadrawati - Chandrapur # 1
Bhadrawati - Chandrapur # 2
Bhadrawati - Chandrapur # 3
Bhadrawati - Chandrapur # 4
Bhadrawati -Raipur # 1
Bhadrawati-Parli # 1
Bhadrawati-Parli # 2
Bhadrawati-Raipur # 2
Bhadrawati-Raipur # 3
Bhatapara -Korba
Bhatapara-Bhilai
Bhilai - Raipur # 1
Bhilai - Seoni
Bhilai -Bhadrawati
Bhilai -Korba # 1
Bhilai -Korba # 2
Bhilai-Koradi
Bilaspur-Seoni # 1
Bilaspur-Seoni # 2
Bilaspur-Sipat # 1
Bilaspur-Sipat # 2
balco
Boisar - Padhge
Boisar-Tarapur
Boisar-Tarapur # 1
Boisar-Tarapur # 2
Boisar-Vapi
Budhipadar- Korba (E)
DB Power-KSK
DB Power-Raigarh
IEPL -Mouda
IEPL-Wardha
Jharsuguda-Raigarh # 1
Jharsuguda-Rourkela # 1
Jharsuguda-Raigarh # 2
Jharsuguda-Rourkela # 2
Kolhapur - Mapusa # 1
Kolhapur - Mapusa # 2
Koradi - Satpura
Korba - Korba (W)
Korba-Mahan ( Essar)
Korba-Pathadi
Korba-Raipur # 3
Korba-Raipur # 4
Korba-Vandana
Korba-Vindhyachal # 2
KSK - Raigarh
KSK-Raipur
KWPCL- Raigarh
KWPCL-Raipur
Mahan ( Essar)-Vindhyachal
Mouda-Wardha # 2
Padhge -Tarapur # 1
Padhge -Tarapur # 2
Parli (PGCIL)-Parli(MSETCL) # 1
Parli (PGCIL)-Parli(MSETCL) # 2
Parli-Wardha # 1
Parli-Wardha # 2
Pathadi-Sipat
Raigarh - Rourkela # 1
Raigarh - SEL # 1
Raigarh - SEL # 2
Raigarh-Raipur # 4
Raigarh-Raipur # 1
Raipur-Sipat # 1
Raipur-Sipat # 2
Raipur-Sipat # 3
Raipur-Wardha # 1
Raipur-Wardha # 2
Ranchi- Sipat # 1
Ranchi- Sipat # 2
Satpura - Seoni
SEL-Rourkela-SEL # 1
SEL-Rourkela-SEL # 2
Seoni-Wardha # 1
Seoni-Wardha # 2
ICT-1:315MVA : RAIPUR
ICT-2:315MVA : RAIPUR
ICT-3:315MVA : RAIPUR
ICT-1:315MVA : MAPUSA
ICT-2:315MVA : MAPUSA
ICT-1:315MVA :BOISAR
ICT-2:315MVA :BOISAR
ICT-1:315MVA :BHATAPARA
ICT-2:315MVA :BHATAPARA
ICT-1:315MVA :RAIGARH
ICT-2:315MVA :RAIGARH
ICT-1:1500MVA: SEONI
ICT-2:1500MVA: SEONI
ICT-3:1500MVA: SEONI
ICT-1:315MVA: SEONI
ICT-2:315MVA: SEONI
ICT-1:315MVA: WARDHA
ICT-2:315MVA: WARDHA
ICT-3:315MVA: WARDHA
ICT-1:1500MVA: WARDHA
ICT-2:1500MVA: WARDHA
ICT-3:1500MVA: WARDHA
ICT-1:315MVA:SOLAPUR
ICT-2:315MVA:SOLAPUR
ICT-1:315MVA:PUNE
ICT-2:315MVA:PUNE
ICT-3:315MVA:PUNE
ICT-1:1500MVA: BILASPUR
ICT-2:1500MVA: BILASPUR
ICT-3:1500MVA: BILASPUR
POLE # 1 : BHADRAWATI
POLE # 2 : BHADRAWATI
Bus Reactor / Bhadrawati (50)
Bus Reactor / Raipur (80)
Bus Reactor / Mapusa (50)
Bus Reactor / Kolhapur (80)
Bus Reactor / Raigarh (63)
Bus Reactor / Seoni (3 X 80 MVAR)
Bus Reactor /(SLR) in Raipur-Sipat # 3 at Raipur
Bus Reactor / Wardha (50)
Bus Reactor / Solapur (63)
Bus Reactor / Parli (63)
Bus Reactor / Pune (50)
Bus Reactor / Wardha (3 X 80 MVAR)
Bus Reactor / Bilaspur (3 X 80 MVAR)
Bus Reactor / Bilaspur (3 X 80 MVAR): Ranchi-1
Formulas:
Outage deemed available = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to PGCIL = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to sys conts. = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to Other = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]

## ANX-II
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
| NIL |  | NIL
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
Sl. No. | Type of failures | Restoration Time (Days) |  |  | Remarks
A | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 | Insualtor Failure | Terrain Type
|  | Plain | River bed | Hilly
i | Insualtor Failure in single phase
ii | Insualtor Failure in two phases
ii | Insualtor Failure in three phases
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 | Tower Damage ( not collapse)
i | One arm damage
ii | Two arm damage
5 | Snapping of phase conductor
i | Conductor snapping in single phase
ii | Conductor snapping in two phases
iii | Conductor snapping in three phases
6 | Failure of Earth wire
7 | Insulator failure with conductor snapping | 0.9775 |  |  | 400kv Bhatapara -Korba on 03.10.13.
8 | Any other combination of failures
B | Elements of sub-station for each KV class seperately
1 | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
| Other major failures in ICTs | Single phase Unit |  | Three phase Unit
(i) Replacement of faulty bushings
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 | Failures of Reactors
Restoration of failed Reactors

## Elementwise
POWERGRID CORPORATION OF INDIA LIMITED
LINE TRIPPING DETAILS OF WRTS - 1 FOR OCTOBER-2013 | [26 empty] | 744
TOTAL NUMBER OF ELEMENTS : 138
SN | Voltage KV | Element Name | Tripping Date | Tripping Time | Resto-ration Date | Resto-ration Time | Attributed to PGCIL | Attributed to PGCIL |  | Attributed to Other | Attributed to Other |  | Attributed to sys conts. | Attributed to sys conts. |  | Outage deemed available | Outage deemed available |  | Cat. Code | Actual Detail Reason of Tripping | Tripping Code | Charging Code | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  |  |  |  | A | B | C | D=A*B*C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 | 400 | Akola-Aurangabad # 1 | 2013-10-01 | 0:46 | 2013-10-01 | 6:10 | [9 empty] | 0.225 | 5 | 24 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/01 | 10/06
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 5 | 24
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 5.4 |  |  |  |  | 241.23 | 2 | 0 | 0 | 744 | 482.46 | 358950.24 | 0 | 100%
2 | 400 | Akola-Wardha # 1 | 2013-09-30 | 23:53 | 2013-10-01 | 6:38 | [9 empty] | 6:38 | 6 | 38 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 09/2333 | 10/05
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 6 | 38
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.6333 |  |  |  |  | 161.865 | 2 | 0 | 0 | 744 | 323.73 | 240855.12 | 0 | 100%
3 | 400 | Bhadrawati - Chandrapur # 1 | 2013-10-11 | 1:40 | 2013-10-12 | 16:54 | [9 empty] | 1899-12-31 15:14 | 39 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/728 | 10/852
| 400 | Bhadrawati - Chandrapur # 1 | 2013-10-27 | 10:45 | 2013-10-27 | 13:14 |  |  |  | 0.10347 | 2 | 29 | [6 empty] | SBBU | Line tripped due to bus-bar protection operation at MSECTL Chandrapur. | - | 10/1868
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 2 | 29 |  | 0 | 0 |  | 39 | 14
|  | Element Availability= | [6 empty] | 0 |  |  | 2.4833 |  |  | 0 |  |  | 39.2333 |  |  |  |  | 20 | 2 | 0 | 0 | 741.5167 | 40 | 29660.6667 | 0 | 100%
4 | 400 | Bhadrawati - Chandrapur # 2 | 2013-10-27 | 10:45 | 2013-10-27 | 13:52 |  |  |  | 0.12986 | 3 | 7 | [6 empty] | SBBU | Line tripped due to bus-bar protection operation at MSECTL Chandrapur. | - | 10/1874
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 3 | 7 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 3.1167 |  |  | 0 |  |  | 0 |  |  |  |  | 20 | 2 | 0 | 0 | 740.8833 | 40 | 29635.3333 | 0 | 100%
5 | 400 | Bhadrawati -Raipur # 1 | 2013-10-04 | 13:04 | 2013-10-04 | 13:14 | 0:10 | 0 | 10 | [9 empty] | OSPT | Line H/T for isolating line reactor for AMP works | 10/241
| 400 | Bhadrawati -Raipur # 1 | 2013-10-04 | 13:14 | 2013-10-04 | 13:52 |  |  |  | 0.026389 | 0 | 38 | [6 empty] | OMSU | Line charging delayed due to delay in code received of code. | - | 10/246
|  | Sub-Total= | [5 empty] | 0 | 10 |  | 0 | 38 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0.16667 |  |  | 0.63333 |  |  | 0 |  |  | 0 |  |  |  |  | 333 | 2 | 0.16667 | 111 | 743.3667 | 666 | 495082.2 | 0.00022421 | 99.98%
6 | 400 | Bhadrawati-Parli # 1 | 2013-10-12 | 10:07 | 2013-10-12 | 13:30 | 3:23 | 3 | 23 | [9 empty] | OSPT | Outage availed to line maintenance works | 10/821 | -
| 400 | Bhadrawati-Parli # 1 | 2013-10-12 | 13:30 | 2013-10-12 | 17:30 | [9 empty] | 4:00 | 4 | 0 | GOMD | Line could not be taken into service due to system high voltage. | - | 10/853
| 400 | Bhadrawati-Parli # 1 | 2013-10-13 | 17:26 | 2013-10-14 | 9:29 | [9 empty] | 0.66875 | 16 | 3 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/946 | 10/987
| 400 | Bhadrawati-Parli # 1 | 2013-10-18 | 0:25 | 2013-10-18 | 0:30 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to O/V at Parli end. | -- | --
| 400 | Bhadrawati-Parli # 1 | 2013-10-18 | 0:30 | 2013-10-19 | 11:05 | [9 empty] | 1899-12-31 10:35 | 34 | 35 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 10/1198 | 10/1287
| 400 | Bhadrawati-Parli # 1 | 2013-10-20 | 23:26 | 2013-10-21 | 7:30 | [9 empty] | 0.33611 | 8 | 4 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1380 | 10/1393
| 400 | Bhadrawati-Parli # 1 | 2013-10-29 | 17:31 | 2013-10-29 | 18:46 | [9 empty] | 0.052083 | 1 | 15 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/2053 | 10/2060
|  | Sub-Total= | [5 empty] | 3 | 23 |  | 0 | 0 |  | 0 | 5 |  | 63 | 57
|  | Element Availability= | [6 empty] | 3.3833 |  |  | 0 |  |  | 0.083333 |  |  | 63.95 |  |  |  |  | 378.667 | 2 | 3.3833 | 2562.3134 | 743.9167 | 757.334 | 563393.3848 | 0.004548 | 99.55%
7 | 400 | Bhadrawati-Parli # 2 | 2013-09-22 | 12:27 | 2013-10-05 | 10:56 | [9 empty] | 106:56 | 106 | 56 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 09/1636 | 09/332
| 400 | Bhadrawati-Parli # 2 | 2013-10-06 | 0:07 | 2013-10-07 | 19:24 | [9 empty] | 1899-12-31 19:17 | 43 | 17 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/393 | 10/495
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 149 | 73
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 150.2167 |  |  |  |  | 378.667 | 2 | 0 | 0 | 744 | 757.334 | 563456.496 | 0 | 100%
8 | 400 | Bhatapara -Korba | 2013-10-03 | 12:58 | 2013-10-03 | 13:28 | 0:30 | 0 | 30 | [9 empty] | LEFT | Line tripped due to Yph- e fault F.L=103km from Bhatapara,F/L=13km from Korba. Insualtor string falshover at Loc. No.41, heavy raifall & lightning at site. | - | -
| 400 | Bhatapara -Korba | 2013-10-03 | 13:28 | 2013-10-04 | 9:00 | [6 empty] | 19:32 | 19 | 32 |  |  |  | LNCC | Line rectification works affected due to heavy rainfall & lightning till 04/10/13-09:00 hrs. Affected site condition was not approachable due to continuous raining. | - | -
| 400 | Bhatapara -Korba | 2013-10-04 | 9:00 | 2013-10-04 | 12:26 | 3:26 | 3 | 26 | [9 empty] | OSPT | Outage availed for line rectification work after stoppage of rain. | - | 10/238
| 400 | Bhatapara -Korba | 2013-10-08 | 0:03 | 2013-10-08 | 0:08 | 0:05 | 0 | 5 | [9 empty] | LEFT | Line tripped due to R ph - E fault, F/L=24Km from Korba.
| 400 | Bhatapara -Korba | 2013-10-08 | 0:08 | 2013-10-09 | 7:10 | [9 empty] | 1899-12-31 07:02 | 31 | 2 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | 10/524
|  | Sub-Total= | [5 empty] | 3 | 61 |  | 0 | 0 |  | 19 | 32 |  | 31 | 2
|  | Element Availability= | [6 empty] | 4.0167 |  |  | 0 |  |  | 19.5333 |  |  | 31.0333 |  |  |  |  | 123.73 | 2 | 4.0167 | 993.9643 | 724.4667 | 247.46 | 179276.5213 | 0.0055443 | 99.45%
9 | 400 | Bhilai -Bhadrawati | 2013-10-03 | 10:44 | 2013-10-03 | 11:03 | 0:19 | 0 | 19 | [9 empty] | OSPT | Line H/T for isolating Line reactor for AMP works at Bhadrawati end. | 10/164 | 10/168
| 400 | Bhilai -Bhadrawati | 2013-10-27 | 10:16 | 2013-10-27 | 14:09 | 3:53 | 3 | 53 | [9 empty] | OSPT | Line outage availed for line maintenance works. | 10/1860 | 10/1878
| 400 | Bhilai -Bhadrawati | 2013-10-27 | 14:09 | 2013-10-27 | 15:09 |  |  |  | 1:00 | 1 | 0 | [6 empty] | OMSU | Line charging delayed due to delay at CSPTCL Bhilai end. | 10/1860 | 10/1878
|  | Sub-Total= | [5 empty] | 3 | 72 |  | 1 | 0 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 4.2 |  |  | 1 |  |  | 0 |  |  | 0 |  |  |  |  | 322 | 2 | 4.2 | 2704.8 | 743 | 644 | 478492 | 0.0056528 | 99.43%
10 | 400 | Bhilai -Korba # 1 | 2013-10-29 | 12:03 | 2013-10-29 | 12:18 |  |  |  | 0.010417 | 0 | 15 | [6 empty] | SBBU | Line tripped due to Busbar protection operated at Korba end. | -- | --
| 400 | Bhilai -Korba # 1 | 2013-10-29 | 12:18 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-01 11:42 | 59 | 42 | GOMD | Line kept uncharged due to outage taken by NTPC for maintenance works | 10/2047 | --
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 15 |  | 0 | 0 |  | 59 | 42
|  | Element Availability= | [6 empty] | 0 |  |  | 0.25 |  |  | 0 |  |  | 59.7 |  |  |  |  | 197 | 2 | 0 | 0 | 743.75 | 394 | 293037.5 | 0 | 100%
11 | 400 | Bhilai-Koradi | 2013-10-19 | 12:21 | 2013-10-19 | 19:21 | [9 empty] | 7:00 | 7 | 0 | OSFD | Outage availed by MSETCL for replacing hanging IPS tube between Line CT and Line reactor at Koradi end. | 10/1296 | 10/1319
| 400 | Bhilai-Koradi | 2013-10-30 | 3:21 | 2013-10-30 | 3:26 | 0:05 | 0 | 5 | [9 empty] | LEFT | Line A/R successful at Bhilai end but tripped at Koradi end on Y ph- E fault. F/L=40.24Km from Bhilai end. | -- | --
| 400 | Bhilai-Koradi | 2013-10-30 | 3:26 | 2013-10-30 | 3:57 | [9 empty] | 0.021528 | 0 | 31 | LVRD | Line kept uncharged as per WRLDC instruction for voltage regulation | -- | 10/2090
|  | Sub-Total= | [5 empty] | 0 | 5 |  | 0 | 0 | 0 | 0 | 0 | 0.31319 | 7 | 31
|  | Element Availability= | [6 empty] | 0.083333 |  |  | 0 |  |  | 0 |  |  | 7.5167 |  |  |  |  | 272 | 2 | 0.083333 | 45.3333 | 744 | 544 | 404736 | 0.00011201 | 99.99%
12 | 400 | Boisar-Tarapur # 1 | 2013-10-03 | 13:53 | 2013-10-03 | 21:35 | [9 empty] | 0.32083 | 7 | 42 | OSPD | Line outage availed by NPCIL for Jumper tightening works at NPCIL S/S end. | 10/176 | 10/197
| 400 | Boisar-Tarapur # 1 | 2013-10-22 | 8:19 | 2013-10-22 | 19:34 | [9 empty] | 0.46875 | 11 | 15 | OSPD | Outage availed by NPCIL for maintenance works | 10/1472 | 10/1533
| 400 | Boisar-Tarapur # 1 | 2013-10-23 | 8:49 | 2013-10-23 | 19:56 | [9 empty] | 0.46319 | 11 | 7 | OSPD | OCC Outage availed by NPCIL for maintenance works | 10/1560 | 10/1621
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 29 | 64
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 30.0667 |  |  |  |  | 20.881 | 2 | 0 | 0 | 744 | 41.762 | 31070.928 | 0 | 100%
13 | 400 | Boisar-Tarapur # 2 | 2013-10-14 | 1:53 | 2013-10-14 | 2:20 | [6 empty] | 0.01875 | 0 | 27 |  |  |  | GOVC | Line tripped due to O/V at Boisar end.
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 27 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.45 |  |  | 0 |  |  |  |  | 20.881 | 2 | 0 | 0 | 743.55 | 41.762 | 31052.1351 | 0 | 100%
14 | 220 | Budhipadar- Korba (E) | 2013-10-12 | 17:35 | 2013-10-12 | 18:24 | [9 empty] | 0.034028 | 0 | 49 | LPRD | Line tripped due to over loading of line. |  | WR-10/863, ER-10/344, NL-10/135
| 220 | Budhipadar- Korba (E) | 2013-10-22 | 10:03 | 2013-10-22 | 10:18 |  |  |  | 0.010417 | 0 | 15 | [6 empty] | SBBU | Line tripped due to Bus fault at Korba (east) end | - | -
| 220 | Budhipadar- Korba (E) | 2013-10-22 | 10:18 | 2013-10-22 | 22:18 | [9 empty] | 0.5 | 12 | 0 | OSFD | Outage continue by CSEB after bus fault at Korba (east) end |  | 10/1543, ER-10/5353, NL-10/253
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 15 |  | 0 | 0 |  | 12 | 49
|  | Element Availability= | [6 empty] | 0 |  |  | 0.25 |  |  | 0 |  |  | 12.8167 |  |  |  |  | 184 | 1 | 0 | 0 | 743.75 | 184 | 136850 | 0 | 100%
15 | 400 | DB Power-KSK | 2013-10-13 | 8:09 | 2013-10-13 | 9:47 |  |  |  | 0.068056 | 1 | 38 | [6 empty] | OMSU | Line tripped due to DT sent from DBPL end |  | 10/914
| 400 | DB Power-KSK | 2013-10-20 | 9:35 | 2013-10-20 | 18:50 | [9 empty] | 0.38542 | 9 | 15 | OSFD | Emergency outage availed by DBPL to attend hotspot at DBPL end. | 10/1342 | 10/1361
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 1 | 38 |  | 0 | 0 |  | 9 | 15
|  | Element Availability= | [6 empty] | 0 |  |  | 1.6333 |  |  | 0 |  |  | 9.25 |  |  |  |  | 85.01 | 2 | 0 | 0 | 742.3667 | 170.02 | 126217.1807 | 0 | 100%
16 | 400 | DB Power-Raigarh | 2013-10-13 | 8:09 | 2013-10-13 | 9:35 |  |  |  | 0.059722 | 1 | 26 | [6 empty] | OMSU | Line tripped due to DT sent from DBPL end |  | 10/916
| 400 | DB Power-Raigarh | 2013-10-20 | 9:45 | 2013-10-20 | 18:44 | [9 empty] | 0.37431 | 8 | 59 | OSFD | Emergency outage availed by DBPL to attend hotspot at DBPL end. | 10/1343 | 10/1362
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 1 | 26 |  | 0 | 0 |  | 8 | 59
|  | Element Availability= | [6 empty] | 0 |  |  | 1.4333 |  |  | 0 |  |  | 8.9833 |  |  |  |  | 1.129 | 2 | 0 | 0 | 742.5667 | 2.258 | 1676.7155 | 0 | 100%
17 | 400 | Jharsuguda-Raigarh # 1 | 2013-10-14 | 12:18 | 2013-10-14 | 19:20 | [9 empty] | 7:02 | 7 | 2 | LCSD | Outage availed by ER-II for Line constrction Works | WR-1001, NL-161, ER-339 | WR-1012, NL-162, ER-351
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 7 | 2
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.0333 |  |  |  |  | 114.46 | 2 | 0 | 0 | 744 | 228.92 | 170316.48 | 0 | 100%
18 | 400 | Jharsuguda-Raigarh # 2 | 2013-10-28 | 2:50 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-02 21:10 | 93 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 93 | 10
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 93.1667 |  |  |  |  | 110.98 | 2 | 0 | 0 | 744 | 221.96 | 165138.24 | 0 | 100%
19 | 400 | Kolhapur - Mapusa # 1 | 2013-09-28 | 18:01 | 2013-10-01 | 9:05 | [9 empty] | 9:05 | 9 | 5 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 09/2194 | 10/16
| 400 | Kolhapur - Mapusa # 1 | 2013-10-01 | 17:09 | 2013-10-03 | 9:35 | [9 empty] | 1899-12-31 16:26 | 40 | 26 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/50 | 10/159
| 400 | Kolhapur - Mapusa # 1 | 2013-10-03 | 21:48 | 2013-10-04 | 9:26 | [9 empty] | 0.48472 | 11 | 38 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/204 | 10/225
| 400 | Kolhapur - Mapusa # 1 | 2013-10-08 | 16:43 | 2013-10-09 | 9:58 | [9 empty] | 0.71875 | 17 | 15 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/554 | 10/602
| 400 | Kolhapur - Mapusa # 1 | 2013-10-11 | 16:38 | 2013-10-12 | 9:11 | [9 empty] | 0.68958 | 16 | 33 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/771 | 10/819
| 400 | Kolhapur - Mapusa # 1 | 2013-10-12 | 16:44 | 2013-10-15 | 9:15 | [9 empty] | 1900-01-01 16:31 | 16 | 31 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/851 | 10/1043
| 400 | Kolhapur - Mapusa # 1 | 2013-10-16 | 21:39 | 2013-10-17 | 9:27 | [9 empty] | 0.49167 | 11 | 48 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1135 | 10/1154
| 400 | Kolhapur - Mapusa # 1 | 2013-10-18 | 16:30 | 2013-10-19 | 9:39 | [9 empty] | 0.71458 | 17 | 9 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1244 | 10/1283
| 400 | Kolhapur - Mapusa # 1 | 2013-10-20 | 17:06 | 2013-10-21 | 9:46 | [9 empty] | 0.69444 | 16 | 40 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1359 | 10/1406
| 400 | Kolhapur - Mapusa # 1 | 2013-10-24 | 21:58 | 2013-10-25 | 10:08 | [9 empty] | 0.50694 | 12 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1703 | 10/1728
| 400 | Kolhapur - Mapusa # 1 | 2013-10-25 | 16:59 | 2013-10-26 | 10:53 | [9 empty] | 0.74583 | 17 | 54 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1752 | 10/1792
| 400 | Kolhapur - Mapusa # 1 | 2013-10-30 | 21:28 | 2013-10-31 | 24:00 | [9 empty] | 1899-12-31 02:32 | 26 | 32 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/2187
|  | Sub-Total= | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 208 | 341
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 213.6833 |  |  |  |  | 150 | 2 | 0 | 0 | 744 | 300 | 223200 | 0 | 100%
20 | 400 | Kolhapur - Mapusa # 2 | 2013-10-04 | 16:49 | 2013-10-08 | 10:26 | [9 empty] | 1900-01-02 17:37 | 89 | 37 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/262 | 10/538
| 400 | Kolhapur - Mapusa # 2 | 2013-10-09 | 18:17 | 2013-10-10 | 9:31 | [9 empty] | 0.63472 | 15 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/632 | 10/660
| 400 | Kolhapur - Mapusa # 2 | 2013-10-10 | 16:37 | 2013-10-11 | 10:57 | [9 empty] | 0.76389 | 18 | 20 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/687 | 10/755
| 400 | Kolhapur - Mapusa # 2 | 2013-10-15 | 17:40 | 2013-10-16 | 9:27 | [9 empty] | 0.65764 | 15 | 47 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1072 | 10/1098
| 400 | Kolhapur - Mapusa # 2 | 2013-10-17 | 20:38 | 2013-10-18 | 9:48 | [9 empty] | 0.54861 | 13 | 10 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1186 | 10/1216
| 400 | Kolhapur - Mapusa # 2 | 2013-10-19 | 16:46 | 2013-10-19 | 19:11 | [9 empty] | 0.10069 | 2 | 25 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1310 | 10/1322
| 400 | Kolhapur - Mapusa # 2 | 2013-10-19 | 21:50 | 2013-10-20 | 8:04 | [9 empty] | 0.42639 | 10 | 14 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1326 | 10/1339
| 400 | Kolhapur - Mapusa # 2 | 2013-10-21 | 16:35 | 2013-10-22 | 19:32 | [9 empty] | 1899-12-31 02:57 | 26 | 57 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1427 | 10/1480
| 400 | Kolhapur - Mapusa # 2 | 2013-10-22 | 21:28 | 2013-10-23 | 9:48 | [9 empty] | 0.51389 | 12 | 20 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1539 | 25477
| 400 | Kolhapur - Mapusa # 2 | 2013-10-23 | 21:49 | 2013-10-24 | 10:24 | [9 empty] | 0.52431 | 12 | 35 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1632 | 10/1656
| 400 | Kolhapur - Mapusa # 2 | 2013-10-25 | 17:32 | 2013-10-29 | 9:25 | [9 empty] | 1900-01-02 15:53 | 87 | 53 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1814
|  | Sub-Total= | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 332
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 304.5333 |  |  |  |  | 150 | 2 | 0 | 0 | 744 | 300 | 223200 | 0 | 100%
21 | 400 | Korba - Korba (W) | 2013-10-01 | 10:29 | 2013-10-01 | 17:55 | [9 empty] | 0.30972 | 7 | 26 | OSPD | Outage availed by CSPTCL for maintenance work. | 10/29 | 10/56
| 400 | Korba - Korba (W) | 2013-10-19 | 11:51 | 2013-10-19 | 20:22 | [9 empty] | 0.35486 | 8 | 31 | OSPD | Line H/T for CT Replacement work at Korba (W) | 10/1295 | 10/1325
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 15 | 57
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 15.95 |  |  |  |  | 14 | 2 | 0 | 0 | 744 | 28 | 20832 | 0 | 100%
22 | 400 | Korba-Vindhyachal # 2 | 2013-10-08 | 11:48 | 2013-10-10 | 10:25 | [9 empty] | 1899-12-31 22:37 | 46 | 37 | OSPD | Line H/T to availed outage by NTPC for maintenance works | 10/545 | 10/666
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 46 | 37
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 46.6167 |  |  |  |  | 288.99 | 2 | 0 | 0 | 744 | 577.98 | 430017.12 | 0 | 100%
23 | 400 | Padhge -Tarapur # 1 | 2013-10-14 | 2:05 | 2013-10-14 | 2:10 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to O/V at Boisar end.
| 400 | Padhge -Tarapur # 1 | 2013-10-14 | 2:10 | 2013-10-14 | 7:23 | [9 empty] | 0.21736 | 5 | 13 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | 10/979
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 5 | 13
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 5.2167 |  |  |  |  | 91.119 | 2 | 0 | 0 | 743.9167 | 182.238 | 135569.8855 | 0 | 100%
24 | 400 | Raigarh - SEL # 2 | 2013-10-05 | 13:06 | 2013-10-05 | 18:22 | [9 empty] | 0.21944 | 5 | 16 | OSPD | Line H/T to availed outage availed by Sterlite | WR-'10/347, NLDC 10/61, ER- 10/118 | WR- 10/373, NLDC-10 /67, ER-10/127
| 400 | Raigarh - SEL # 2 | 2013-10-13 | 4:19 | 2013-10-13 | 5:01 |  |  |  | 0.029167 | 0 | 42 | [6 empty] | OMSU | Line tripped due to Bph-E. fault in LILO portion of M/S SEL ltd. Fl= 18km from SEL, 101km from Raigarh |  | 10/898
| 400 | Raigarh - SEL # 2 | 2013-10-19 | 9:50 | 2013-10-19 | 16:02 | [9 empty] | 0.25833 | 6 | 12 | OSPD | Outage availed by SEL for maintenance work | WR-10/1284, NL-204 , ER- 10/461 | WR-10/1305, NL-10/205, ER-10/470
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 42 |  | 0 | 0 |  | 11 | 28
|  | Element Availability= | [6 empty] | 0 |  |  | 0.7 |  |  | 0 |  |  | 11.4667 |  |  |  |  | 105 | 2 | 0 | 0 | 743.3 | 210 | 156093 | 0 | 100%
25 | 400 | Raigarh-Raipur # 4 | 2013-10-02 | 11:35 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-28 12:25 | 708 | 25 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/103
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 708 | 25
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 708.4167 |  |  |  |  | 220.884 | 2 | 0 | 0 | 744 | 441.768 | 328675.392 | 0 | 100%
26 | 400 | Raigarh-Raipur # 1 | 2013-10-13 | 17:10 | 2013-10-30 | 10:38 | [9 empty] | 401:28 | 17 | 28 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/945 | 10/2121
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 17 | 28
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 17.4667 |  |  |  |  | 217.02 | 2 | 0 | 0 | 744 | 434.04 | 322925.76 | 0 | 100%
27 | 400 | Raipur-Sipat # 3 | 2013-10-02 | 11:19 | 2013-10-02 | 19:08 | [9 empty] | 0.32569 | 7 | 49 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/100 | 10/110
| 400 | Raipur-Sipat # 3 | 2013-10-31 | 15:43 | 2013-10-31 | 18:50 | 3:07 | 3 | 7 | [9 empty] | OSPT | Line outage availed for maintenance work at loc. No.310 | 10/2252 | 10/2266
|  | Sub-Total= | [5 empty] | 3 | 7 |  | 0 | 0 |  | 0 | 0 |  | 7 | 49
|  | Element Availability= | [6 empty] | 3.1167 |  |  | 0 |  |  | 0 |  |  | 7.8167 |  |  |  |  | 160 | 2 | 3.1167 | 997.3333 | 744 | 320 | 238080 | 0.0041891 | 99.58%
28 | 400 | Ranchi- Sipat # 2 | 2013-10-02 | 12:25 | 2013-10-02 | 13:55 | [9 empty] | 0.0625 | 1 | 30 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/105 | 10/110
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 1 | 30
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 1.5 |  |  |  |  | 405.772 | 2 | 0 | 0 | 744 | 811.544 | 603788.736 | 0 | 100%
29 | 765 | Seoni-Wardha # 1 | 2013-10-21 | 17:57 | 2013-10-30 | 14:54 | [9 empty] | 1900-01-07 20:57 | 212 | 57 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1430, NL-10/238 | 10/2156
| 765 | Seoni-Wardha # 1 | 2013-10-30 | 14:54 | 2013-10-30 | 15:32 | 0.026389 | 0 | 38 | [9 empty] | OMST | Line charging delay due to adjustment of PLCC AGC at Seoni end. | - | 10/2156
|  | Sub-Total= | [5 empty] | 0 | 38 |  | 0 | 0 |  | 0 | 0 |  | 212 | 57
|  | Element Availability= | [6 empty] | 0.63333 |  |  | 0 |  |  | 0 |  |  | 212.95 |  |  |  |  | 267.894 | 4 | 0.63333 | 678.6648 | 744 | 1071.576 | 797252.544 | 0.00085125 | 99.91%
30 | 765 | Seoni-Wardha # 2 | 2013-09-10 | 13:03 | 2013-10-21 | 9:42 | [9 empty] | 489:42 | 489 | 42 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-'10/1404, NL-10/229
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 489 | 42
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 489.7 |  |  |  |  | 260.763 | 4 | 0 | 0 | 744 | 1043.052 | 776030.688 | 0 | 100%
31 | 400 | Vandana-Birsinghpur | 2013-10-20 | 15:38 | 2013-10-21 | 3:14 | [9 empty] | 0.48333 | 11 | 36 | OSPD | Line outage availed by Birsinghpur (MPPTCL) for attending broken SF6 gas pipe in MPPTCL switchyard damged by monkeys at Birsinghpur end. | 10/1354 | 10/1386
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 11 | 36
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.6 |  |  |  |  | 211.874 | 2 | 0 | 0 | 744 | 423.748 | 315268.512 | 0 | 100%
32 | 400/220 | ICT-1:315MVA: SEONI | 2013-10-22 | 10:31 | 2013-10-22 | 15:02 | [9 empty] | 4:31 | 4 | 31 | SCSD | ICT outage availed for faciliating civil works below/adjacent of bays. | 10/1486 | 10/1510
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 4 | 31
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 4.5167 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
33 | 400/220 | ICT-2:315MVA: SEONI | 2013-10-21 | 10:02 | 2013-10-21 | 14:55 | [9 empty] | 4:53 | 4 | 53 | SCSD | ICT outage availed for faciliating civil works below/adjacent of bays. | 10/1407 | 10/1421
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 4 | 53
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 4.8833 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
34 | 400/220 | ICT-2:315MVA:PUNE | 2013-10-04 | 12:14 | 2013-10-10 | 10:24 | [9 empty] | 1900-01-04 22:10 | 142 | 10 | SPRD | H/T as per WRLDC instructions for power regulation | 10/240 | 10/670
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 142 | 10
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 142.1667 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
35 | 400 | ICT-3:315MVA:PUNE | 2013-10-11 | 10:40 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-19 13:20 | 493 | 20 | SPRD | H/T as per WRLDC instructions for power regulation | 10/752
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 493 | 20
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 493.3333 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
36 | 400 | Bus Reactor / Mapusa (50) | 2013-10-17 | 15:17 | 2013-10-18 | 0:03 | [9 empty] | 0.36528 | 8 | 46 | SVRD | Bus reactor H/T as per WRLDC instructions for Voltage regulation | 10/1171 | 10/1196
| 400 | Bus Reactor / Mapusa (50) | 2013-10-19 | 11:32 | 2013-10-19 | 16:30 | [9 empty] | 0.20694 | 4 | 58 | SVRD | B/R H/T as per WRLDC instruction for voltage regulation | 10/1294 | 10/1309
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 12 | 104
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 13.7333 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
37 | 400 | Bus Reactor / Pune (50) | 2013-10-21 | 11:59 | 2013-10-31 | 24:00 | [9 empty] | 1900-01-09 12:01 | 252 | 1 | SVRD | Line H/T as per WRLDC instructions for Voltage regulation | 10/1412
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 252 | 1
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 252.0167 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
38 | HVDC | POLE # 1 : BHADRAWATI | 2013-10-01 | 16:26 | 2013-10-01 | 16:40 |  |  |  | 0.0097222 | 0 | 14 | [6 empty] | OMSU | HVDC pole tripped due to failure of MSEDCL auxillary power supply |  | 10/47, SR/20,NL/9
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 14 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.23333 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 0 | 0 | 743.7667 | 250 | 185941.6667 | 0 | 100%
39 | HVDC | POLE # 2 : BHADRAWATI | 2013-10-01 | 16:26 | 2013-10-01 | 16:41 |  |  |  | 0.010417 | 0 | 15 | [6 empty] | OMSU | HVDC pole tripped due to failure of MSEDCL auxillary power supply |  | 10/47, SR/20,NL/9
|  | Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 15 |  | 0 | 0 |  | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.25 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 0 | 0 | 743.75 | 250 | 185937.5 | 0 | 100%
| Voltage | Elements Name
| 765 | Akola-Aurangabad # 1
| 400 | Akola-Aurangabad # 2
| 220 | Akola-Wardha # 1
| 132 | Akola-Wardha # 2
| 765/400 | Balco-Birsinghpur
| 400/220 | Balco-Korba
| HVDC | Bhadrawati - Chandrapur # 1
Bhadrawati - Chandrapur # 2
Bhadrawati - Chandrapur # 3
Bhadrawati - Chandrapur # 4
Bhadrawati -Raipur # 1
Bhadrawati-Parli # 1
Bhadrawati-Parli # 2
Bhadrawati-Raipur # 2
Bhadrawati-Raipur # 3
Bhatapara -Korba
Bhatapara-Bhilai
Bhilai - Raipur # 1
Bhilai - Seoni
Bhilai -Bhadrawati
Bhilai -Korba # 1
Bhilai -Korba # 2
Bhilai-Koradi
Bilaspur-Seoni # 1
Bilaspur-Seoni # 2
Bilaspur-Sipat # 1
Bilaspur-Sipat # 2
balco
Boisar - Padhge
Boisar-Tarapur
Boisar-Tarapur # 1
Boisar-Tarapur # 2
Boisar-Vapi
Budhipadar- Korba (E)
DB Power-KSK
DB Power-Raigarh
IEPL -Mouda
IEPL-Wardha
Jharsuguda-Raigarh # 1
Jharsuguda-Rourkela # 1
Jharsuguda-Raigarh # 2
Jharsuguda-Rourkela # 2
Kolhapur - Mapusa # 1
Kolhapur - Mapusa # 2
Koradi - Satpura
Korba - Korba (W)
Korba-Mahan ( Essar)
Korba-Pathadi
Korba-Raipur # 3
Korba-Raipur # 4
Korba-Vandana
Korba-Vindhyachal # 2
KSK - Raigarh
KSK-Raipur
KWPCL- Raigarh
KWPCL-Raipur
Mahan ( Essar)-Vindhyachal
Mouda-Wardha # 2
Padhge -Tarapur # 1
Padhge -Tarapur # 2
Parli (PGCIL)-Parli(MSETCL) # 1
Parli (PGCIL)-Parli(MSETCL) # 2
Parli-Wardha # 1
Parli-Wardha # 2
Pathadi-Sipat
Raigarh - Rourkela # 1
Raigarh - SEL # 1
Raigarh - SEL # 2
Raigarh-Raipur # 4
Raigarh-Raipur # 1
Raipur-Sipat # 1
Raipur-Sipat # 2
Raipur-Sipat # 3
Raipur-Wardha # 1
Raipur-Wardha # 2
Ranchi- Sipat # 1
Ranchi- Sipat # 2
Satpura - Seoni
SEL-Rourkela-SEL # 1
SEL-Rourkela-SEL # 2
Seoni-Wardha # 1
Seoni-Wardha # 2
ICT-1:315MVA : RAIPUR
ICT-2:315MVA : RAIPUR
ICT-3:315MVA : RAIPUR
ICT-1:315MVA : MAPUSA
ICT-2:315MVA : MAPUSA
ICT-1:315MVA :BOISAR
ICT-2:315MVA :BOISAR
ICT-1:315MVA :BHATAPARA
ICT-2:315MVA :BHATAPARA
ICT-1:315MVA :RAIGARH
ICT-2:315MVA :RAIGARH
ICT-1:1500MVA: SEONI
ICT-2:1500MVA: SEONI
ICT-3:1500MVA: SEONI
ICT-1:315MVA: SEONI
ICT-2:315MVA: SEONI
ICT-1:315MVA: WARDHA
ICT-2:315MVA: WARDHA
ICT-3:315MVA: WARDHA
ICT-1:1500MVA: WARDHA
ICT-2:1500MVA: WARDHA
ICT-3:1500MVA: WARDHA
ICT-1:315MVA:SOLAPUR
ICT-2:315MVA:SOLAPUR
ICT-1:315MVA:PUNE
ICT-2:315MVA:PUNE
ICT-3:315MVA:PUNE
ICT-1:1500MVA: BILASPUR
ICT-2:1500MVA: BILASPUR
ICT-3:1500MVA: BILASPUR
POLE # 1 : BHADRAWATI
POLE # 2 : BHADRAWATI
Bus Reactor / Bhadrawati (50)
Bus Reactor / Raipur (80)
Bus Reactor / Mapusa (50)
Bus Reactor / Kolhapur (80)
Bus Reactor / Raigarh (63)
Bus Reactor / Seoni (3 X 80 MVAR)
Bus Reactor /(SLR) in Raipur-Sipat # 3 at Raipur
Bus Reactor / Wardha (50)
Bus Reactor / Solapur (63)
Bus Reactor / Parli (63)
Bus Reactor / Pune (50)
Bus Reactor / Wardha (3 X 80 MVAR)
Bus Reactor / Bilaspur (3 X 80 MVAR)
Bus Reactor / Bilaspur (3 X 80 MVAR): Ranchi-1
Formulas:
Outage deemed available = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to Other = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to PGCIL = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]
Attributed to sys conts. = DATEDIF([Tripping Date],[Resto-ration Date],"D")+[Resto-ration Time]-[Tripping Time]