## certificate
Avialiblity Index for the month of JUNE- 2013 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 220kV Tarapur - Boisar | 100 | 34 | 400 KV D/C Raipur-Sipat # 2 | 100
2 | 400kV Korba-Korba (W) | 100 | 35 | 400 kV S/C Raipur-Sipat # 3 | 100
3 | 400kV Korba-Bhilai # 1 | 99.7963 | 36 | 765 KV S/C Sipat - Bilaspur # 1 | 100
4 | 400kV Korba-Bhilai # 2 | 100 | 37 | 765 KV S/C Bilaspur - Seoni # 1 | 100
5 | 400kV Bhilai-Koradi | 100 | 38 | 765 KV S/C Sipat - Bilaspur # 2 | 100
6 | 400kV Koradi-Satpura | 100 | 39 | 765 KV S/C Bilaspur - Seoni # 2 | 100
7 | 400kV Bhilai - Raipur # 1 | 100 | 40 | 765 KV S/C Seoni-Wardha # 1 | 100
8 | 400 KV Bhilai - Bhadrawati | 100 | 41 | 765 KV S/C Seoni-Wardha # 2 | 100
9 | 400 kV Raipur - Bhadrawati # 1 | 100 | 42 | 400 KV D/C Wardha-Akola # 1 | 100
10 | 400kV Raipur - Bhadrawati # 2 | 100 | 43 | 400 KV D/C Wardha-Akola # 2 | 100
11 | 400kV Raipur - Bhadrawati # 3 | 100 | 44 | 400 KV D/C Akola-Aurangabad # 1 | 100
12 | 400kV B'vati-Chandrapur # 1 | 100 | 45 | 400 KV D/C Akola-Aurangabad # 2 | 100
13 | 400kV B'vati-Chandrapur # 2 | 100 | 46 | 400KV Bhadrawati-Parli # 1 | 100
14 | 400kV B'vati-Chandrapur # 3 | 100 | 47 | 400KV Bhadrawati-Parli # 2 | 100
15 | 400kV B'vati-Chandrapur # 4 | 100 | 48 | 400KV Parli-Parli # 1 | 98.5949
16 | 400kV Kolhapur - Mapusa # 1 | 100 | 49 | 400KV Parli-Parli # 2 | 99.0065
17 | 400kV Kolhapur - Mapusa # 2 | 100 | 50 | 400KV Korba-Raipur-3 | 100
18 | 400kV Tarapur - Padghe # 1 | 100 | 51 | 400KV Korba-Raipur-4 | 100
19 | 400kV Tarapur - Padghe # 2 | 100 | 52 | 400KV Wardha-Parli # 1 | 100
20 | 400 KV BOISAR - Padge | 98.892 | 53 | 400KV Wardha-Parli # 2 | 100
21 | 400kV Tarapur - Boisar #1 | 100 | 54 | 400KV Korba-Balco (lilo of Korba-Biringsinghpur # 2) | 100
22 | 400kV Tarapur - Boisar #2 | 100 | 55 | 400KV Balco-Birsinghpur (lilo of Korba-Biringsinghpur # 2) | 100
23 | 400 KV Vapi - Boisar | 99.0741 | 56 | 400KV Mouda-Wardha # 2 | 99.9884
24 | 400kV Vindhyachal - Mahan ( Essar) | 100 | 57 | 400KV Korba-Vandana (lilo of Korba-Birsinghpur # 1) | 100
25 | 400kV Mahan ( Essar) - Korba | 100 | 58 | 400KV Vandana-Bhirshingpur- (lilo of Korba-Birsinghpur # 1) | 100
26 | 400 kV Vindyanchal-Korba #2 | 100 | 59 | 400KV Raipur-Wardha # 1 | 100
27 | 400 KV Satpura - Seoni (LILO portion) | 100 | 60 | 400KV Raipur-Wardha # 2 | 100
28 | 400 KV Seoni - Bhilai (LILO portion) | 100 | 61 | 400KV D/C Wardha-IEPL (Lilo of Mouda- Wardha # 1 ) | 100
29 | 400KV Bhilai- Bhatapara | 100 | 62 | 400KV D/C IEPL -Mouda (Lilo of Mouda- Wardha # 1 ) | 100
30 | 400KV Korba - Bhatapara | 100 | 63 | D/C Raipur-Raipur (pooling/Durg) # 1 | 100
31 | 400kV Korba - Pathadi | 100 | 64 | D/C Raipur-Raipur (pooling/Durg) # 2 | 100
32 | 400kV Pathadi - Sipat | 100 | 65 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 1 | 100
33 | 400 KV D/C Raipur-Sipat # 1 | 100 | 66 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 2 | 100
67 | 400KV Raipur - Raigarh # 1 | 100 | 102 | 765/220kV AT # 2 / Bilaspur | 100
68 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] | 100 | 103 | 400/220kV ICT # 2 / Bhatapara | 100
69 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] | 100 | 104 | 400/220kV ICT # 2 / Seoni | 100
70 | 400KV D/C Sipat-Ranchi # 1 | 99.9769 | 105 | 400/220kV ICT # 3 / Raipur | 100
71 | 400KV D/C Sipat-Ranchi # 2 | 100 | 106 | 400/220kV ICT # 1 / Wardha | 100
72 | 220KV Korba-Bhudhipadar # 3 | 100 | 107 | 400/220kV ICT # 2 / Wardha | 100
73 | 400KV Raipur - Raigarh # 4 | 100 | 108 | 400/220kV ICT # 3 / Wardha | 100
74 | 400KV Raigarh - Jharsuguda # 2 ( lilo of Raigarh-Rourkela # 3) | 100 | 109 | 400/220kV ICT # 1 / Solapur | 100
75 | 400KV Jharsuguda-Rourkela # 2 ( lilo of Raigarh-Rourkela # 3) | 100 | 110 | 400/220kV ICT # 2 / Solpaur | 100
76 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] | 99.9884 | 111 | 400/220kV ICT # 1 / Pune | 100
77 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] | 100 | 112 | 400/220kV ICT # 2 / Pune | 100
78 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] | 100 | 113 | 400/220kV ICT # 3 / Pune | 100
79 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] | 99.4443 | 114 | 765/400kV AT # 3 / Bilaspur | 100
80 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] | 100 | 115 | 765/400kV AT # 1 / Raigarh (Kotra) | 100
81 | Raipur-KWPCL (lilo of Raipur - Raigarh # 2 ) | 100 | 116 | Bus reactor / B'vati | 100
82 | KWPCL- Raigarh (lilo of Raipur - Raigarh # 2 ) | 100 | 117 | Bus Reactor / Raipur | 100 | 122
83 | 400KV Raigarh - Jharsuguda # 1 (lilo of Raigarh - Rourkela#1) | 100 | 118 | Bus Reactor / Mapusa | 100
84 | 400KV Jharsuguda- Rourkela # 1 (lilo of Raigarh - Rourkela#1) | 100 | 119 | Bus Reactor / Kolhapur | 100
85 | 400/220kV ICT # 1 / Raipur | 100.00 | 120 | Bus Reactor / Raigarh | 100
86 | 400/220kV ICT # 2 / Raipur | 100 | 121 | Bus Reactor / Seoni (3 x 80) | 100
87 | 400/220kV ICT # 1 / Mapusa | 100 | 122 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur | 100
88 | 400/220kV ICT # 2 / Mapusa | 100 | 123 | Bus Reactor / Wardha | 100
89 | 400/220kV ICT # 1 / Boisar | 100 | 124 | Bus Reactor / Solapur | 100
90 | 400/220kV ICT # 2 / Boisar | 100 | 125 | Bus Reactor / Parli | 100
91 | 400/220kV ICT # 1 / Bhatapara | 100 | 126 | Bus Reactor / Pune | 100
92 | 400/220kV ICT # 1 / Raigarh | 100 | 127 | 765KV Bus Reactor / Wardha(3x80) | 100
93 | 400/220kV ICT # 2 / Raigarh | 100 | 128 | 765KV Bus Reactor / Bilaspur(3x80) | 100
94 | 765/400kV AT # 1 / Seoni | 100 | 129 | 765KV Bina line Switchable Line Reactor at Seoni (3x80) | 100
95 | 765/400kV AT # 2 / Seoni | 100 | 130 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80) | 100
96 | 765/400kV AT # 3 / Seoni | 100 | 131 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80) | 100
97 | 400/220kV ICT # 1 / Seoni | 100 | 132 | 765KV Ranchi # 1 Switchable line Reactor charged as Bus Reactor at Bilaspur | 100
98 | 765/220kV AT # 1 / Wardha | 100 | 133 | 765KV Bus Reactor at Raigarh (Kotra) | 100
99 | 765/220kV AT # 2 / Wardha | 100 | 134 | 500 MW HVDC B'vati Pole # 1 | 100
100 | 765/220kV AT # 3 / Wardha | 100 | 135 | 500 MW HVDC B'vati Pole # 2 | 98.93
101 | 765/220kV AT # 1 / Bilaspur | 100
66
85
Availability Bus Reactors =
System Availability :-

## iNDEX
WRTS-I SYSTEM AVAILABILITY DETAILS :
AVAILABILITY INDEX FOR JUNE-2013
| Element Name | 2013-06-16 |  |  |  | Total Outage | Total Outage |  | Line | [6 empty] | Element | Target
[6 empty] | Hrs | Hrs | Individual | length | NSC1 | OH1* | Cktkm1 | THM * | NAFM | Availability | wise | Availability
Sl. |  | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | PGCIL | OTHERS | THM | Ckrkm1 |  | NSC1 | * NSC1 | Cktkm1 * |  | =100-100*O | Availability | as per
No. |  | Hrs | Mints | Hrs | Mints | OH1 | OH2 |  |  |  | *CktKm1 |  | NSC1 |  |  | Achieved | SOP
[6 empty] | Hrs | Hrs
1 | 220kV Tarapur - Boisar |  |  |  |  | 0 | 0 | 720 | 20.56 | 1 | 0 | 20.56 | 14803.2 | 0 | 100 | 100 | 90%
2 | 400kV Korba-Korba (W) |  |  |  |  | 0 | 0 | 720 | 14 | 2 | 0 | 28 | 20160 | 0 | 100 | 100 | 90%
3 | 400kV Korba-Bhilai # 1 | 1 | 28 |  |  | 1.4667 | 0 | 720 | 197 | 2 | 577.8667 | 394 | 283680 | 0.002037 | 99.7963 | 99.7963 | 90%
4 | 400kV Korba-Bhilai # 2 |  |  |  |  | 0 | 0 | 720 | 192 | 2 | 0 | 384 | 276480 | 0 | 100 | 100 | 90%
5 | 400kV Bhilai-Koradi |  |  | 0 | 43 | 0 | 0.71667 | 719.2833 | 272 | 2 | 0 | 544 | 391290.1333 | 0 | 100 | 100 | 90%
6 | 400kV Koradi-Satpura |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 149 | 2 | 0 | 298 | 214535.1667 | 0 | 100 | 100 | 90%
7 | 400kV Bhilai - Raipur # 1 |  |  |  |  | 0 | 0 | 720 | 13 | 2 | 0 | 26 | 18720 | 0 | 100 | 100 | 90%
8 | 400 KV Bhilai - Bhadrawati |  |  | 32 | 46 | 0 | 32.7667 | 687.2333 | 322 | 2 | 0 | 644 | 442578.2667 | 0 | 100 | 100 | 90%
9 | 400 kV Raipur - Bhadrawati # 1 |  |  |  |  | 0 | 0 | 720 | 333 | 2 | 0 | 666 | 479520 | 0 | 100 | 100 | 90%
10 | 400kV Raipur - Bhadrawati # 2 |  |  |  |  | 0 | 0 | 720 | 345.55 | 2 | 0 | 691.1 | 497592 | 0 | 100 | 100 | 90%
11 | 400kV Raipur - Bhadrawati # 3 |  |  |  |  | 0 | 0 | 720 | 345.55 | 2 | 0 | 691.1 | 497592 | 0 | 100 | 100 | 90%
12 | 400kV B'vati-Chandrapur # 1 |  |  |  |  | 0 | 0 | 720 | 20 | 2 | 0 | 40 | 28800 | 0 | 100 | 100 | 90%
13 | 400kV B'vati-Chandrapur # 2 |  |  |  |  | 0 | 0 | 720 | 20 | 2 | 0 | 40 | 28800 | 0 | 100 | 100 | 90%
14 | 400kV B'vati-Chandrapur # 3 |  |  |  |  | 0 | 0 | 720 | 22.42 | 2 | 0 | 44.84 | 32284.8 | 0 | 100 | 100 | 90%
15 | 400kV B'vati-Chandrapur # 4 |  |  |  |  | 0 | 0 | 720 | 22.42 | 2 | 0 | 44.84 | 32284.8 | 0 | 100 | 100 | 90%
16 | 400kV Kolhapur - Mapusa # 1 |  |  |  |  | 0 | 0 | 720 | 150 | 2 | 0 | 300 | 216000 | 0 | 100 | 100 | 90%
17 | 400kV Kolhapur - Mapusa # 2 |  |  |  |  | 0 | 0 | 720 | 150 | 2 | 0 | 300 | 216000 | 0 | 100 | 100 | 90%
18 | 400kV Tarapur - Padghe # 1 |  |  |  |  | 0 | 0 | 720 | 91.119 | 2 | 0 | 182.238 | 131211.36 | 0 | 100 | 100 | 90%
19 | 400kV Tarapur - Padghe # 2 |  |  |  |  | 0 | 0 | 720 | 91.119 | 2 | 0 | 182.238 | 131211.36 | 0 | 100 | 100 | 90%
20 | 400 KV BOISAR - Padge | 7 | 55 | 5 | 31 | 7.9167 | 5.5167 | 714.4833 | 101 | 2 | 1599.1667 | 202 | 144325.6333 | 0.01108 | 98.892 | 98.892 | 90%
21 | 400kV Tarapur - Boisar #1 |  |  |  |  | 0 | 0 | 720 | 20.881 | 2 | 0 | 41.762 | 30068.64 | 0 | 100 | 100 | 90%
22 | 400kV Tarapur - Boisar #2 |  |  |  |  | 0 | 0 | 720 | 20.881 | 2 | 0 | 41.762 | 30068.64 | 0 | 100 | 100 | 90%
23 | 400 KV Vapi - Boisar | 6 | 40 |  |  | 6.6667 | 0 | 720 | 91 | 2 | 1213.3333 | 182 | 131040 | 0.0092593 | 99.0741 | 99.0741 | 90%
24 | 400kV Vindhyachal - Mahan ( Essar) |  |  |  |  | 0 | 0 | 720 | 19 | 2 | 0 | 38 | 27360 | 0 | 100 | 100 | 90%
25 | 400kV Mahan ( Essar) - Korba |  |  |  |  | 0 | 0 | 720 | 196 | 2 | 0 | 392 | 282240 | 0 | 100 | 100 | 90%
26 | 400 kV Vindyanchal-Korba #2 |  |  |  |  | 0 | 0 | 720 | 288.994 | 2 | 0 | 577.988 | 416151.36 | 0 | 100 | 100 | 90%
27 | 400 KV Satpura - Seoni (LILO portion) |  |  |  |  | 0 | 0 | 720 | 1.507 | 2 | 0 | 3.014 | 2170.08 | 0 | 100 | 100 | 90%
28 | 400 KV Seoni - Bhilai (LILO portion) |  |  |  |  | 0 | 0 | 720 | 1.498 | 2 | 0 | 2.996 | 2157.12 | 0 | 100 | 100 | 90%
29 | 400KV Bhilai- Bhatapara |  |  | 234 | 15 | 0 | 234.25 | 485.75 | 90.453 | 2 | 0 | 180.906 | 87875.0895 | 0 | 100 | 100 | 90%
30 | 400KV Korba - Bhatapara |  |  |  |  | 0 | 0 | 720 | 123.73 | 2 | 0 | 247.46 | 178171.2 |  |  | 100 | 90%
31 | 400kV Korba - Pathadi |  |  |  |  | 0 | 0 | 720 | 39.536 | 2 | 0 | 79.072 | 56931.84 | 0 | 100 | 100 | 90%
32 | 400kV Pathadi - Sipat |  |  |  |  | 0 | 0 | 720 | 29.117 | 2 | 0 | 58.234 | 41928.48 | 0 | 100 | 100 | 90%
33 | 400 KV D/C Raipur-Sipat # 1 |  |  |  |  | 0 | 0 | 720 | 149.12 | 2 | 0 | 298.24 | 214732.8 | 0 | 100 | 100 | 90%
34 | 400 KV D/C Raipur-Sipat # 2 |  |  |  |  | 0 | 0 | 720 | 149.12 | 2 | 0 | 298.24 | 214732.8 | 0 | 100 | 100 | 90%
35 | 400 kV S/C Raipur-Sipat # 3 |  |  |  |  | 0 | 0 | 720 | 162.04 | 2 | 0 | 324.08 | 233337.6 | 0 | 100 | 100 | 90%
36 | 765 KV S/C Sipat - Bilaspur # 1 |  |  |  |  | 0 | 0 | 720 | 21.507 | 4 | 0 | 86.028 | 61940.16 | 0 | 100 | 100 | 90%
37 | 765 KV S/C Bilaspur - Seoni # 1 |  |  |  |  | 0 | 0 | 720 | 337.046 | 4 | 0 | 1348.184 | 970692.48 | 0 | 100 | 100 | 90%
38 | 765 KV S/C Sipat - Bilaspur # 2 |  |  |  |  | 0 | 0 | 720 | 22.216 | 4 | 0 | 88.864 | 63982.08 | 0 | 100 | 100 | 90%
39 | 765 KV S/C Bilaspur - Seoni # 2 |  |  |  |  | 0 | 0 | 720 | 338.33 | 4 | 0 | 1353.32 | 974390.4 | 0 | 100 | 100 | 90%
40 | 765 KV S/C Seoni-Wardha # 1 |  |  |  |  | 0 | 0 | 720 | 267.894 | 4 | 0 | 1071.576 | 771534.72 | 0 | 100 | 100 | 90%
41 | 765 KV S/C Seoni-Wardha # 2 |  |  |  |  | 0 | 0 | 720 | 260.763 | 4 | 0 | 1043.052 | 750997.44 |  |  | 100 | 90%
42 | 400 KV D/C Wardha-Akola # 1 |  |  | 0 | 40 | 0 | 0.66667 | 719.3333 | 161.865 | 2 | 0 | 323.73 | 232869.78 | 0 | 100 | 100 | 90%
43 | 400 KV D/C Wardha-Akola # 2 |  |  |  |  | 0 | 0 | 720 | 161.865 | 2 | 0 | 323.73 | 233085.6 | 0 | 100 | 100 | 90%
44 | 400 KV D/C Akola-Aurangabad # 1 |  |  |  |  | 0 | 0 | 720 | 241.23 | 2 | 0 | 482.46 | 347371.2 |  |  | 100 | 90%
45 | 400 KV D/C Akola-Aurangabad # 2 |  |  |  |  | 0 | 0 | 720 | 241.23 | 2 | 0 | 482.46 | 347371.2 |  |  | 100 | 90%
46 | 400KV Bhadrawati-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 378.667 | 2 | 0 | 757.334 | 545280.48 |  |  | 100 | 90%
47 | 400KV Bhadrawati-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 378.667 | 2 | 0 | 757.334 | 545280.48 |  |  | 100 | 90%
48 | 400KV Parli-Parli # 1 | 10 | 7 |  |  | 10.1167 | 0 | 720 | 4.958 | 2 | 100.3169 | 9.916 | 7139.52 |  |  | 98.5949 | 90%
49 | 400KV Parli-Parli # 2 | 7 | 8 | 2 | 0 | 7.1333 | 2 | 718 | 4.958 | 2 | 70.7341 | 9.916 | 7119.688 |  |  | 99.0065 | 90%
50 | 400KV Korba-Raipur-3 |  |  |  |  | 0 | 0 | 720 | 212.83 | 2 | 0 | 425.66 | 306475.2 |  |  | 100 | 90%
51 | 400KV Korba-Raipur-4 |  |  |  |  | 0 | 0 | 720 | 212.83 | 2 | 0 | 425.66 | 306475.2 |  |  | 100 | 90%
52 | 400KV Wardha-Parli # 1 |  |  |  |  | 0 | 0 | 720 | 336.939 | 4 | 0 | 1347.756 | 970384.32 |  |  | 100 | 90%
53 | 400KV Wardha-Parli # 2 |  |  |  |  | 0 | 0 | 720 | 336.939 | 4 | 0 | 1347.756 | 970384.32 |  |  | 100 | 90%
54 | 400KV Korba-Balco (lilo of Korba-Biringsinghpur # 2) |  |  |  |  | 0 | 0 | 720 | 7.454 | 2 | 0 | 14.908 | 10733.76 |  |  | 100 | 90%
55 | 400KV Balco-Birsinghpur (lilo of Korba-Biringsinghpur # 2) |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 219.188 | 2 | 0 | 438.376 | 315594.1887 |  |  | 100 | 90%
56 | 400KV Mouda-Wardha # 2 | 0 | 5 | 0 | 15 | 0.083333 | 0.25 | 719.75 | 123.45 | 4 | 41.15 | 493.8 | 355412.55 |  |  | 99.9884 | 90%
57 | 400KV Korba-Vandana (lilo of Korba-Birsinghpur # 1) |  |  |  |  | 0 | 0 | 720 | 14.768 | 2 | 0 | 29.536 | 21265.92 |  |  | 100 | 90%
58 | 400KV Vandana-Bhirshingpur- (lilo of Korba-Birsinghpur # 1) |  |  |  |  | 0 | 0 | 720 | 211.874 | 2 | 0 | 423.748 | 305098.56 |  |  | 100 | 90%
59 | 400KV Raipur-Wardha # 1 |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 370.565 | 4 | 0 | 1482.26 | 1067103.6783 |  |  | 100 | 90%
60 | 400KV Raipur-Wardha # 2 |  |  |  |  | 0 | 0 | 720 | 370.565 | 4 | 0 | 1482.26 | 1067227.2 |  |  | 100 | 90%
61 | 400KV D/C Wardha-IEPL (Lilo of Mouda- Wardha # 1 ) |  |  |  |  | 0 | 0 | 720 | 52.62 | 4 | 0 | 210.48 | 151545.6 |  |  | 100 | 90%
62 | 400KV D/C IEPL -Mouda (Lilo of Mouda- Wardha # 1 ) |  |  | 0 | 37 | 0 | 0.61667 | 719.3833 | 70.83 | 4 | 0 | 283.32 | 203815.686 |  |  | 100 | 90%
63 | D/C Raipur-Raipur (pooling/Durg) # 1 |  |  |  |  | 0 | 0 | 720 | 21.43 | 2 | 0 | 42.86 | 30859.2 |  |  | 100 | 90%
64 | D/C Raipur-Raipur (pooling/Durg) # 2 |  |  |  |  | 0 | 0 | 720 | 21.43 | 2 | 0 | 42.86 | 30859.2 |  |  | 100 | 90%
65 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 1 |  |  |  |  | 0 | 0 | 720 | 6.288 | 2 | 0 | 12.576 | 9054.72 |  |  | 100 | 90%
66 | 400KV Raigarh - Raigarh ( Kotra ) pooling # 2 |  |  |  |  | 0 | 0 | 720 | 6.288 | 2 | 0 | 12.576 | 9054.72 |  |  | 100 | 90%
67 | 400KV Raipur - Raigarh # 1 |  |  |  |  | 0 | 0 | 720 | 217.02 | 2 | 0 | 434.04 | 312508.8 |  |  | 100 | 90%
68 | 400kV Raigarh -Starlite (SEL) # 1 [ lilo of Raigarh - Rourkela # 2] |  |  | 0 | 40 | 0 | 0.66667 | 719.3333 | 99.46 | 2 | 0 | 198.92 | 143089.7867 |  |  | 100 | 90%
69 | 400kV Starlite (SEL) - Rourkela # 1 [lilo of Raigarh - Rourkela # 2] |  |  |  |  | 0 | 0 | 720 | 113 | 2 | 0 | 226 | 162720 |  |  | 100 | 90%
70 | 400KV D/C Sipat-Ranchi # 1 | 0 | 10 |  |  | 0.16667 | 0 | 720 | 405.772 | 2 | 135.2573 | 811.544 | 584311.68 |  |  | 99.9769 | 90%
71 | 400KV D/C Sipat-Ranchi # 2 |  |  |  |  | 0 | 0 | 720 | 405.772 | 2 | 0 | 811.544 | 584311.68 |  |  | 100 | 90%
72 | 220KV Korba-Bhudhipadar # 3 |  |  |  |  | 0 | 0 | 720 | 184 | 1 | 0 | 184 | 132480 |  |  | 100 | 90%
73 | 400KV Raipur - Raigarh # 4 |  |  |  |  | 0 | 0 | 720 | 220.884 | 2 | 0 | 441.768 | 318072.96 |  |  | 100 | 90%
74 | 400KV Raigarh - Jharsuguda # 2 ( lilo of Raigarh-Rourkela # 3) |  |  | 0 | 32 | 0 | 0.53333 | 719.4667 | 110.98 | 2 | 0 | 221.96 | 159692.8213 |  |  | 100 | 90%
75 | 400KV Jharsuguda-Rourkela # 2 ( lilo of Raigarh-Rourkela # 3) |  | 0 |  |  | 0 | 0 | 720 | 143.06 | 2 | 0 | 286.12 | 206006.4 |  |  | 100 | 90%
76 | 400KV Raipur -KSK (Mahanadi) [lilo of Raipur - Raigarh # 3] | 0 | 5 | 1 | 38 | 0.083333 | 1.6333 | 718.3667 | 134.74 | 2 | 22.4567 | 269.48 | 193585.4493 |  |  | 99.9884 | 90%
77 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] |  |  | 4 | 55 | 0 | 4.9167 | 715.0833 | 85.01 | 2 | 0 | 170.02 | 121578.4683 |  |  | 100 | 90%
78 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 1.129 | 2 | 0 | 2.258 | 1625.5718 |  |  | 100 | 90%
79 | 400kV Raigarh -Starlite (SEL) # 2 [ lilo of Raigarh - Rourkela # 4] | 4 | 0 | 0 | 10 | 4 | 0.16667 | 719.8333 | 105 | 2 | 840 | 210 | 151165 |  |  | 99.4443 | 90%
80 | 400kV Starlite (SEL) - Rourkela # 2 [ lilo of Raigarh - Rourkela # 4] |  |  |  |  | 0 | 0 | 720 | 104.28 | 2 | 0 | 208.56 | 150163.2 |  |  | 100 | 90%
81 | D/C Raipur-KWPCL (lilo of Raipur - Raigarh # 2 ) |  |  | 0 | 5 | 0 | 0.083333 | 719.9167 | 208.29 | 2 | 0 | 416.58 | 299902.885 |  |  | 100 | 90%
82 | D/C KWPCL- Raigarh (lilo of Raipur - Raigarh # 2 ) |  |  |  |  | 0 | 0 | 720 | 8.73 | 2 | 0 | 17.46 | 12571.2 |  |  | 100 | 90%
83 | 400KV Raigarh - Jharsuguda # 1 (lilo of Raigarh - Rourkela#1) |  |  |  |  | 0 | 0 | 720 | 114.46 | 2 | 0 | 228.92 | 164822.4 |  |  | 100 | 90%
84 | 400KV Jharsuguda- Rourkela # 1 (lilo of Raigarh - Rourkela#1) |  |  |  |  | 0 | 0 | 720 | 142.448 | 2 | 0 | 284.896 | 205125.12 |  |  | 100 | 90%
85 | 400/220kV ICT # 1 / Raipur | 229 | 0 |  |  | 229 | 0 | 720 | 315 | 2.5 | 180337.5 | 787.5 | 567000 | 0.31806 | 68.1944 | 100 | 90%
86 | 400/220kV ICT # 2 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
87 | 400/220kV ICT # 1 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
88 | 400/220kV ICT # 2 / Mapusa |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
89 | 400/220kV ICT # 1 / Boisar |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
90 | 400/220kV ICT # 2 / Boisar |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
91 | 400/220kV ICT # 1 / Bhatapara |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
92 | 400/220kV ICT # 1 / Raigarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
93 | 400/220kV ICT # 2 / Raigarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
94 | 765/400kV AT # 1 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
95 | 765/400kV AT # 2 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
96 | 765/400kV AT # 3 / Seoni |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
97 | 400/220kV ICT # 1 / Seoni |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
98 | 765/220kV AT # 1 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
99 | 765/220kV AT # 2 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
100 | 765/220kV AT # 3 / Wardha |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
101 | 765/220kV AT # 1 / Bilaspur |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
102 | 765/220kV AT # 2 / Bilaspur |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
103 | 400/220kV ICT # 2 / Bhatapara |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
104 | 400/220kV ICT # 2 / Seoni |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
105 | 400/220kV ICT # 3 / Raipur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
106 | 400/220kV ICT # 1 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
107 | 400/220kV ICT # 2 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
108 | 400/220kV ICT # 3 / Wardha |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
109 | 400/220kV ICT # 1 / Solapur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
110 | 400/220kV ICT # 2 / Solpaur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
111 | 400/220kV ICT # 1 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
112 | 400/220kV ICT # 2 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
113 | 400/220kV ICT # 3 / Pune |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100 | 90%
114 | 765/400kV AT # 3 / Bilaspur |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
115 | 765/400kV AT # 1 / Raigarh (Kotra) |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100 | 90%
116 | Bus reactor / B'vati |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100 | 90%
117 | Bus Reactor / Raipur |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 0 | 100 | 100 | 90%
118 | Bus Reactor / Mapusa |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100 | 90%
119 | Bus Reactor / Kolhapur |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 0 | 100 | 100 | 90%
120 | Bus Reactor / Raigarh |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100 | 90%
121 | Bus Reactor / Seoni (3 x 80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100 | 90%
122 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100 | 90%
123 | Bus Reactor / Wardha |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100 | 90%
124 | Bus Reactor / Solapur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100 | 90%
125 | Bus Reactor / Parli |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100 | 90%
126 | Bus Reactor / Pune |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100 | 90%
127 | 765KV Bus Reactor / Wardha(3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100 | 90%
128 | 765KV Bus Reactor / Bilaspur(3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100 | 90%
129 | 765KV Bina line Switchable Line Reactor at Seoni (3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100 | 90%
130 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100 | 90%
131 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100 | 90%
132 | 765KV Ranchi # 1 Switchable line Reactor charged as Bus Reactor at Bilaspur |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100 | 90%
133 | 765KV Bus Reactor at Raigarh (Kotra) |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 |  |  | 100 | 90%
134 | 500 MW HVDC B'vati Pole # 1 |  |  |  |  | 0 | 0 | 720 | 500 | 1 | 0 | 500 | 360000 |  |  | 100 | 85%
135 | 500 MW HVDC B'vati Pole # 2 | 7 | 41 |  |  | 7.6833 | 0 | 720 | 500 | 1 | 3841.6667 | 500 | 360000 |  |  | 98.9329 | 85%

## Jun-2013
ANNEXURE-I
OUTAGE DETAILS FOR THE MONTH OF :JUN-2013
ELEMENT WISE AC TRANSMISSION LINE
SN | ELEMENTS NAME | TRIPPING |  | RESTORATION |  | OUTAGE HOURS (HRS.MIN) | [11 empty] | CAT. CODE | DETAILED REASONS OF TRIPPING | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
|  | DATE | TIME | DATE | TIME | Attributed to PGCIL HRS:MIN | Attributed to PGCIL |  | Attributed to Other HRS:MIN | Attributed to Other |  | Attributed to sys conts. HRS:MIN | Attributed to sys conts. |  | Outage deemed available HRS:MIN | Outage deemed available |  |  |  | TRIPPING | CHARGING | A | B | C | D=A*B*C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
[7 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN | [8 empty] | 720
1 | 220kV Tarapur-Boisar
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20.56 | 1 | 0 | 0 | 720 | 20.56 | 14803.2 | 0 | 100%
2 | 400KV Korba-Korba(W)
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 14 | 2 | 0 | 0 | 720 | 28 | 20160 | 0 | 100%
3 | 400KV Korba-Bhilai # 1 | 2013-06-17 | 7:34 | 2013-06-17 | 9:02 | 0.061111 | 1 | 28 | [9 empty] | SRET | Line tripped due to operation of Reactor protection at Bhilai end, Line charged without Reactor | --
| Sub-Total= | [5 empty] | 1 | 28 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 1.4667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 197 | 2 | 1.4667 | 577.8667 | 720 | 394 | 283680 | 0.002037 | 99.8%
4 | 400KV Korba - Bhilai # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 192 | 2 | 0 | 0 | 720 | 384 | 276480 | 0 | 100%
5 | 400KV Bhilai- Koradi | 2013-06-27 | 15:20 | 2013-06-27 | 16:03 |  |  |  | 0:43 | 0 | 43 | [6 empty] | OMSU | Line tripped due to reactor Bucholz relay maloperation at Bhilai end . Reactor was out of service before tripping at Bhilai | -- | 06/2191
| Sub-Total= | [5 empty] | 0 | 0 | 0.029861 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0.71667 |  |  | 0 |  |  | 0 |  |  |  |  | 272 | 2 | 0 | 0 | 719.2833 | 544 | 391290.1333 | 0 | 100%
6 | 400KV Koradi - Satpura | 2013-06-14 | 2:02 | 2013-06-14 | 2:07 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage. | -- | --
|  | 2013-06-14 | 2:07 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-15 21:53 | 405 | 53 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 405 | 53
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 405.8833 |  |  |  |  | 149 | 2 | 0 | 0 | 719.9167 | 298 | 214535.1667 | 0 | 100%
7 | 400KV Raipur-Bhilai#1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 2 | 0 | 0 | 720 | 26 | 18720 | 0 | 100%
8 | 400KV Bhilai-Bhadrawati | 2013-06-21 | 9:52 | 2013-06-22 | 18:38 | [6 empty] | 1899-12-31 08:46 | 32 | 46 |  |  |  | LNCC | OCC approved outage availed for rectification of bend towers due to heavy wind & thunder. | 06/1794 | --
|  | 2013-06-22 | 18:38 | 2013-06-24 | 12:52 | [9 empty] | 1899-12-31 18:14 | 42 | 14 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 06/1901 | 06/2004
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 32 | 46 |  | 42 | 14
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 32.7667 |  |  | 42.2333 |  |  |  |  | 322 | 2 | 0 | 0 | 687.2333 | 644 | 442578.2667 | 0 | 100%
9 | 400KV Raipur - Bhadrawati # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 333 | 2 | 0 | 0 | 720 | 666 | 479520 | 0 | 100%
10 | 400KV Bhadrawati - Raipur # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 345.55 | 2 | 0 | 0 | 720 | 691.1 | 497592 | 0 | 100%
11 | 400KV Raipur-Bhadrawati # 3
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 345.55 | 2 | 0 | 0 | 720 | 691.1 | 497592 | 0 | 100%
12 | 400KV Bhadrawati- Chandrapur # 1 | 2013-06-09 | 16:16 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-20 07:44 | 511 | 44 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/766 | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 511 | 44
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 511.7333 |  |  |  |  | 20 | 2 | 0 | 0 | 720 | 40 | 28800 | 0 | 100%
13 | 400KV Bhadrawati- Chandrapur # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 511.7333
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.5289 |  |  |  |  | 20 | 2 | 0 | 0 | 720 | 40 | 28800 | 0 | 100%
14 | 400KV Bhadrawati-Chandrapur # 3
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 22.42 | 2 | 0 | 0 | 720 | 44.84 | 32284.8 | 0 | 100%
15 | 400KV Bhadrawati-Chandrapur # 4
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 22.42 | 2 | 0 | 0 | 720 | 44.84 | 32284.8 | 0 | 100%
16 | 400KV Kolhapur-Mapusa # 1 | 2013-06-06 | 16:44 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-23 07:16 | 583 | 16 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 06/453
| Sub-Total= | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 583 | 16
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 583.2667 |  |  |  |  | 150 | 2 | 0 | 0 | 720 | 300 | 216000 | 0 | 100%
17 | 400KV Kolhapur - Mapusa # 2 | 2013-05-28 | 16:46 | 2013-06-01 | 8:49 | [9 empty] | 08:49 | 8 | 49 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 05/2172 | 06/19
| 400KV Kolhapur - Mapusa # 2 | 2013-06-01 | 17:09 | 2013-06-02 | 8:34 | [9 empty] | 0.64236 | 15 | 25 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | WR-6/61 | 06/94
| 400KV Kolhapur - Mapusa # 2 | 2013-06-02 | 16:07 | 2013-06-04 | 10:05 | [9 empty] | 1899-12-31 17:58 | 41 | 58 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | -- | 06/117
| 400KV Kolhapur - Mapusa # 2 | 2013-06-04 | 17:09 | 2013-06-06 | 10:04 | [9 empty] | 1899-12-31 16:55 | 40 | 55 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 06/284 | 06/470
| Sub-Total= | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0958 | 104 | 187
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 107.1167 |  |  |  |  | 150 | 2 | 0 | 0 | 720 | 300 | 216000 | 0 | 100%
18 | 400KV Tarapur - Padghe # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 91.119 | 2 | 0 | 0 | 720 | 182.238 | 131211.36 | 0 | 100%
19 | 400KV Tarapur - Padghe # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 91.119 | 2 | 0 | 0 | 720 | 182.238 | 131211.36 | 0 | 100%
20 | 400KV Boisar - Padghe | 2013-06-25 | 7:35 | 2013-06-25 | 15:30 | 0.32986 | 7 | 55 | [9 empty] | OSPT | OCC approved outage availed for insulator replacement works . | 06/2043 | --
|  | 2013-06-25 | 15:30 | 2013-06-25 | 21:01 |  |  |  | 5:31 | 5 | 31 | [6 empty] | OMSU | Line charging delayed at Padghe (MSETCL) end due to ICT tripping at Padghe end. | -- | 06/2084
|  | 2013-06-26 | 8:22 | 2013-06-26 | 20:49 | [9 empty] | 0.51875 | 12 | 27 | OSPD | OCC approved outage availed for maintenance works by MSETCL. | 06/2111 | 06/2137
| Sub-Total= | [5 empty] | 7 | 55 |  | 5 | 31 |  | 0 | 0 |  | 12 | 27
| Element Availability= | [6 empty] | 7.9167 |  |  | 5.5167 |  |  | 0 |  |  | 12.45 |  |  |  |  | 101 | 2 | 7.9167 | 1599.1667 | 714.4833 | 202 | 144325.6333 | 0.01108 | 98.89%
21 | 400kV Tarapur-Boisar # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 20.881 | 2 | 0 | 0 | 720 | 41.762 | 30068.64 | 0 | 100%
22 | 400kV Tarapur-Boisar # 2 | 2013-06-06 | 8:16 | 2013-06-06 | 18:25 | [9 empty] | 0.42292 | 10 | 9 | OSPD | Outage availed by NPCIL(tarapur) for CB maintenance work at NPCIL end. | 06/457 | 06/512
|  | 2013-06-07 | 9:27 | 2013-06-07 | 18:41 | [9 empty] | 0.38472 | 9 | 14 | OSPD | Outage availed by NPCIL for maintenance works at Tarapur | 06/569 | 06/622
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 19 | 23
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 19.3833 |  |  |  |  | 20.881 | 2 | 0 | 0 | 720 | 41.762 | 30068.64 | 0 | 100%
23 | 400KV Boisar - Vapi | 2013-06-05 | 7:58 | 2013-06-05 | 19:55 | [9 empty] | 0.49792 | 11 | 57 | LCSD | OCC approved outage for line stringing works of upcoming 400kv Vapi-Navi mumbai line availed by WR-2. | 06/360 | 06/427
|  | 2013-06-06 | 8:28 | 2013-06-06 | 17:45 | [9 empty] | 0.38681 | 9 | 17 | LCSD | Outage availed by WRTS-2 for Stringing of 400 Vapi-Navi Mumbai LILO at Kala. | 06/458 | 06/506
|  | 2013-06-27 | 10:41 | 2013-06-27 | 17:21 | 0.27778 | 6 | 40 | [9 empty] | OSPT | OCC approved outage availed for line AMP works, insulator replacement done at loc 114,22,28,23,26. | 06/2174 | 06/2197
| Sub-Total= | [5 empty] | 6 | 40 |  | 0 | 0 |  | 0 | 0 |  | 20 | 74
| Element Availability= | [6 empty] | 6.6667 |  |  | 0 |  |  | 0 |  |  | 21.2333 |  |  |  |  | 91 | 2 | 6.6667 | 1213.3333 | 720 | 182 | 131040 | 0.0092593 | 99.07%
24 | 400KV Vindhyachal - Mahan
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 19 | 2 | 0 | 0 | 720 | 38 | 27360 | 0 | 100%
25 | 400KV Korba - Mahan
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 196 | 2 | 0 | 0 | 720 | 392 | 282240 | 0 | 100%
26 | 400KV Korba - Vindhyachal # 2 | 2013-06-18 | 9:07 | 2013-06-20 | 18:23 | [9 empty] | 1900-01-01 09:16 | 57 | 16 | OSPD | OCC approved outage availed by NTPC for maintenance works | 06/1573 | 06/1753
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 57 | 16
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 57.2667 |  |  |  |  | 288.99 | 2 | 0 | 0 | 720 | 577.98 | 416145.6 | 0 | 100%
27 | 400KV Seoni-Satpura
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1.507 | 2 | 0 | 0 | 720 | 3.014 | 2170.08 | 0 | 100%
28 | 400KV Seoni-Bhilai | 2013-06-11 | 11:48 | 2013-06-11 | 19:52 | [9 empty] | 8:04 | 8 | 4 | LCSD | Outage availed for stringing works of upcoming 765kv D/C Raipur(PS)- Wardha | 06/923 | 06/971
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 8 | 4
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.0667 |  |  |  |  | 1.498 | 2 | 0 | 0 | 720 | 2.996 | 2157.12 | 0 | 100%
29 | 400KV Bhilai -Bhatapara | 2013-06-03 | 17:44 | 2013-06-13 | 11:59 | [6 empty] | 1900-01-08 18:15 | 234 | 15 |  |  |  | LNCC | Line tripped due to Bph - E fault, Fault distance 28.7 Km from Bhatapara end. On patrolling tower no.426 & 427 found collasped due to heavy wind & thunder. Line taken on ERS. | -- | 06/1127
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 234 | 15 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 234.25 |  |  | 0 |  |  |  |  | 90.453 | 2 | 0 | 0 | 485.75 | 180.906 | 87875.0895 | 0 | 100%
30 | 400KV Korba-Bhatapara
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 123.73 | 2 | 0 | 0 | 720 | 247.46 | 178171.2 | 0 | 100%
31 | 400kv Korba- Pathadi
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 39.536 | 2 | 0 | 0 | 720 | 79.072 | 56931.84 | 0 | 100%
32 | 400KV Sipat-Pathadi | 2013-06-07 | 10:28 | 2013-06-08 | 18:36 | [9 empty] | 1899-12-31 08:08 | 32 | 8 | OSPD | OCC approved Outage availed by NTPC for 400kv CTs replacement work. | 06/578 | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 32 | 8
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 32.1333 |  |  |  |  | 29.117 | 2 | 0 | 0 | 720 | 58.234 | 41928.48 | 0 | 100%
33 | 400KV Raipur-Sipat # 1 | 2013-06-14 | 13:25 | 2013-06-15 | 18:24 | [9 empty] | 1899-12-31 04:59 | 28 | 59 | OSPD | OCC approved outage for ERS works at Loc. no.152 & 153 for divertion works for Railway line of LAFARGE Cement Ltd. | 02/1228 | 06/1344
|  | 2013-06-18 | 6:37 | 2013-06-20 | 20:24 | [9 empty] | 1900-01-01 13:47 | 61 | 47 | OSPD | OCC approved outage for ERS works for divertion works for railway line of LAFARGE Cement Ltd. | 06/1565 | 06/1751
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 89 | 106
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 90.7667 |  |  |  |  | 149.12 | 2 | 0 | 0 | 720 | 298.24 | 214732.8 | 0 | 100%
34 | 400KV Raipur-Sipat # 2 | 2013-06-14 | 13:25 | 2013-06-17 | 18:34 | [9 empty] | 1900-01-02 05:09 | 77 | 9 | OSPD | OCC approved outage for ERS works at Loc. no.152 & 153 for divertion works for Railway line of LAFARGE Cement Ltd. | 06/1228 | 06/1524
|  | 2013-06-20 | 13:18 | 2013-06-20 | 21:16 | [9 empty] | 0.33194 | 7 | 58 | OSPD | Outage availed M/s LAFARGE to attend balance works of line shifting. | 06/1744 | 06/1765
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 84 | 67
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 85.1167 |  |  |  |  | 149.12 | 2 | 0 | 0 | 720 | 298.24 | 214732.8 | 0 | 100%
35 | 400KV Raipur - Sipat # 3
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 160 | 2 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
[16 empty] | 0 | 0
36 | 765KV Sipat- Bilaspur# 1 | 2013-06-03 | 12:13 | 2013-06-03 | 19:49 | [9 empty] | 0.31667 | 7 | 36 | LCSD | OCC approved outage availed for LANCO bays & line crossing works near Bilaspur. | WR-6/192 ,NL-6/35, | WR-6/227, NL-6/43
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 7 | 36
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.6 |  |  |  |  | 21.507 | 4 | 0 | 0 | 720 | 86.028 | 61940.16 | 0 | 100%
37 | 765KV Seoni-Bilaspur # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337.046 | 4 | 0 | 0 | 720 | 1348.184 | 970692.48 | 0 | 100%
38 | 765KV Sipat- Bilaspur# 2 | 2013-06-05 | 9:20 | 2013-06-05 | 18:40 | [9 empty] | 0.38889 | 9 | 20 | LCSD | OCC approved outage availed for line crossing works near Bilaspur. | WR-6/371 NL-6/75 | WR-6/422 NLDC-6/83
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 9 | 20
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.3333 |  |  |  |  | 22.216 | 4 | 0 | 0 | 720 | 88.864 | 63982.08 | 0 | 100%
39 | 765KV Seoni - Bilaspur# 2 | 2013-06-04 | 10:12 | 2013-06-04 | 20:20 | [9 empty] | 0.42222 | 10 | 8 | LCSD | OCC approved outage availed for line crossing works near Bilaspur. | WR-6/258 NL-6/56 | WR-6/302 NL-6/67
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 10 | 8
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.1333 |  |  |  |  | 338.33 | 4 | 0 | 0 | 720 | 1353.32 | 974390.4 | 0 | 100%
40 | 765KV Seoni - Wardha # 1 | 2013-06-02 | 20:11 | 2013-06-14 | 10:30 | [9 empty] | 1900-01-10 14:19 | 278 | 19 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | WR-06/147, NL-06/27, | WR-06/1211 NLDC-06/204
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 278 | 19
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 278.3167 |  |  |  |  | 267.894 | 4 | 0 | 0 | 720 | 1071.576 | 771534.72 | 0 | 100%
41 | 765KV Seoni - Wardha # 2 | 2013-05-27 | 12:57 | 2013-06-01 | 10:48 | [9 empty] | 10:48 | 10 | 48 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | WR-5/2043 NL-5/288 | WR-6/31 NL-6/07
|  | 2013-06-14 | 10:54 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-15 13:06 | 397 | 6 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | WR-06/1217 NLDC-06/205 | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 407 | 54
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 407.9 |  |  |  |  | 260.763 | 4 | 0 | 0 | 720 | 1043.052 | 750997.44 | 0 | 100%
42 | 400KV Wardha-Akola # 1 | 2013-06-05 | 2:11 | 2013-06-05 | 2:11 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R operated sucessfully at both ends due to B Ph Earth Fault. | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-09 | 17:06 | 2013-06-09 | 17:06 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R operated sucessfully at both ends on Rph Earth fault. Fault location is 161km from Akola end and 3.5km Wardha end | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-14 | 04:06 | 2013-06-14 | 04:11 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Akola end. | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-14 | 04:11 | 2013-06-14 | 9:07 | [9 empty] | 0.20556 | 4 | 56 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1206
| 400KV Wardha-Akola # 1 | 2013-06-15 | 0:34 | 2013-06-15 | 0:39 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Akola end. | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-15 | 0:39 | 2013-06-15 | 7:25 | [9 empty] | 0.28194 | 6 | 46 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1297
| 400KV Wardha-Akola # 1 | 2013-06-16 | 0:43 | 2013-06-16 | 0:48 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on Overvoltage at Wardha end | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-16 | 0:48 | 2013-06-16 | 9:00 | [9 empty] | 0.34167 | 8 | 12 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1385
| 400KV Wardha-Akola # 1 | 2013-06-16 | 12:47 | 2013-06-16 | 12:52 | [6 empty] | 0.0034722 | [5 empty] | GOVC | Line tripped on overvoltage at Akola end. | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-16 | 12:52 | 2013-06-16 | 14:16 | [9 empty] | 0.058333 | 1 | 24 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1412
| 400KV Wardha-Akola # 1 | 2013-06-17 | 3:08 | 2013-06-17 | 3:13 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to over volate at Akola end.
| 400KV Wardha-Akola # 1 | 2013-06-17 | 3:13 | 2013-06-18 | 4:52 | [9 empty] | 1899-12-31 01:39 | 25 | 39 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1556
| 400KV Wardha-Akola # 1 | 2013-06-25 | 1:22 | 2013-06-25 | 1:27 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Akola end. | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-25 | 1:27 | 2013-06-25 | 6:07 | [9 empty] | 0.19444 | 4 | 40 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | 06/2041
| 400KV Wardha-Akola # 1 | 2013-06-26 | 1:19 | 2013-06-26 | 6:10 | [9 empty] | 0.20208 | 4 | 51 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 06/2098 | 06/2104
| 400KV Wardha-Akola # 1 | 2013-06-27 | 3:14 | 2013-06-27 | 3:19 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on Overvoltage at Wardha end | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-27 | 3:19 | 2013-06-27 | 5:28 | [9 empty] | 0.089583 | 2 | 9 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/2158
| 400KV Wardha-Akola # 1 | 2013-06-28 | 2:22 | 2013-06-28 | 2:27 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to overvolatge at Akola end | --
| 400KV Wardha-Akola # 1 | 2013-06-28 | 2:27 | 2013-06-28 | 5:52 | [9 empty] | 0.14236 | 3 | 25 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/2218
| 400KV Wardha-Akola # 1 | 2013-06-29 | 3:05 | 2013-06-29 | 3:10 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to overvoltage at Akola end | -- | --
| 400KV Wardha-Akola # 1 | 2013-06-29 | 3:10 | 2013-06-29 | 6:04 | [9 empty] | 0.12083 | 2 | 54 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/2294
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 40 |  | 59 | 356
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.66667 |  |  | 64.9333 |  |  |  |  | 161.865 | 2 | 0 | 0 | 719.3333 | 323.73 | 232869.78 | 0 | 100%
43 | 400kv Wardha-Akola # 2 | 2013-06-17 | 18:51 | 2013-06-17 | 18:51 | 0 | 0 | 0 | [9 empty] | LART | A/R successful on B ph - E fault. Fault location is 46 Km from Akola, 112 Km from Wardha, Fault current is 2.76 KA | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 161.865 | 2 | 0 | 0 | 720 | 323.73 | 233085.6 | 0 | 100%
44 | 400KV Akola - Aurangabad # 1 | 2013-06-16 | 12:59 | 2013-06-16 | 14:24 | [9 empty] | 0.059028 | 1 | 25 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/1408 | 06/1416
|  | 2013-06-26 | 1:05 | 2013-06-26 | 6:27 | [9 empty] | 0.22361 | 5 | 22 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 06/2097 | 06/2105
|  | 2013-06-26 | 22:20 | 2013-06-27 | 5:50 | [9 empty] | 0.3125 | 7 | 30 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/2139 | 06/2157
|  | 2013-06-28 | 10:20 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-01 13:40 | 61 | 40 | LCSD | For replacing existing ACSR conductor Jack Bus with INVAR conductor at Aurangabad. | -- | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 74 | 117
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 75.95 |  |  |  |  | 241.23 | 2 | 0 | 0 | 720 | 482.46 | 347371.2 | 0 | 100%
45 | 400KV Akola - Aurangabad # 2 | 2013-06-16 | 2:54 | 2013-06-16 | 9:33 | [9 empty] | 0.27708 | 6 | 39 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/1373 | 06/1400
|  | 2013-06-16 | 22:49 | 2013-06-17 | 7:19 | [9 empty] | 0.35417 | 8 | 30 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/1439 | 06/1467
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 14 | 69
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 15.15 |  |  |  |  | 241.23 | 2 | 0 | 0 | 720 | 482.46 | 347371.2 | 0 | 100%
46 | 400KV Bhadrawati - Parli # 1 | 2013-06-13 | 23:50 | 2013-06-22 | 9:41 | [9 empty] | 1900-01-07 09:51 | 201 | 51 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/1183 | 06/1866
|  | 2013-06-30 | 2:13 | 2013-06-30 | 24:00 | [9 empty] | 0.90764 | 21 | 47 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | - | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 222 | 98
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 223.6333 |  |  |  |  | 378.667 | 2 | 0 | 0 | 720 | 757.334 | 545280.48 | 0 | 100%
47 | 400KV Bhadrawati - Parli # 2 | 2013-06-02 | 19:24 | 2013-06-13 | 9:24 | [9 empty] | 1900-01-09 14:00 | 254 | 0 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 06/141 | 06/1105
|  | 2013-06-23 | 16:17 | 2013-06-29 | 10:28 | [9 empty] | 1900-01-04 18:11 | 138 | 11 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/1938 | 06/32306
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 392 | 11
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 392.1833 |  |  |  |  | 378.667 | 2 | 0 | 0 | 720 | 757.334 | 545280.48 | 0 | 100%
48 | 400KV Parli -Parli # 1 | 2013-06-09 | 9:13 | 2013-06-09 | 19:20 | 10:07 | 10 | 7 | [9 empty] | OSPT | OCC approved Outage availed for AMP work | 06/737 | 06/788
| Sub-Total= | [5 empty] | 10 | 7 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 10.1167 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 4.958 | 2 | 10.1167 | 100.3169 | 720 | 9.916 | 7139.52 | 0.014051 | 98.59%
49 | 400KV Parli- Parli # 2 | 2013-06-07 | 10:11 | 2013-06-07 | 17:19 | 7:08 | 7 | 8 | [9 empty] | OSPT | OCC approved outage availed for AMP Works | 06/576
|  | 2013-06-07 | 17:19 | 2013-06-07 | 19:19 |  |  |  | 2:00 | 2 | 0 | [6 empty] | OMSU | Line charging delayed at MSETCL end. |  | 06/624
| Sub-Total= | [5 empty] | 7 | 8 |  | 2 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 7.1333 |  |  | 2 |  |  | 0 |  |  | 0 |  |  |  |  | 4.958 | 2 | 7.1333 | 70.7341 | 718 | 9.916 | 7119.688 | 0.009935 | 99.01%
50 | 400KV Korba- Raipur # 3 | 2013-06-22 | 9:29 | 2013-06-22 | 19:12 | [9 empty] | 0.40486 | 9 | 43 | OSPD | OCC approved outage availed by NTPC for relay firmware upgradation works. | 06/1868 | 06/1900
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 9 | 43
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.7167 |  |  |  |  | 212.83 | 2 | 0 | 0 | 720 | 425.66 | 306475.2 | 0 | 100%
51 | 400KV Korba-Raipur # 4 | 2013-06-24 | 9:47 | 2013-06-25 | 16:48 | [9 empty] | 1899-12-31 07:01 | 31 | 1 | OSPD | OCC approved outage availed by NTPC for Main # 2 Micom relay firmware upgradation works. | 06/1991 | 06/2071
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 31 | 1
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 31.0167 |  |  |  |  | 212.83 | 2 | 0 | 0 | 720 | 425.66 | 306475.2 | 0 | 100%
52 | 400KV Wardha- Parli # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 336.939 | 4 | 0 | 0 | 720 | 1347.756 | 970384.32 | 0 | 100%
53 | 400KV Wardha-Parli # 2 | 2013-06-06 | 4:13 | 2013-06-06 | 4:13 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R operated sucessfully at both ends on BPh to Earth Fault F/L=129 km from Wardha | -- | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 336.939 | 4 | 0 | 0 | 720 | 1347.756 | 970384.32 | 0 | 100%
54 | 400KV Korba - Balco
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 7.454 | 2 | 0 | 0 | 720 | 14.908 | 10733.76 | 0 | 100%
55 | 400KV Balco- Birsinghpur | 2013-06-19 | 13:01 | 2013-06-19 | 13:06 |  |  |  | 0:05 | 0 | 5 | [6 empty] | SBBU | Line tripped due to Busbar differential protection operation at BALCO end. | -- | 06/1731
|  | 2013-06-19 | 13:06 | 2013-06-20 | 11:05 | [9 empty] | 21:59 | 21 | 59 | GOMD | Line unable to restore after operation of Busbar differential protection at BALCO end. | -- | 06/1731
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 5 |  | 0 | 0 |  | 21 | 59
| Element Availability= | [6 empty] | 0 |  |  | 0.083333 |  |  | 0 |  |  | 21.9833 |  |  |  |  | 219.188 | 2 | 0 | 0 | 719.9167 | 438.376 | 315594.1887 | 0 | 100%
56 | 400KV Wardha-Mouda # 2 | 2013-06-04 | 15:46 | 2013-06-04 | 15:56 |  |  |  | 0:10 | 0 | 10 | [6 empty] | OMSU | Line tripped due to DT received at Wardha end while online relay testing was done at NTPC Mouda end. | -- | --
| 400KV Wardha-Mouda # 2 | 2013-06-04 | 15:56 | 2013-06-05 | 8:56 | [9 empty] | 17:00 | 17 | 0 | GOMD | Line unable to restore after trippping due to problem at NTPC Mouda end. | -- | 06/364
| 400KV Wardha-Mouda # 2 | 2013-06-06 | 1:39 | 2013-06-06 | 1:44 | 0:05 | 0 | 5 | [9 empty] | LEFT | Line tripped on earth fault.fault location is 24.1km from Wardha end | -- | --
| 400KV Wardha-Mouda # 2 | 2013-06-06 | 1:44 | 2013-06-06 | 10:10 | [9 empty] | 0.35139 | 8 | 26 | GOMD | Line unable to restore due to voltage regulation, hence kept uncharged as per WRLDC instructions. | -- | 06/460
| 400KV Wardha-Mouda # 2 | 2013-06-09 | 18:01 | 2013-06-09 | 18:06 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on over voltage at Mouda end | -- | --
| 400KV Wardha-Mouda # 2 | 2013-06-09 | 18:06 | 2013-06-09 | 23:38 | [9 empty] | 0.23056 | 5 | 32 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/784 | 06/805
| 400KV Wardha-Mouda # 2 | 2013-06-12 | 15:12 | 2013-06-14 | 15:26 | [9 empty] | 1900-01-01 00:14 | 48 | 14 | OSPD | Outage availed by NTPC for Busbar modification work at NTPC mauda end. | 06/1028 | 06/1234
| 400KV Wardha-Mouda # 2 | 2013-06-15 | 12:04 | 2013-06-15 | 20:47 | [9 empty] | 0.36319 | 8 | 43 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/1322 | 06/1355
| 400KV Wardha-Mouda # 2 | 2013-06-17 | 14:55 | 2013-06-20 | 20:23 | [9 empty] | 1900-01-02 05:28 | 77 | 28 | OSPD | Outage availed by NTPC for Busbar modification works at Mouda | 06/1505 | 06/1757
| 400KV Wardha-Mouda # 2 | 2013-06-30 | 1:21 | 2013-06-30 | 10:08 | [9 empty] | 0.36597 | 8 | 47 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 06/2372 | 06/2398
| Sub-Total= | [5 empty] | 0 | 5 |  | 0 | 10 |  | 0 | 5 |  | 171 | 190
| Element Availability= | [6 empty] | 0.083333 |  |  | 0.16667 |  |  | 0.083333 |  |  | 174.1667 |  |  |  |  | 123.45 | 4 | 0.083333 | 41.15 | 719.75 | 493.8 | 355412.55 | 0.00011578 | 99.99%
57 | 400KV Korba-Vandana | 2013-06-20 | 11:46 | 2013-06-21 | 19:00 | [9 empty] | 1899-12-31 07:14 | 31 | 14 | OSPD | OCC approved outage availed by NTPC for maintenance works
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 31 | 14
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 31.2333 |  |  |  |  | 14.768 | 2 | 0 | 0 | 720 | 29.536 | 21265.92 | 0 | 100%
58 | 400KV Vandana - Bhirsingpur | 2013-06-20 | 12:00 | 2013-06-22 | 9:53 | [9 empty] | 1899-12-31 21:53 | 45 | 53 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | 06/1870
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 45 | 53
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 45.8833 |  |  |  |  | 211.874 | 2 | 0 | 0 | 720 | 423.748 | 305098.56 | 0 | 100%
59 | 400KV Raipur - Wardha # 1 | 2013-06-01 | 9:13 | 2013-06-02 | 19:49 | [9 empty] | 1899-12-31 10:36 | 34 | 36 | LCSD | Outage availed for stringing works of upcoming 765kv Raipur-Wardha line. | WR-6/23 NLDCl-6/03 | WR-06/144, NL-06/26,
|  | 2013-06-05 | 18:46 | 2013-06-05 | 18:46 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R operated sucessfully at both ends on Y-Ph to Earth Fault F/L=1.94 km from Raipur. | -- | --
|  | 2013-06-16 | 14:54 | 2013-06-16 | 14:59 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to overvoltage at Wardha. | -- | --
|  | 2013-06-16 | 14:59 | 2013-06-17 | 7:49 | [9 empty] | 0.70139 | 16 | 50 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1470
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 50 | 86
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 51.4333 |  |  |  |  | 370.565 | 4 | 0 | 0 | 719.9167 | 1482.26 | 1067103.6783 | 0 | 100%
60 | 400KV Raipur - Wardha # 2 | 2013-06-01 | 9:25 | 2013-06-02 | 20:34 | [9 empty] | 1899-12-31 11:09 | 35 | 9 | LCSD | Outage availed for stringing works of upcoming 765kv Raipur-Wardha line. | WR-6/25 NLDC-6/04 | WR-06/151, NL-06/28,
|  | 2013-06-06 | 22:33 | 2013-06-06 | 22:33 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R successfully at both ends on Yph-e fault. F/L= 144.6km Wardha end.
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 35 | 9
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 35.15 |  |  |  |  | 370.565 | 4 | 0 | 0 | 720 | 1482.26 | 1067227.2 | 0 | 100%
61 | 400KV Wardha- IEPL
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 52.62 | 4 | 0 | 0 | 720 | 210.48 | 151545.6 | 0 | 100%
62 | 400KV Mouda - IEPL | 2013-05-31 | 20:40 | 2013-06-01 | 16:55 | [9 empty] | 16:55 | 16 | 55 | LVRD | Line kept un charged as per WRLDC instructions for Voltage regulation | -- | 06/58
| 400KV Mouda - IEPL | 2013-06-01 | 19:00 | 2013-06-01 | 19:05 | [6 empty] | 0:05 | 0 | 5 |  |  |  | GOVC | Line tripped due to overvoltage at Mouda end. | -- | --
| 400KV Mouda - IEPL | 2013-06-01 | 19:05 | 2013-06-04 | 11:22 | [9 empty] | 1900-01-01 16:17 | 64 | 17 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
| 400KV Mouda - IEPL | 2013-06-05 | 3:57 | 2013-06-05 | 4:02 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Mouda end .DT received at IEPL end. | -- | --
| 400KV Mouda - IEPL | 2013-06-05 | 4:02 | 2013-06-05 | 11:21 | [9 empty] | 0.30486 | 7 | 19 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/387
| 400KV Mouda - IEPL | 2013-06-05 | 18:05 | 2013-06-05 | 18:10 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Mouda end. | -- | --
| 400KV Mouda - IEPL | 2013-06-05 | 18:10 | 2013-06-07 | 15:12 | [9 empty] | 1899-12-31 21:02 | 45 | 2 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/603
| 400KV Mouda - IEPL | 2013-06-08 | 2:18 | 2013-06-08 | 2:23 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to overvoltage at Mouda end. | -- | --
| 400KV Mouda - IEPL | 2013-06-08 | 2:23 | 2013-06-12 | 11:48 | [9 empty] | 1900-01-03 09:25 | 105 | 25 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1013
| 400KV Mouda - IEPL | 2013-06-14 | 1:38 | 2013-06-14 | 1:49 | [6 empty] | 0.0076389 | 0 | 11 |  |  |  | GOVC | Line tripped due to overvoltage at Mauda end. | -- | --
| 400KV Mouda - IEPL | 2013-06-14 | 1:49 | 2013-06-20 | 12:30 | [9 empty] | 1900-01-05 10:41 | 154 | 41 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1738
| 400KV Mouda - IEPL | 2013-06-25 | 3:40 | 2013-06-25 | 3:46 | [6 empty] | 0.0041667 | 0 | 6 |  |  |  | GOVC | Line tripped due to overvoltage at Mauda end . DT received at IEPL end | -- | --
| 400KV Mouda - IEPL | 2013-06-25 | 3:46 | 2013-06-29 | 7:49 | [9 empty] | 1900-01-03 04:03 | 100 | 3 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 37 |  | 491 | 162
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.61667 |  |  | 493.7 |  |  |  |  | 70.83 | 4 | 0 | 0 | 719.3833 | 283.32 | 203815.686 | 0 | 100%
63 | 400KV Raipur-Raipur PS # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21.43 | 2 | 0 | 0 | 720 | 42.86 | 30859.2 | 0 | 100%
64 | 400KV Raipur-Raipur PS # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21.43 | 2 | 0 | 0 | 720 | 42.86 | 30859.2 | 0 | 100%
65 | 400KV Raigarh-Raigarh(Kotra)PS # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 6.288 | 2 | 0 | 0 | 720 | 12.576 | 9054.72 | 0 | 100%
66 | 400KV Raigarh-Raigarh(Kotra)PS # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 6.288 | 2 | 0 | 0 | 720 | 12.576 | 9054.72 | 0 | 100%
[7 empty] | 31 | 143 |  | 7 | 89 |  | 266 | 153 |  | 4322 | 2555.7333 | [7 empty] | 3602.5677 |  |  | 18034290.2605
[8 empty] | 33.3833 |  |  | 8.4833 |  |  | 268.55 |  |  | 4364.5956 | [10 empty] | 0.00019976
99.98%
67 | 400KV Raipur-Raigarh # 1 | 2013-06-09 | 8:29 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-20 15:31 | 519 | 31 | LVRD | Line H/T as per WRLDC instructions for Voltage regulation | 06/741 | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 519 | 31
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 519.5167 |  |  |  |  | 217.02 | 2 | 0 | 0 | 720 | 434.04 | 312508.8 | 0 | 100%
68 | 400KV Raipur -KWPCL | 2013-06-16 | 21:23 | 2013-06-16 | 21:28 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to overvoltage. | -- | --
|  | 2013-06-16 | 21:28 | 2013-06-16 | 21:37 | [9 empty] | 0.00625 | 0 | 9 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1438
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 0 | 9
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 0.15 |  |  |  |  | 208.29 | 2 | 0 | 0 | 719.9167 | 416.58 | 299902.885 | 0 | 100%
69 | 400KV KWPCL-Raigarh
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 8.73 | 2 | 0 | 0 | 720 | 17.46 | 12571.2 | 0 | 100%
70 | 400KV Raigarh-SEL # 1 | 2013-06-01 | 8:01 | 2013-06-01 | 8:06 | [6 empty] | 0:05 | 0 | 5 |  |  |  | GOVC | Line tripped on over voltage at Raigarh end. | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-01 | 8:06 | 2013-06-01 | 13:11 | [9 empty] | 0.21181 | 5 | 5 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-6/42 ER-6/15 NL-6/10
| 400KV Raigarh-SEL # 1 | 2013-06-02 | 17:59 | 2013-06-02 | 18:04 | [6 empty] | 0:05 | 0 | 5 |  |  |  | GOVC | Line tripped due to over voltage at Raigarh end. | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-02 | 18:04 | 2013-06-02 | 18:57 | [9 empty] | 0.036806 | 0 | 53 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-06/132, NL-06/25, ER-06/58
| 400KV Raigarh-SEL # 1 | 2013-06-03 | 6:03 | 2013-06-03 | 6:08 | [6 empty] | 0:05 | 0 | 5 |  |  |  | GOVC | Line tripped due to over voltage at Raigarh end. | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-03 | 6:08 | 2013-06-03 | 8:25 | [9 empty] | 0.095139 | 2 | 17 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-6/169, NL-6/29, ER-6/73
| 400KV Raigarh-SEL # 1 | 2013-06-04 | 6:01 | 2013-06-04 | 6:06 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to over voltage at Raigarh end. | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-04 | 6:06 | 2013-06-04 | 6:45 | [9 empty] | 0.027083 | 0 | 39 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation |  | WR-6/242, NL-6/48, ER-6/119
| 400KV Raigarh-SEL # 1 | 2013-06-05 | 6:01 | 2013-06-05 | 6:06 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Raigarh end | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-05 | 6:06 | 2013-06-05 | 13:04 | [9 empty] | 0.29028 | 6 | 58 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-6/402 NL-6/79 ER-6/172
| 400KV Raigarh-SEL # 1 | 2013-06-05 | 17:33 | 2013-06-05 | 17:38 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Raigarh end | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-05 | 17:38 | 2013-06-05 | 20:05 | [9 empty] | 0.10208 | 2 | 27 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-06/435 ER-6/187 NLDC-6/81
| 400KV Raigarh-SEL # 1 | 2013-06-08 | 7:57 | 2013-06-08 | 8:02 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Raigarh end. | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-08 | 8:02 | 2013-06-09 | 7:13 | [9 empty] | 0.96597 | 23 | 11 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | 06/693 | 06/732, ER/302,Nldc/141
| 400KV Raigarh-SEL # 1 | 2013-06-16 | 2:09 | 2013-06-16 | 2:14 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on Overvoltage at Raigarh end | -- | --
| 400KV Raigarh-SEL # 1 | 2013-06-16 | 2:14 | 2013-06-17 | 20:29 | [9 empty] | 1899-12-31 18:15 | 42 | 15 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-06/1529 NLDC-06/246, ER-540
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 40 |  | 80 | 225
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.66667 |  |  | 83.75 |  |  |  |  | 99.46 | 2 | 0 | 0 | 719.3333 | 198.92 | 143089.7867 | 0 | 100%
71 | 400KV SEL -Rourkela #1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 113 | 2 | 0 | 0 | 720 | 226 | 162720 | 0 | 100%
72 | 400KV Raipur-KSK | 2013-06-08 | 1:37 | 2013-06-08 | 1:42 | 0:05 | 0 | 5 | [9 empty] | LEFT | Line tripped on Rph_Earth fault . F/L is 71.88km from Raipur end. | -- | --
|  | 2013-06-08 | 1:42 | 2013-06-08 | 7:00 | [9 empty] | 0.22083 | 5 | 18 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
|  | 2013-06-23 | 15:59 | 2013-06-23 | 17:37 | [6 empty] | 0.068056 | 1 | 38 |  |  |  | GOVC | Line tripped on over voltage at KSK. | -- | 06/1949
| Sub-Total= | [5 empty] | 0 | 5 |  | 0 | 0 |  | 1 | 38 |  | 5 | 18
| Element Availability= | [6 empty] | 0.083333 |  |  | 0 |  |  | 1.6333 |  |  | 5.3 |  |  |  |  | 134.74 | 2 | 0.083333 | 22.4567 | 718.3667 | 269.48 | 193585.4493 | 0.000116 | 99.99%
73 | 400KV KSK (Mahanadi) - DBPL [lilo of KSK - Raigarh ] | 2013-06-08 | 1:37 | 2013-06-08 | 5:42 |  |  |  | 4:05 | 4 | 5 | [6 empty] | OMSU | Line tripped due to DT receipt at DBPL during tripping of Raipur-KSK line.Charging delayed by DBPL due to CB problem. | -- | 06/651
|  | 2013-06-08 | 6:01 | 2013-06-08 | 6:06 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at DBPL end. | -- | --
|  | 2013-06-08 | 6:06 | 2013-06-08 | 7:54 | [9 empty] | 0.075 | 1 | 48 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/662
|  | 2013-06-22 | 16:54 | 2013-06-22 | 16:59 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at DBPL. | -- | --
|  | 2013-06-22 | 16:59 | 2013-06-22 | 19:31 | [9 empty] | 0.10556 | 2 | 32 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1903
|  | 2013-06-27 | 18:24 | 2013-06-27 | 19:04 |  |  |  | 0:40 | 0 | 40 | [6 empty] | OMSU | Line tripped due to DT received at KSK end.CB opened only at KSK end. | -- | 06/2199
| Sub-Total= | [5 empty] | 0 | 0 |  | 4 | 45 |  | 0 | 10 |  | 3 | 80
| Element Availability= | [6 empty] | 0 |  |  | 4.75 |  |  | 0.16667 |  |  | 4.3333 |  |  |  |  | 85.01 | 2 | 0 | 0 | 715.0833 | 170.02 | 121578.4683 | 0 | 100%
74 | 400KV DBPL- Raigarh [lilo of KSK - Raigarh ] | 2013-06-22 | 16:54 | 2013-06-22 | 16:59 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at DBPL. | -- | --
|  | 2013-06-22 | 17:36 | 2013-06-22 | 19:38 | [9 empty] | 0.084722 | 2 | 2 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | 06/1895
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 5 |  | 2 | 2
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.083333 |  |  | 2.0333 |  |  |  |  | 1.129 | 2 | 0 | 0 | 719.9167 | 2.258 | 1625.5718 | 0 | 100%
75 | 400KV Raipur-Raigarh # 4 | 2013-06-02 | 18:03 | 2013-06-30 | 24:00 | [9 empty] | 1900-01-27 05:57 | 677 | 57 | LVRD | Line hand tripped as per WRLDC instructions for Voltage regulation | 06/130 | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 677 | 57
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 677.95 |  |  |  |  | 220.884 | 2 | 0 | 0 | 720 | 441.768 | 318072.96 | 0 | 100%
76 | 400KV Raigarh-Jharsuguda # 2 | 2013-06-02 | 1:45 | 2013-06-02 | 2:12 |  |  |  | 0:27 | 0 | 27 | [6 empty] | OMSU | Line tripped only at Raigarh end . DT received at Raigarh from Jharsuguda end. | -- | 06/85
|  | 2013-06-22 | 17:32 | 2013-06-22 | 17:37 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Raigarh end. | -- | --
|  | 2013-06-22 | 17:37 | 2013-06-27 | 20:54 | [9 empty] | 1900-01-04 03:17 | 123 | 17 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-06/2200 NLDC-06/333, ERLDC-06/820
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 27 |  | 0 | 5 |  | 123 | 17
| Element Availability= | [6 empty] | 0 |  |  | 0.45 |  |  | 0.083333 |  |  | 123.2833 |  |  |  |  | 110.98 | 2 | 0 | 0 | 719.4667 | 221.96 | 159692.8213 | 0 | 100%
78 | 400KV Jharsuguda-Rourkela # 2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 143.06 | 2 | 0 | 0 | 720 | 286.12 | 206006.4 | 0 | 100%
77 | 400KV Raigarh - SEL # 2 | 2013-06-09 | 7:23 | 2013-06-09 | 11:23 | 4:00 | 4 | 0 | [9 empty] | OSPT | Line outage availed by ER-2 for Jumper tightening works. | 06/735, ER-06/303, Nldc-142
| 400KV Raigarh - SEL # 2 | 2013-06-09 | 11:23 | 2013-06-09 | 21:33 | [9 empty] | 10:10 | 10 | 10 | LVRD | Line kept uncharged for Voltage regulation. |  | WR-6/794, ER-6/322, Nldc-6/148
| 400KV Raigarh - SEL # 2 | 2013-06-18 | 12:55 | 2013-06-18 | 13:00 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped on overvoltage at Raigarh end. | -- | --
| 400KV Raigarh - SEL # 2 | 2013-06-18 | 13:00 | 2013-06-19 | 14:12 | [9 empty] | 1899-12-31 01:12 | 25 | 12 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-06/1666 ER-06/602 NLDC-06/269
| 400KV Raigarh - SEL # 2 | 2013-06-25 | 15:22 | 2013-06-25 | 18:53 | [9 empty] | 0.14653 | 3 | 31 | LCSD | Outage availed by ER2 for construction of LILO of 132kv Sambalpur-Raiganjpur at Kuchinda | WR-06/2067 ER-06/752 NLDC-06/310 | WR-06/2079 ER-06/759 NLDC-06/312
| 400KV Raigarh - SEL # 2 | 2013-06-28 | 4:00 | 2013-06-28 | 4:05 | [6 empty] | 0.0034722 | 0 | 5 |  |  |  | GOVC | Line tripped due to over volatge at Raigarh end. | --
| 400KV Raigarh - SEL # 2 | 2013-06-28 | 4:05 | 2013-06-28 | 19:27 | [9 empty] | 0.64028 | 15 | 22 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | WR-06/2272 NLDC-06/344, ERLDC-06/860
| Sub-Total= | [5 empty] | 4 | 0 |  | 0 | 0 |  | 0 | 10 |  | 53 | 75
| Element Availability= | [6 empty] | 4 |  |  | 0 |  |  | 0.16667 |  |  | 54.25 |  |  |  |  | 105 | 2 | 4 | 840 | 719.8333 | 210 | 151165 | 0.0055568 | 99.44%
79 | 400KV SEL -Rourkela #2
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 104.28 | 2 | 0 | 0 | 720 | 208.56 | 150163.2 | 0 | 100%
80 | 400KV Ranchi - Sipat # 1 | 2013-06-09 | 19:07 | 2013-06-09 | 19:17 | 0:10 | 0 | 10 | [9 empty] | LEFT | Line tripped due to R ph -E fault, Fault distance 416.6 Km from Sipat end. Fault in ER-2 portion. | -- | --
|  | 2013-06-09 | 19:17 | 2013-06-10 | 11:06 | [9 empty] | 0.65903 | 15 | 49 | LVRD | Line kept uncharged as per WRLDC instructions for Voltage regulation | -- | --
|  | 2013-06-17 | 1:46 | 2013-06-17 | 1:46 | 0 | 0 | 0 | [9 empty] | LART | A/R successful on Y ph - E fault. Fault location is 191 Km from Ranchi. | --
| Sub-Total= | [5 empty] | 0 | 10 |  | 0 | 0 |  | 0 | 0 |  | 15 | 49
| Element Availability= | [6 empty] | 0.16667 |  |  | 0 |  |  | 0 |  |  | 15.8167 |  |  |  |  | 405.772 | 2 | 0.16667 | 135.2573 | 720 | 811.544 | 584311.68 | 0.00023148 | 99.98%
81 | 400KV Ranchi- Sipat # 2 | 2013-06-08 | 15:36 | 2013-06-08 | 15:36 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R operated sucessfully at both ends on Rph_Earth fault. Fault location is 182km from Ranchi end | -- | --
|  | 2013-06-11 | 10:46 | 2013-06-11 | 10:46 | 0:00 | 0 | 0 | [9 empty] | LART | Line A/R operated sucessfully at both ends on Bph to Earth fault.Fault location is 31.3km from Ranchi end. | -- | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 405.772 | 2 | 0 | 0 | 720 | 811.544 | 584311.68 | 0 | 100%
82 | 220KV Korba( e) -Budipadar # 3 | 2013-06-19 | 9:10 | 2013-06-20 | 20:39 | [9 empty] | 1899-12-31 11:29 | 35 | 29 | LCSD | Outage availed for Crossing works of 765kv Raigarh(Kotra)-Raigarh(Tamnar ) line | WR-06/1640 ER-06/590 NLDC-06/263 | --
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 35 | 29
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 35.4833 |  |  |  |  | 184 | 1 | 0 | 0 | 720 | 184 | 132480 | 0 | 100%
83 | 400KV Raigarh-Jharsuguda # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.46 | 2 | 0 | 0 | 720 | 424.92 | 305942.4 | 0 | 100%
84 | 400KV Jharsuguda-Rourkela # 1
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 212.46 | 2 | 0 | 0 | 720 | 424.92 | 305942.4 | 0 | 100%
[7 empty] | 4 | 15 |  | 4 | 72 |  | 1 | 113 |  | 1512 | 592 | [7 empty] | 997.714 |  |  | 4145670.7025
[8 empty] | 4.25 |  |  | 5.2 |  |  | 2.8833 |  |  | 1521.8667 | [7 empty] | 4600.2817 |  |  | 22179960.963
[29 empty] | 0.00020741 | 99.98%
1 | ICT # 1 400/220KV at Raipur | 2013-05-28 | 0:15 | 2013-06-10 | 13:00 | 229:00 | [9 empty] | 229 | 0 | SEFT | ICT tripped on diffrential protection due to failure of Yph Bushing of 220kV side at Raipur S/S. | -- | 06/851
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 229 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 229 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
2 | ICT # 2 400/220KV at Raipur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
3 | ICT # 1 400/220KV at Mapusa
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
4 | ICT # 2 400/220KV at Mapusa
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
5 | ICT# 1 400/220KV at Boisar
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
6 | ICT# 2 400/220KV at Boisar
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
7 | ICT # 1 400/220kV at Bhatapara
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
8 | ICT # 1 400/220kV at Raigarh
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
9 | ICT # 2 400/220kV at Raigarh
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
10 | AT-1 765/400KV at Seoni
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
11 | AT-2 765/400KV at Seoni
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
12 | AT-3 765/400KV at Seoni
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
13 | ICT # 1 400/220kV at Seoni
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
14 | AT -I 765/400 KV at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
15 | AT - 2 765/400 KV at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
16 | AT - 3 765/400 KV at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
17 | AT-1 765/400KV at Bilaspur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
18 | AT-2 765/400KV at Bilaspur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
19 | ICT # 2 400/220kV at Bhatapara
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
20 | ICT # 2 400/220kV at Seoni
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
21 | ICT- 3 400/220KVat Raipur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
22 | ICT-1 400/220KV at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
23 | ICT-2 400/220KV at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
24 | ICT-3 400/220KV at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 500 | 2.5 | 0 | 0 | 720 | 1250 | 900000 | 0 | 100%
25 | ICT-1 400/220KV at Solapur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
26 | ICT-2 400/220KV at Solapur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
27 | ICT-1 400/220KV at Pune
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
28 | ICT-2 400/220KV at Pune
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
29 | ICT-3 400/220KV at Pune
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
30 | AT-3 765/400KV at Bilaspur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
31 | AT-1 765/400KV at Raigarh PS (Kotra)
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
[8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 229 | [7 empty] | 0 |  |  | 39240000
0
100%
1 | 400 KV Bus reactor at Bhadrawati
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
2 | 400 KV Bus reactor at Raipur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
3 | Bus reactor at Mapusa
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
4 | Bus reactor at Kolhapur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
5 | 400 KV Bus reactor at Raigarh
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
6 | 765 KV Bus reactor at Seoni
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
7 | Switchable Line Reactor in Raipur-Sipat # 3 line at Raipur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
8 | 400 KV Bus reactor at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
9 | Bus Reactor at Solapur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
10 | 400 KV Bus reactor at Parli
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
11 | 400 KV Bus reactor at Pune | 2013-04-02 | 10:53 | 2013-06-29 | 4:10 | [9 empty] | 676:10 | 676 | 10 | SVRD | H/T as per WRLDC instruction for voltage regulation. | 04/123 | 06/2290
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 676 | 10
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 676.1667 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
12 | 765KV Bus reactor at Wardha
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
13 | 765KV Bus reactor at Bilapsur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
14 | 765KV Bina line Switchable Line Reactor at Seoni (3x80)
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
15 | 765KV Seoni # 1 Switchable Line Reactor at Bilaspur (3x80)
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
16 | 765KV Seoni # 2 Switchable Line Reactor at Bilaspur (3x80)
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
17 | 765KV Ranchi # 1 Switchable reactor at Bilaspur
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
18 | 765KV Bus Reactor at Kotra PS
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
[7 empty] | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | [7 empty] | 0 |  |  | 7254720
[8 empty] | #VALUE! |  |  | #VALUE! |  |  | #VALUE! |  |  | #VALUE! | [10 empty] | 0
100%
[25 empty] | 3602.5677 |  |  | 64529010.2605
5.5829e-05
99.99%
SN | HVDC POLE | TRIPPING |  | RESTORATION |  | OUTAGE HOURS (HRS.MIN) | [11 empty] | CAT. CODE | DETAILED REASONS OF TRIPPING | WRLDC CODE FOR |  | TCR Pole Capacity ( 50:50%) WR & SR | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | =TCR X OH | THM | RC ( Rated Capacity) Pole Capacity ( 50:50%) WR & SR | =THM X RC | NAFM | TAFM (in Percentage)
|  | DATE | TIME | DATE | TIME | Attributed to PGCIL HRS:MIN | Attributed to PGCIL |  | Attributed to Other HRS:MIN | Attributed to Other |  | Attributed to sys conts. HRS:MIN | Attributed to sys conts. |  | Outage deemed available HRS:MIN | Outage deemed available |  |  |  | TRIPPING | CHARGING | A | B | C | D=A X C | E | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 | HVDC Pole-1 at Bhadrawati
| Sub-Total= | [5 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 0 | 0 | 720 | 250 | 180000 | 0 | 100%
2 | HVDC pole # 2 at Bhadrawati | 2013-06-25 | 9:35 | 2013-06-25 | 17:16 | 0.32014 | 7 | 41 | [9 empty] | OSPT | Outage availed for Maintenance works | WR-06/2048 SR-06/771 NLDC-06/308 | WR-06/2072 SR-06/791 NLDC-06/311
| Sub-Total= | [5 empty] | 7 | 41 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
| Element Availability= | [6 empty] | 7.6833 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 250 | 1 | 7.6833 | 1920.8333 | 720 | 250 | 180000 | 0.010671 | 98.93%
| HVDC SYSTEM TOTAL= | [5 empty] | 7 | 41 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | [7 empty] | 1920.8333 |  |  | 360000
[8 empty] | 7.6833 |  |  | 0 |  |  | 0 |  |  | 0 | [10 empty] | 0.0053356
[26 empty] | HVDC SYSTEM AVAILABILITY= |  | 99.47%
Formulas:
OUTAGE HOURS (HRS.MIN) = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Attributed to Other HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Attributed to sys conts. HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]
Outage deemed available HRS:MIN = DATEDIF([TRIPPING],[RESTORATION],"D")+[TIME]-[TIME]

## ANX-II
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees | [5 empty] | 234.25 | 9.7604
Sl. No. | Type of failures | Restoration Time (Days) |  |  | Remarks
A | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 | Insualtor Failure | Terrain Type
|  | Plain | River bed | Hilly
i | Insualtor Failure in single phase
ii | Insualtor Failure in two phases
ii | Insualtor Failure in three phases
2 | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately. | 9.7604 |  |  | Line tripped due to Bph - E fault, Fault distance 28.7 Km from Bhatapara end. On patrolling tower no.426 & 427 found collasped due to heavy wind & thunder. Line taken on ERS.
3 | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 | Tower Damage ( not collapse)
i | One arm damage
ii | Two arm damage
5 | Snapping of phase conductor
i | Conductor snapping in single phase
ii | Conductor snapping in two phases
iii | Conductor snapping in three phases
6 | Failure of Earth wire
7 | Insulator failure with conductor snapping
8 | Any other combination of failures
B | Elements of sub-station for each KV class seperately
1 | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
| Other major failures in ICTs | Single phase Unit |  | Three phase Unit
(i) Replacement of faulty bushings
| (ii) Replacement of failed/blasted bushings |  |  | 9.5417 | ICT tripped on diffrential protection due to failure of Yph Bushing of 220kV side at Raipur S/S.
(iii) Replacement of faulty tap changers
2 | Failures of Reactors
Restoration of failed Reactors