## TRAVL
POWERGRID TRANSMISSION SYSTEM AVAILABILITY FOR - DEC-2014 | [21 empty] | 744
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | WR1L1 | 220kV TARAPUR-BOISAR | 20.56 | WR-1 | [17 empty] | 100
2 | WR1L3 | 400kV KORBA-KORBA(WEST) | 14 | WR-1 | [17 empty] | 100
3 | WR1L4 | 400kV KORBA-BHILAI I | 197 | WR-1 | Earthwire | 2014-12-13 | 12:25 | 2014-12-13 | 17:21 |  |  | 0.20542 | 4.93 | 0 | 0 | 0 | 2 | N | -1.7946 | EMERGENCY OUTAGE AVAILED TO RECTIFY THE DISLOCATED EARTH WIRE AT LOC. NO. 330 |  | 99.3374 | OSFT
4 | WR1L5 | 400kV KORBA-BHILAI II | 192 | WR-1 |  | 2014-12-11 | 09:33 | 2014-12-12 | 20:02 |  |  |  | 0 | 0 | 0 | 34.48 |  |  |  | H/T FOR CVT REPLACEMENT WORKS AT NTPC,KORBA |  | 100 | OSPD
5 | WR1L6 | 400kV BHILAI-KORADI | 272 | WR-1 | [17 empty] | 100
6 | WR1L7 | 400kV KORADI-SATPURA | 149 | WR-1 | [17 empty] | 100
7 | WR1L8 | 400kV RAIPUR-BHILAI I | 13 | WR-1 |  | 2014-12-22 | 9:41 | 2014-12-22 | 20:45 |  |  |  | 0 | 0 | 0 | 11.07 |  |  |  | OUTAGE AVAILED FOR NTAMC WORKS AT RAIPUR |  | 100 | SCSD
8 | WR1L9 | 400kV BHILAI-BHADRAVATI I | 322 | WR-1 |  | 2014-12-24 | 9:19 | 2014-12-30 | 13:10 |  |  |  | 0 | 0 | 0 | 147.85 |  |  |  | H/T FOR DIVERSION OF LINE (SHIFTING OF TOWER) BY VIDHARBHA INDUSTRIAL DEV. CORPORATION. |  | 100 | OSPD
9 | WR1L10 | 400kV RAIPUR-BHADRAVATI I | 333 | WR-1 |  | 2014-12-23 | 12:11 | 2014-12-23 | 12:51 |  |  |  | 0.67 | 0 | 0 | 0 |  |  |  | H/T FOR TAKING OUT L/R AT BHADRAWATI END FOR ATTENDING OIL LEAKAGE. |  |  | OSPT
|  |  |  | WR-1 |  | 2014-12-24 | 8:33 | 2014-12-30 | 12:37 |  |  |  | 0 | 0 | 0 | 148.07 |  |  |  | H/T FOR DIVERSION OF LINE (SHIFTING OF TOWER) BY VIDHARBHA INDUSTRIAL DEV. CORPORATION. |  |  | OSPD
[6 empty] | Sub Total --> | [6 empty] | 0.67 | 0 | 0 | 148.07 | [5 empty] | 99.9099
10 | WR1L11 | 400kV RAIPUR-BHADRAVATI II | 345.55 | WR-1 | [17 empty] | 100
11 | WR1L12 | 400kV RAIPUR-BHADRAVATI III | 345.55 | WR-1 | [17 empty] | 100
12 | WR1L13 | 400kV BHADRAVATI-CHANDRAPUR I | 20 | WR-1 | [17 empty] | 100
13 | WR1L14 | 400kV BHADRAVATI-CHANDRAPUR II | 20 | WR-1 | [17 empty] | 100
14 | WR1L15 | 400kV BHADRAVATI-CHANDRAPUR III | 22.42 | WR-1 |  | 2014-12-09 | 08:38 | 2014-12-09 | 16:29 |  |  |  | 0 | 0 | 0 | 7.85 |  |  |  | OUTAGE AVAILED BY MSETCL FOR MAINTENANCE WORK AT CHANDRAPUR END. |  | 100 | OSPD
15 | WR1L16 | 400kV BHADRAVATI-CHANDRAPUR IV | 22.42 | WR-1 |  | 2014-12-10 | 08:15 | 2014-12-10 | 18:23 |  |  |  | 0 | 0 | 0 | 10.13 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR AMP WORKS |  | 100 | LVRD
16 | WR1L17 | 400kV KOLHAPUR-MAPUSA I | 150 | WR-1 |  | 2014-12-03 | 17:03 | 2014-12-04 | 06:58 |  |  |  | 0 | 0 | 0 | 13.92 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-05 | 17:10 | 2014-12-06 | 09:05 |  |  |  | 0 | 0 | 0 | 15.92 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-07 | 14:16 | 2014-12-07 | 16:00 |  |  |  | 0 | 1.73 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR ATTENDING HANGING ROPE BY M/S KEC BREAKDOWN OF OPGW DURING ONLINE STRINGING OF OPGW WIRE. THIS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. FOR REPLACEMENT OF GI EARTHWIRE BY OPGW |  |  | OMSU
|  |  |  | WR-1 |  | 2014-12-07 | 16:00 | 2014-12-08 | 07:40 |  |  |  | 0 | 0 | 0 | 15.67 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-11 | 20:08 | 2014-12-12 | 06:42 |  |  |  | 0 | 0 | 0 | 10.57 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-13 | 20:39 | 2014-12-14 | 8:20 |  |  |  | 0 | 0 | 0 | 11.68 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-14 | 16:14 | 2014-12-15 | 8:06 |  |  |  | 0 | 0 | 0 | 15.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-15 | 17:53 | 2014-12-16 | 8:32 |  |  |  | 0 | 0 | 0 | 14.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-16 | 16:24 | 2014-12-17 | 08:51 |  |  |  | 0 | 0 | 0 | 16.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-18 | 16:49 | 2014-12-19 | 9:08 |  |  |  | 0 | 0 | 0 | 16.32 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-19 | 16:14 | 2014-12-20 | 8:49 |  |  |  | 0 | 0 | 0 | 16.58 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-21 | 17:03 | 2014-12-22 | 7:12 |  |  |  | 0 | 0 | 0 | 14.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-22 | 16:53 | 2014-12-23 | 8:51 |  |  |  | 0 | 0 | 0 | 15.97 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-23 | 17:42 | 2014-12-24 | 8:34 |  |  |  | 0 | 0 | 0 | 14.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-24 | 20:41 | 2014-12-25 | 8:30 |  |  |  | 0 | 0 | 0 | 11.82 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-25 | 17:25 | 2014-12-26 | 7:14 |  |  |  | 0 | 0 | 0 | 13.82 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-26 | 16:37 | 2014-12-27 | 8:06 |  |  |  | 0 | 0 | 0 | 15.48 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-27 | 16:54 | 2014-12-28 | 8:55 |  |  |  | 0 | 0 | 0 | 16.02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-29 | 16:06 | 2014-12-31 | 8:28 |  |  |  | 0 | 0 | 0 | 40.37 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 1.73 | 0 | 290.13 | [5 empty] | 100
17 | WR1L18 | 400kV KOLHAPUR-MAPUSA II |  | WR-1 |  | 2014-11-30 | 16:41 | 2014-12-02 | 9:32 |  |  |  | 0 | 0 | 0 | 33.53 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-01 | 16:39 | 2014-12-02 | 9:17 |  |  |  | 0 | 0 | 0 | 16.63 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-02 | 17:46 | 2014-12-03 | 07:14 |  |  |  | 0 | 0 | 0 | 13.47 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-04 | 19:49 | 2014-12-05 | 7:37 |  |  |  | 0 | 0 | 0 | 11.8 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-06 | 17:17 | 2014-12-07 | 10:19 |  |  |  | 0 | 0 | 0 | 17.03 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-08 | 16:11 | 2014-12-09 | 08:52 |  |  |  | 0 | 0 | 0 | 16.68 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-09 | 19:43 | 2014-12-10 | 07:31 |  |  |  | 0 | 0 | 0 | 11.8 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-10 | 20:40 | 2014-12-11 | 09:08 |  |  |  | 0 | 0 | 0 | 12.47 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-12 | 16:46 | 2014-12-13 | 08:55 |  |  |  | 0 | 0 | 0 | 16.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-17 | 16:38 | 2014-12-18 | 7:47 |  |  |  | 0 | 0 | 0 | 15.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-20 | 17:16 | 2014-12-21 | 8:02 |  |  |  | 0 | 0 | 0 | 14.77 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-28 | 16:31 | 2014-12-29 | 7:29 |  |  |  | 0 | 0 | 0 | 14.97 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-31 | 16:15 | 2014-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 7.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 202.2 | [5 empty] | 100
18 | WR1L19 | 400kV TARAPUR-PADGHE I | 91.119 | WR-1 |  | 2014-12-16 | 8:43 | 2014-12-16 | 20:10 |  |  |  | 0 | 0 | 0 | 11.45 |  |  |  | OUTAGE WAS AVAILED BY NPCIL FOR MAINTENANCE WORK. |  |  | OSPD
|  |  |  | WR-1 |  | 2014-12-17 | 08:17 | 2014-12-17 | 19:30 |  |  |  | 0 | 0 | 0 | 11.22 |  |  |  | OTAGE AVAILED BY NPCIL FOR MAINTENANCE WORK |  |  | OSPD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 22.67 | [5 empty] | 100
19 | WR1L20 | 400kV TARAPUR-PADGHE II | 91.119 | WR-1 | [17 empty] | 100
20 | WR1L21 | 400kV BOISAR-PADGHE | 101 | WR-1 | [17 empty] | 100
21 | WR1L22 | 400kV TARAPUR-BOISAR I | 20.881 | WR-1 | [17 empty] | 100
22 | WR1L23 | 400kV TARAPUR-BOISAR II | 20.881 | WR-1 | [17 empty] | 100
23 | WR1L24 | 400kV VAPI-BOISAR | 91 | WR-1 | [17 empty] | 100
24 | WR1L25 | 400kV MAHAN-VINDHYACHAL | 19 | WR-1 | [17 empty] | 100
25 | WR1L26 | 400kV KORBA-MAHAN | 196 | WR-1 |  | 2014-12-20 | 21:27 | 2014-12-20 | 21:42 |  |  |  | 0 | 0.25 | 0 | 0 |  |  |  | TRIPPED DUE TO MALOPERATION OF RELAY ONLY AT KORBA END |  |  | SRMU
|  |  |  | WR-1 |  | 2014-12-20 | 21:42 | 2014-12-21 | 16:07 |  |  |  | 0 | 0 | 0 | 18.42 |  |  |  | LINE UNABLE TO RESTORE AFTER RELAY MALOPERATION AT KORBA END. |  |  | GOMD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.25 | 0 | 18.42 | [5 empty] | 100
26 | WR1L27 | 400kV VINDHYACHAL-KORBA II | 288.994 | WR-1 | [17 empty] | 100
27 | WR1L28 | 400kV SATPURA-SEONI | 1.507 | WR-1 | [17 empty] | 100
28 | WR1L29 | 400kV BHILAI-SEONI | 1.498 | WR-1 | [17 empty] | 100
29 | WR1L30 | 400kV BHILAI-BHATAPARA | 90.453 | WR-1 | [17 empty] | 100
30 | WR1L31 | 400kV BHATAPARA-KORBA | 123.73 | WR-1 |  | 2014-12-23 | 10:08 | 2014-12-24 | 20:03 |  |  |  | 0 | 0 | 0 | 33.92 |  |  |  | FOR CROSSING WORKS OF 800KV HVDC CHAMPA-KURUKSHETRA LINE |  | 100 | LCSD
31 | WR1L34 | 400kV RAIPUR-SIPAT I | 149.12 | WR-1 |  | 2014-12-31 | 15:20 | 2014-12-31 | 16:36 |  |  |  | 0 | 1.27 | 0 | 0 |  |  |  | LINE TRIPPED ON R-N DURING ONLINE OPGW WORK , FLR=37.8 KM FROM RAIPUR END AND FLR=105 KM FROM SIPAT END. THIS IS TAKEN UNDER MASTER COMMUNINCATION NETWROK PROJECT FOR WESTREN REGION. FOR REPLACEMENT OF GI EARTHWIRE BY OPGW |  | 100 | OMSU
32 | WR1L62 | 400KV RAIPUR-SIPAT II | 149.12 | WR-1 |  | 2014-12-29 | 10:01 | 2014-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 61.98 |  |  |  | OUTAGE AVAILED BY NTPC FOR REPLACEMENT OF BURNT/JOINTED CABLES. |  | 100 | OSPD
33 | WR1L63 | 400kV RAIPUR-SIPAT III | 162.04 | WR-1 | [17 empty] | 100
34 | WR1L64 | 765kV BILASPUR-SIPAT I | 21.507 | WR-1 | [17 empty] | 100
35 | WR1L65 | 765kV SEONI-BILASPUR I | 337.046 | WR-1 |  | 2014-12-31 | 9:29 | 2014-12-31 | 18:29 |  |  |  | 9 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORK. |  | 98.7903 | OSPT
36 | WR1L66 | 765kV BILASPUR-SIPAT II | 22.216 | WR-1 | [17 empty] | 100
37 | WR1L67 | 765kV SEONI-BILASPUR II | 338.33 | WR-1 |  | 2014-12-29 | 10:01 | 2014-12-29 | 19:05 |  |  |  | 9.07 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR AMP WORKS |  |  | OSPT
|  |  |  | WR-1 |  | 2014-12-30 | 10:00 | 2014-12-30 | 18:41 |  |  |  | 8.68 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORK. |  |  | OSPT
[6 empty] | Sub Total --> | [6 empty] | 17.75 | 0 | 0 | 0 | [5 empty] | 97.6142
38 | WR1L68 | 765kV SEONI-WARDHA I | 267.894 | WR-1 |  | 2014-12-27 | 23:30 | 2014-12-28 | 10:59 |  |  |  | 0 | 0 | 0 | 11.48 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 100 | LVRD
39 | WR1L69 | 765kV SEONI-WARDHA II | 260.763 | WR-1 |  | 2014-12-12 | 21:40 | 2014-12-16 | 12:36 |  |  |  | 0 | 0 | 0 | 86.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-18 | 20:29 | 2014-12-18 | 20:39 |  |  |  | 0 | 0 | 0.17 | 0 |  |  |  | LINE TRIPPED ON OVER VOLTAGE AT WARDHA END. |  |  | GOVC
|  |  |  | WR-1 |  | 2014-12-18 | 20:39 | 2014-12-19 | 8:33 |  |  |  | 0 | 0 | 0 | 11.9 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-21 | 23:59 | 2014-12-22 | 0:09 |  |  |  | 0 | 0 | 0.17 | 0 |  |  |  | LINE TRIPPED ON OVER VOLTAGE |  |  | GOVC
|  |  |  | WR-1 |  | 2014-12-22 | 0:09 | 2014-12-22 | 7:19 |  |  |  | 0 | 0 | 0 | 7.17 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-22 | 9:33 | 2014-12-22 | 19:00 |  |  |  | 0 | 0 | 0 | 9.45 |  |  |  | OUTAGE AVAILED FOR CROSSING WORKS OF 765 KV KORADI-AKOLA # 2 BY ADANI POWER. |  |  | LCSD
|  |  |  | WR-1 |  | 2014-12-22 | 19:00 | 2014-12-23 | 9:10 |  |  |  | 0 | 0 | 0 | 14.17 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-26 | 21:41 | 2014-12-26 | 21:51 |  |  |  | 0 | 0 | 0.17 | 0 |  |  |  | LINE TRIPPED ON OVER VOLTAGE |  |  | GOVC
|  |  |  | WR-1 |  | 2014-12-26 | 21:51 | 2014-12-27 | 9:43 |  |  |  | 0 | 0 | 0 | 11.87 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-28 | 18:10 | 2014-12-31 | 9:00 |  |  |  | 0 | 0 | 0 | 62.83 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-31 | 19:44 | 2014-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 4.27 |  |  |  | LINE WAS TRIPPED ON OVER VOLTAGE AND KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.51 | 208.59 | [5 empty] | 100
40 | WR1L70 | 400kV WARDHA-AKOLA I | 161.865 | WR-1 | [17 empty] | 100
41 | WR1L71 | 400kV WARDHA-AKOLA II | 161.865 | WR-1 |  | 2014-12-12 | 09:37 | 2014-12-12 | 18:32 |  |  |  | 0 | 0 | 0 | 8.92 |  |  |  | H/T TO AVAIL OUTAGE BY MSETCL |  | 100 | OSPD
42 | WR1L72 | 400kV AURANGABAD-AKOLA I | 289.966 | WR-1 |  | 2014-12-04 | 07:51 | 2014-12-04 | 09:22 |  |  |  | 0 | 1.52 | 0 | 0 |  |  |  | LINE TRIPPED AT AKOLA MSETCL END DUE TO OPERATION OF BUCHHOLZ RELAY OF REACTOR . |  | 100 | SREU
43 | WR1L73 | 400kV AURANGABAD-AKOLA II | 289.966 | WR-1 |  | 2014-12-09 | 10:47 | 2014-12-09 | 11:30 |  |  |  | 0.72 | 0 | 0 | 0 |  |  |  | H/T FOR TAKING L/R IN SERVICE AT AKOLA END |  |  | OMST
| #N/A |  |  | WR-1 |  | 2014-12-23 | 11:53 | 2014-12-23 | 20:03 |  |  |  | 0 | 0 | 0 | 8.17 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
| #N/A |  |  |  |  | Sub Total --> | [6 empty] | 0.72 | 0 | 0 | 8.17 | [5 empty] | 99.9032
44 | WR1L74 | 400kV BHADRAVATI-PARLI I | 378.667 | WR-1 | [17 empty] | 100
45 | WR1L76 | 400kV PARLI(POWERGRID)-PARLI(MSPTCL) I | 4.958 | WR-1 | [17 empty] | 100
46 | WR1L77 | 400kV PARLI(POWERGRID)-PARLI(MSETCL) II | 4.958 | WR-1 | [17 empty] | 100
47 | WR1L78 | 400kV KORBA-RAIPUR III | 212.83 | WR-1 | [17 empty] | 100
48 | WR1L79 | 400kV KORBA-RAIPUR IV | 212.83 | WR-1 | [17 empty] | 100
49 | WR1L80 | 400kV WARDHA-PARLI I | 336.939 | WR-1 | [17 empty] | 100
50 | WR1L81 | 400kV WARDHA-PARLI II | 336.939 | WR-1 |  | 2014-12-20 | 8:33 | 2014-12-20 | 15:00 |  |  |  | 0 | 6.45 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR STRINGING WORKS OF BROKEN EARTH WIRE BETWEEN SPAN 387 TO 390, WORK COULD NOT STARTED DUE TO SEVER ROW ISSUE AND VILLAGER MISCREANT NATURE. |  |  | OMSU
|  |  |  | WR-1 | Eartwire failure | 2014-12-20 | 15:00 | 2014-12-20 | 18:28 |  |  | 0.14458 | 3.47 | 0 | 0 | 0 | 2 | N | -1.8554 | OUTAGE CONTINUE AFTER RESOLVING ROW ISSUE FOR STRINGING WORKS OF BROKEN EARTH WIRE BETWEEN SPAN 387 TO 390 |  |  | OSPT
[6 empty] | Sub Total --> | [6 empty] | 3.47 | 6.45 | 0 | 0 | [5 empty] | 99.5295
51 | WR1L82 | 400kV KORBA-BALCO | 7.454 | WR-1 | [17 empty] | 100
52 | WR1L83 | 400kV BALCO-BIRSINGHPUR | 219.188 | WR-1 |  | 2014-12-14 | 22:53 | 2014-12-14 | 23:04 |  |  |  | 0 | 0 | 0.18 | 0 |  |  |  | LINE TRIPPED ON OVER VOLTAGE |  |  | GOVC
|  |  |  | WR-1 |  | 2014-12-14 | 23:04 | 2014-12-15 | 0:15 |  |  |  | 0 | 0 | 0 | 1.18 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.18 | 1.18 | [5 empty] | 100
53 | WR1L84 | 400kV WARDHA-MAUDA II | 123.45 | WR-1 |  | 2014-12-20 | 1:28 | 2014-12-20 | 9:41 |  |  |  | 0 | 0 | 0 | 8.22 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-28 | 0:11 | 2014-12-28 | 9:46 |  |  |  | 0 | 0 | 0 | 9.58 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 17.8 | [5 empty] | 100
54 | WR1L85 | 400kV KORBA-VANDANA | 14.768 | WR-1 | [17 empty] | 100
55 | WR1L86 | 400KV VANDANA-BIRSINGHPUR | 211.874 | WR-1 | [17 empty] | 100
56 | WR1L87 | 400KV RAIPUR-WARDHA I | 370.565 | WR-1 | [17 empty] | 100
57 | WR1L88 | 400KV RAIPUR-WARDHA II | 370.565 | WR-1 |  | 2014-12-06 | 17:12 | 2014-12-06 | 17:49 |  |  |  | 0.62 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DURING TAKING FSC INTO SERVICE AT WARDHA, DT RECEIVED AT RAIPUR END |  | 99.9167 | OMST
58 | WR1L89 | 400KV WARDHA-IEPL | 52.62 | WR-1 | [17 empty] | 100
59 | WR1L90 | 400KV IEPL-MAUDA | 70.83 | WR-1 | [17 empty] | 100
60 | WR1L91 | 400kV RAIPUR-DURG I | 21.43 | WR-1 | [17 empty] | 100
61 | WR1L92 | 400kV RAIPUR-DURG II | 21.43 | WR-1 | [17 empty] | 100
62 | WR1L93 | 400kV RAIGARH-KOTRA PS I | 6.288 | WR-1 | [17 empty] | 100
63 | WR1L94 | 400kV RAIGARH-KOTRA PS II | 6.288 | WR-1 | [17 empty] | 100
64 | WR1L35 | 765kV TAMNAR PS-KOTRA PS I | 47.986 | WR-1 | [17 empty] | 100
65 | WR1L36 | 765kV TAMNAR PS-KOTRA PS II | 47.986 | WR-1 | [17 empty] | 100
66 | WR1L37 | 765kV KOTRA PS-DURG PS I | 239.843 | WR-1 | [17 empty] | 100
67 | WR1L38 | 765kV KOTRA PS-DURG PS II | 239.843 | WR-1 |  | 2014-12-27 | 10:36 | 2014-12-28 | 16:26 |  |  |  | 0 | 0 | 0 | 29.83 |  |  |  | H/T FOR CSD COMMISSIONING |  | 100 | SCSD
68 | WR1L39 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 52.563 | WR-1 | [17 empty] | 100
69 | WR1L40 | 400kV BHADRAVATI-DHARIWAL TPP | 2.923 | WR-1 | [17 empty] | 100
70 | WR1L41 | 400kV DHARIWAL TPP-PARLI | 375.785 | WR-1 | [17 empty] | 100
71 | WR1L42 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 52.563 | WR-1 | [17 empty] | 100
72 | WR1L95 | 765KV DURG PS - KORBA(PG) II | 357.62 | WR-1 | [17 empty] | 100
73 | WR1L99 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WR-1 |  | 2014-11-30 | 20:00 | 2014-12-02 | 7:29 |  |  |  | 0 | 0 | 0 | 31.48 |  |  |  | LINE KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-18 | 17:19 | 2014-12-18 | 18:49 |  |  |  | 1.5 | 0 | 0 | 0 |  |  |  | LINE TRIPPED DUE FAILURE OF TIE CB OPERATION AT AURANGABAD(PG) , |  |  | SEFT
[6 empty] | Sub Total --> | [6 empty] | 1.5 | 0 | 0 | 31.48 | [5 empty] | 99.7984
74 | WR1L100 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WR-1 |  | 2014-12-06 | 09:47 | 2014-12-07 | 20:33 |  |  |  | 0 | 0 | 0 | 34.77 |  |  |  | H/T FOR SPARE REACTOR ERECTION WORKS AT AURANGABAD |  |  | SCSD
|  |  |  | WR-1 | Conductor Snappping | 2014-12-15 | 1:11 | 2014-12-15 | 19:49 |  |  | 1.2763 | 30.63 | 0 | 0 | 0 | 2 | N | -0.72375 | LINE TRIPPED DUE TO R PH TO Y PH FAULT. F/L= |  |  | LPPT
|  |  |  | WR-1 |  | 2014-12-21 | 10:39 | 2014-12-21 | 20:14 |  |  |  | 0 | 0 | 0 | 9.58 |  |  |  | FOR REPLACEMENT OF NGR AND COMPLETION OF BALANCE CONSTRUCTION WORKS |  |  | SCSD
[6 empty] | Sub Total --> | [6 empty] | 30.63 | 0 | 0 | 44.35 | [5 empty] | 95.8831
75 | WR1L108 | 765kV DURG PS -WARDHA_1 | 369.107 | WR-1 |  | 2014-12-17 | 11:49 | 2014-12-17 | 11:59 |  |  |  | 0 | 0 | 0.17 | 0 |  |  |  | LINE TRIPPED ON OVER VOLTAGE AT DURG END. |  |  | GOVC
|  |  |  | WR-1 |  | 2014-12-17 | 11:59 | 2014-12-18 | 11:14 |  |  |  | 0 | 0 | 0 | 23.25 |  |  |  | LINE KEPT OUT AS PER WRLDC INSTRUCTION FOR O/V |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-18 | 23:47 | 2014-12-24 | 8:56 |  |  |  | 0 | 0 | 0 | 129.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0.17 | 152.4 | [5 empty] | 100
76 | WR1L109 | 765kV DURG PS -WARDHA_2 | 369.107 | WR-1 |  | 2014-11-26 | 20:34 | 2014-12-16 | 12:00 |  |  |  | 0 | 0 | 0 | 372 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-16 | 12:00 | 2014-12-17 | 13:31 |  |  |  | 0 | 0 | 0 | 25.52 |  |  |  | LINE KEPT OUT AS PER WRLDC INSTRUCTION FOR O/V |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 397.52 | [5 empty] | 100
77 | WR1L104 | 400kV KORBA-SIPAT | 68.653 | WR-1 |  | 2014-12-03 | 13:40 | 2014-12-04 | 18:15 |  |  |  | 0 | 0 | 0 | 28.58 |  |  |  | FOR 400KV BREAKER REMOVAL, AFTER TWO DAYS BREAKER WILL BE CHARGED WITH TBC BREAKER.AVAILED BY NTPC. |  |  | OSPD
|  |  |  | WR-1 |  | 2014-12-19 | 12:02 | 2014-12-20 | 17:27 |  |  |  | 0 | 0 | 0 | 29.42 |  |  |  | H/T BY NTPC FOR MAITENANCE WORKS. |  |  | OSPD
|  |  |  | WR-1 |  | 2014-12-27 | 11:54 | 2014-12-29 | 19:22 |  |  |  | 0 | 0 | 55.47 | 0 |  |  |  | OUTAGE FOR RESTORATION OF FALLEN OF CONDUCTOR OF 765KV KORBA-JABALPUR LINE AND RESTING OVER EARTHWIRE OF 400KV KORBA-SIPAT LINE DUE TO THEFT OF WIRE " |  |  | LMAC
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 55.47 | 58 | [5 empty] | 100
78 | WR1L2 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WR-1 |  | 2014-12-06 | 10:36 | 2014-12-17 | 17:53 |  |  |  | 0 | 0 | 0 | 271.28 |  |  |  | H/T FOR CROSSING WORKS OF 765 KV RANCHI - DHARAMJAYAGARH # 2 &DIVERTION OF SE RAILWAYS FOR MCL |  | 100 | LCSD
79 | WR1L43 | 400kV RAIPUR-RAIGARH I | 217.02 | WR-1 |  | 2014-12-02 | 10:21 | 2014-12-02 | 21:18 |  |  |  | 0 | 0 | 0 | 10.95 |  |  |  | H/T FOR NTAMC WORKS AT RAIPUR SS. |  | 100 | SCSD
80 | WR1L44 | 400kV RAIPUR-KWPCL | 208.29 | WR-1 |  | 2014-12-08 | 11:21 | 2014-12-08 | 19:26 |  |  |  | 0 | 0 | 0 | 8.08 |  |  |  | FOR NTAMC WORKS AT RAIPUR END |  |  | LCSD
|  |  |  | WR-1 |  | 2014-12-18 | 14:03 | 2014-12-18 | 23:04 |  |  |  | 0 | 0 | 0 | 9.02 |  |  |  | OUTAGE AVAILED BY KWPCL FOR LINE ISOLATOR ALIGNMENT WORK |  |  | OSFD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 17.1 | [5 empty] | 100
81 | WR1L45 | 400kV RAIGARH-KWPCL | 8.73 | WR-1 |  | 2014-12-19 | 13:06 | 2014-12-19 | 19:02 |  |  |  | 0 | 0 | 0 | 5.93 |  |  |  | H/T BY KWPCL FOR MAITENANCE WORKS. |  | 100 | OSPD
82 | WR1L110 | 400kV RAIGARH-IBEUL | 114.46 | WR-1 | [17 empty] | 100
83 | WR1L111 | 400kV IBEUL-JHARSUGUDA | 114.46 | WR-1 | [17 empty] | 100
84 | WR1L49 | 400kV JHARSUGUDA-ROURKELA I | 142.448 | WR-1 | [17 empty] | 100
85 | WR1L98 | 400kV RAIGARH-ROURKELA II | 212.46 | WR-1 | [17 empty] | 100
86 | WR1L50 | 400KV RANCHI-SIPAT I | 405.772 | WR-1 |  | 2014-12-03 | 12:27 | 2014-12-03 | 12:50 |  |  |  | 0 | 0.38 | 0 | 0 |  |  |  | EMERGENCY OUATGE WAS AVAILED FOR TAKING L/R OUT AT RANCHI END.AVAILED BY ER. LINE CHARGED FROM RANCHI BUT COULD NOT BE SYNCHRONIZED AT SIPAT END AS THE LINE VOLTAGE WAS 440 KV AND BUS VOLTAGE WAS 412 KV. |  |  | OMSU
|  |  |  | WR-1 |  | 2014-12-03 | 12:50 | 2014-12-03 | 18:59 |  |  |  | 0 | 0 | 0 | 6.15 |  |  |  | LINE KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0.38 | 0 | 6.15 | [5 empty] | 100
87 | WR1L51 | 400KV RANCHI-SIPAT II | 405.772 | WR-1 |  | 2014-12-01 | 12:45 | 2014-12-02 | 20:42 |  |  |  | 0 | 0 | 0 | 31.95 |  |  |  | OUTAGE WAS AVAILED BY NTPC FOR REPLACEMENT OF LR OTI AT SIPAT END. |  | 100 | OSPD
88 | WR1L52 | 400KV RAIPUR-KSK I | 134.74 | WR-1 | [17 empty] | 100
89 | WR1L105 | KSK-RKKML | 82.248 | WR-1 |  | 2014-12-20 | 8:50 | 2014-12-20 | 18:00 |  |  |  | 0 | 0 | 0 | 9.17 |  |  |  | FOR MAINTENANCE WORKS BY RKKML |  | 100 | OSPD
90 | WR1L106 | RKKML-RAIGARH | 3.896 | WR-1 |  | 2014-12-20 | 8:51 | 2014-12-20 | 17:51 |  |  |  | 0 | 0 | 0 | 9 |  |  |  | FOR MAINTENANCE WORKS BY RKKML |  | 100 | OSPD
91 | WR1L107 | 400KV RAIPUR-KSK II | 161.82 | WR-1 | [17 empty] | 100
92 | WR1L97 | 400kV KSK-RAIGARH II | 113.389 | WR-1 | [17 empty] | 100
93 | WR1L56 | 400kV RAIGARH-JHARSUGUDA II | 110.98 | WR-1 |  | 2014-12-09 | 09:27 | 2014-12-11 | 21:23 |  |  |  | 59.93 | 0 | 0 | 0 |  |  |  | H/T FOR RECTIFICATION OF MECHANICAL INTERLOCK AT JARSUGUDABY ER # 2. |  | 91.9449 | OSPT
94 | WR1L57 | 400kV JHARSUGUDA-ROURKELA II | 143.06 | WR-1 | [17 empty] | 100
95 | WR1L46 | 400kV RAIGARH-STERLITE I | 105 | WR-1 |  | 2014-12-07 | 10:08 | 2014-12-07 | 18:40 |  |  |  | 0 | 0 | 0 | 8.53 |  |  |  | OUTAGE AVAILED BY STERLITE & ER FOR JUMPER TIGHTNING WORK. |  | 100 | OSPD
96 | WR1L47 | 400kV SEL(STERLITE)-ROURKELA-I | 104.28 | WR-1 | [17 empty] | 100
97 | WR1L60 | 765kV KORBA(PG)-BILASPUR | 90 | WR-1 | [17 empty] | 100
98 | WR1L61 | 765kV KORBA(PG)-RANCHI | 302.086 | WR-1 | [17 empty] | 100
99 | WR1L101 | 765kV KORBA(PG)- JHARSUGUDA I | 149.789 | WR-1 | [17 empty] | 100
100 | WR1L102 | 765kV KORBA(PG)- JHARSUGUDA II | 149.789 | WR-1 | [17 empty] | 100
101 | WR1T1 | 400/220kV ICT1 RAIPUR | 315 | WR-1 | [17 empty] | 100
102 | WR1T2 | 400/220kV ICT2 RAIPUR | 315 | WR-1 | [17 empty] | 100
103 | WR1T3 | 400/220kV ICT1 MAPUSA | 315 | WR-1 |  | 2014-12-22 | 10:15 | 2014-12-22 | 20:11 |  |  |  | 9.93 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR AMP WORKS |  | 98.6653 | OSPT
104 | WR1T4 | 400/220kV ICT2 MAPUSA | 315 | WR-1 |  | 2014-12-23 | 9:52 | 2014-12-23 | 19:29 |  |  |  | 0 | 0 | 0 | 9.62 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  |  | SPRD
|  |  |  | WR-1 |  | 2014-12-31 | 11:15 | 2014-12-31 | 13:34 |  |  |  | 2.32 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE AVAILED FOR ATTENDING WATER LEAKAGE IN FF SYSTEM. |  |  | OSFT
[6 empty] | Sub Total --> | [6 empty] | 2.32 | 0 | 0 | 9.62 | [5 empty] | 99.6882
105 | WR1T5 | 400/220kV ICT1 BOISAR | 315 | WR-1 |  | 2014-12-05 | 16:13 | 2014-12-05 | 16:29 |  |  |  | 0.27 | 0 | 0 | 0 |  |  |  | ICT TRIPPED DUE TO BUCHHOLZ RELAY FALSE ALARM. |  | 99.9637 | SRMT
106 | WR1T6 | 400/220kV ICT2 BOISAR | 315 | WR-1 | [17 empty] | 100
107 | WR1T7 | 400/220kV ICT1 BHATAPARA | 315 | WR-1 | [17 empty] | 100
108 | WR1T8 | 400/220kV ICT 1 RAIGARH | 315 | WR-1 | [17 empty] | 100
109 | WR1T9 | 400/220kV ICT 2 RAIGARH | 315 | WR-1 | [17 empty] | 100
110 | WR1T10 | 765/400kV ICT1 SEONI | 1500 | WR-1 | [17 empty] | 100
111 | WR1T11 | 765/400kV ICT2 SEONI | 1500 | WR-1 | [17 empty] | 100
112 | WR1T12 | 765/400kV ICT3 SEONI | 1500 | WR-1 | [17 empty] | 100
113 | WR1T13 | 400/220kV ICT1 SEONI | 315 | WR-1 | [17 empty] | 100
114 | WR1T14 | 765/400kV ICT1 WARDHA | 1500 | WR-1 | [17 empty] | 100
115 | WR1T15 | 765/400kV ICT2 WARDHA | 1500 | WR-1 | [17 empty] | 100
116 | WR1T16 | 765/400kV ICT3 WARDHA | 1500 | WR-1 | [17 empty] | 100
117 | WR1T17 | 765/400kV ICT1 BILASPUR | 1500 | WR-1 | [17 empty] | 100
118 | WR1T18 | 765/400kV ICT2 BILASPUR | 1500 | WR-1 | [17 empty] | 100
119 | WR1T19 | 400/220kV ICT2 BHATAPARA | 315 | WR-1 | [17 empty] | 100
120 | WR1T20 | 400/220kV ICT2 SEONI | 315 | WR-1 | ICT | 2014-11-05 | 17:05 | 2014-12-02 | 17:27 |  |  | 1.7271 | 41.45 | 0 | 0 | 0 | 120 | N | -118.2729 | ICT H/T FOR MAINTENANCE WORK. |  | 94.4288 | OSPT
121 | WR1T21 | 400/220kV ICT3-RAIPUR | 315 | WR-1 | [17 empty] | 100
122 | WR1T22 | 400/220kV ICT1 WARDHA | 315 | WR-1 | [17 empty] | 100
123 | WR1T23 | 400/220kV ICT2 WARDHA | 315 | WR-1 | [17 empty] | 100
124 | WR1T24 | 400/220kV ICT3 WARDHA | 500 | WR-1 | [17 empty] | 100
125 | WR1T25 | 400/220kV ICT1 SOLAPUR | 315 | WR-1 | [17 empty] | 100
126 | WR1T26 | 400/220kV ICT2 SOLAPUR | 315 | WR-1 |  | 2014-12-27 | 10:14 | 2014-12-27 | 19:11 |  |  |  | 0 | 0 | 0 | 8.95 |  |  |  | H/T FOR COMMISSIONING OF SPARE REACTOR AT SOLAPUR |  | 100 | SCSD
127 | WR1T27 | 400/220kV ICT1 PUNE | 315 | WR-1 |  | 2014-11-18 | 19:29 | 2014-12-07 | 15:48 |  |  |  | 0 | 0 | 0 | 159.8 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  | 100 | SPRD
128 | WR1T28 | 400/220kV ICT2 PUNE | 315 | WR-1 |  | 2014-12-07 | 12:24 | 2014-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 587.6 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR POWER REGULATION |  | 100 | SPRD
129 | WR1T29 | 400/220kV ICT3 PUNE | 315 | WR-1 | [17 empty] | 100
130 | WR1T30 | 765/400kV ICT3 BILASPUR | 1500 | WR-1 | [17 empty] | 100
131 | WR1T31 | 765/400kV ICT1-KOTRA PS | 1500 | WR-1 |  | 2014-12-20 | 10:59 | 2014-12-20 | 21:50 |  |  |  | 0 | 0 | 0 | 10.85 |  |  |  | H/T FOR ERECTION OF AUXILARY BUS FOR SPARE ICT |  | 100 | SCSD
132 | WR1T32 | 765/400kV ICT2-KOTRA PS | 1500 | WR-1 |  | 2014-12-22 | 11:39 | 2014-12-23 | 17:41 |  |  |  | 0 | 0 | 0 | 30.03 |  |  |  | FOR ERRECTION OF AUX. BUS AT KOTRA |  | 100 | SCSD
133 | WR1T33 | 765/400kV ICT4-KOTRA PS | 1500 | WR-1 |  | 2014-12-26 | 8:51 | 2014-12-26 | 23:55 |  |  |  | 0 | 0 | 0 | 15.07 |  |  |  | H/T FOR ERECTION OF AUXILARY BUS FOR SPARE ICT |  | 100 | SCSD
134 | WR1T34 | 400/220kV ICT3 MAPUSA | 315 | WR-1 | [17 empty] | 100
135 | WR1T35 | 765/400kV ICT1-TAMNAR(POOLING) | 1500 | WR-1 |  | 2014-12-20 | 13:28 | 2014-12-26 | 19:41 |  |  |  | 0 | 0 | 0 | 150.22 |  |  |  | H/T FOR GANTRY TOWER TH & BEAM ERECTION WORKS |  | 100 | SCSD
136 | WR1T36 | 765/400kV ICT2-TAMNAR(POOLING) | 1500 | WR-1 | [17 empty] | 100
137 | WR1T37 | 765/400kV ICT1-DURG PS | 1500 | WR-1 | [17 empty] | 100
138 | WR1T38 | 765/400kV ICT1-SOLAPUR | 1500 | WR-1 |  | 2014-12-22 | 11:10 | 2014-12-22 | 18:39 |  |  |  | 0 | 0 | 0 | 7.48 |  |  |  | FOR COMMISSIONING OF SPARE ICT UNIT & FIRE FIGHTING & AMP WORKS |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-23 | 10:55 | 2014-12-23 | 18:44 |  |  |  | 0 | 0 | 0 | 7.82 |  |  |  | FOR FIRE FIGHTING WORK & COMMISSINING OF SPARE ICT UNIT & AMP. |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-24 | 10:49 | 2014-12-24 | 18:51 |  |  |  | 0 | 0 | 0 | 8.03 |  |  |  | H/T FOR FOR FIRE FIGHTING WORK & COMMISSINING OF SPARE ICT UNIT. |  |  | SCSD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 23.33 | [5 empty] | 100
139 | WR1T39 | 765/400kV ICT2-SOLAPUR | 1500 | WR-1 |  | 2014-12-26 | 11:00 | 2014-12-26 | 19:43 |  |  |  | 0 | 0 | 0 | 8.72 |  |  |  | H/T FOR COMMISSIONING OF FIRE FIGHTING SYSTEM OF SPARE REACTOR |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-29 | 10:50 | 2014-12-29 | 18:23 |  |  |  | 0 | 0 | 0 | 7.55 |  |  |  | H/T FOR COMMISSIONING OF SPARE ICT UNIT & FIRE FIGHTING WORKS. |  |  | SCSD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 16.27 | [5 empty] | 100
140 | WR1T40 | 400/220kV ICT1-AURANGABAD | 315 | WR-1 | [17 empty] | 100
141 | WR1T41 | 400/220kV ICT2-AURANGABAD | 315 | WR-1 | [17 empty] | 100
142 | WR1T42 | 765/400kV ICT2-AURANGABAD | 1500 | WR-1 | [17 empty] | 100
143 | WR1T43 | 765/400kV ICT3-TAMNAR(POOLING) | 1500 | WR-1 | [17 empty] | 100
144 | WR1T44 | 765/400kV ICT3-KOTRA PS | 1500 | WR-1 |  | 2014-12-24 | 8:34 | 2014-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 183.43 |  |  |  | FOR ERECTION OF AUXILARY BUS FOR SPARE ICT |  | 100 | SCSD
145 | WR1T46 | 765/400kV ICT2-KORBA(PG) | 1500 | WR-1 | [17 empty] | 100
146 | WR1T45 | 765/400kV ICT1-AURANGABAD | 1500 | WR-1 | [17 empty] | 100
147 | WR1T47 | 765/400kV ICT1-KORBA(PG) | 1500 | WR-1 | [17 empty] | 100
148 | WR1R17 | 400kV BUS REACTOR BHADRAWATI | 50 | WR-1 | [17 empty] | 100
149 | WR1R18 | 400kV BUS REACTOR RAIPUR | 80 | WR-1 | [17 empty] | 100
150 | WR1R19 | 400kV BUS REACTOR MAPUSA | 50 | WR-1 | [17 empty] | 100
151 | WR1R20 | 400kV BUS REACTOR KOLHAPUR | 80 | WR-1 | [17 empty] | 100
152 | WR1R1 | 400kV BUS REACTOR RAIGARH | 63 | WR-1 | [17 empty] | 100
153 | WR1R2 | 765kV BUS REACTOR SEONI | 240 | WR-1 |  | 2014-10-29 | 11:36 | 2014-10-29 | 18:15 |  |  |  | 0 | 0 | 0 | 6.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-30 | 10:54 | 2014-12-30 | 19:25 |  |  |  | 0 | 0 | 0 | 8.52 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 15.17 | [5 empty] | 100
154 | WR1R3 | 400kV BUS REACTOR(SWITCHABLE) RAIPUR IN KORBA3 | 50 | WR-1 | [17 empty] | 100
155 | WR1R4 | 400kV BUS REACTOR WARDHA | 50 | WR-1 | [17 empty] | 100
156 | WR1R5 | 400kV BUS REACTOR, SOLAPUR | 63 | WR-1 |  | 2014-12-05 | 11:27 | 2014-12-05 | 16:41 |  |  |  | 0 | 0 | 0 | 5.23 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-06 | 10:05 | 2014-12-06 | 17:38 |  |  |  | 0 | 0 | 0 | 7.55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-21 | 11:38 | 2014-12-21 | 20:28 |  |  |  | 0 | 0 | 0 | 8.83 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-27 | 12:33 | 2014-12-27 | 18:04 |  |  |  | 0 | 0 | 0 | 5.52 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 27.13 | [5 empty] | 100
157 | WR1R6 | 400kV BUS REACTOR, PARLI | 63 | WR-1 | [17 empty] | 100
158 | WR1R7 | 400kV BUS REACTOR, PUNE | 50 | WR-1 | [17 empty] | 100
159 | WR1R8 | 765kV BUS REACTOR, WARDHA | 240 | WR-1 | [17 empty] | 100
160 | WR1R9 | 765kV BUS REACTOR- BILASPUR | 240 | WR-1 |  | 2014-09-29 | 10:21 | 2014-12-31 | 23:22 |  |  |  | 0 | 0 | 0 | 743.37 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 100 | SVRD
161 | WR1R10 | 765kV BUS REACTOR(SWITCHABLE) SEONI IN BINA | 240 | WR-1 | [17 empty] | 100
162 | WR1R11 | 765kV BUS REACTOR(SWITCHABLE) BILASPUR IN SEONI1 | 240 | WR-1 | [17 empty] | 100
163 | WR1R12 | 765kV BUS REACTOR(SWITCHABLE) BILASPUR IN SEONI2 | 240 | WR-1 | [17 empty] | 100
164 | WR1R13 | 765kV BUS REACTOR(SWITCHABLE) BILASPUR IN RANCHI | 240 | WR-1 | [17 empty] | 100
165 | WR1R14 | 765kV BUS REACTOR- KOTRA | 240 | WR-1 | [17 empty] | 100
166 | WR1R15 | 400kV BUS REACTOR- KOTRA | 80 | WR-1 | [17 empty] | 100
167 | WR1R16 | 765kV BUS REACTOR(SWITCHABLE) KOTRA IN DURG1 | 240 | WR-1 | [17 empty] | 100
168 | WR1R21 | 765kV BUS REACTOR(SWITCHABLE) KOTRA IN DURG2 | 240 | WR-1 | [17 empty] | 100
169 | WR1R22 | 765kV BUS REACTOR- TAMNAR PS | 240 | WR-1 | [17 empty] | 100
170 | WR1R23 | 765kV BUS REACTOR- DURG | 240 | WR-1 | [17 empty] | 100
171 | WR1R24 | 765kV BUS REACTOR-SOLAPUR | 240 | WR-1 |  | 2014-12-26 | 8:35 | 2014-12-26 | 19:30 |  |  |  | 0 | 0 | 0 | 10.92 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-01 | 06:47 | 2014-12-02 | 17:14 |  |  |  | 0 | 0 | 0 | 34.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-09 | 11:24 | 2014-12-09 | 19:16 |  |  |  | 0 | 0 | 0 | 7.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-11 | 14:35 | 2014-12-11 | 17:25 |  |  |  | 0 | 0 | 0 | 2.83 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-16 | 9:36 | 2014-12-16 | 17:43 |  |  |  | 0 | 0 | 0 | 8.12 |  |  |  | FF & AMP WORKS |  |  | OSPD
|  |  |  | WR-1 |  | 2014-12-19 | 10:26 | 2014-12-19 | 17:27 |  |  |  | 0 | 0 | 0 | 7.02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-29 | 6:38 | 2014-12-29 | 18:04 |  |  |  | 0 | 0 | 0 | 11.43 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 82.64 | [5 empty] | 100
172 | WR1R25 | 765kV BUS REACTOR(SWITCHABLE) SOLAPUR IN RAICHUR1 | 240 | WR-1 |  | 2014-12-17 | 09:21 | 2014-12-17 | 18:22 |  |  |  | 0 | 0 | 0 | 9.02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 100 | SVRD
173 | WR1R26 | 765kV BUS REACTOR(SWITCHABLE) SOLAPUR IN RAICHUR2 | 240 | WR-1 | [17 empty] | 100
174 | WR1R27 | 765kV BUS REACTOR(SWITCHABLE) WARDHA IN A'BAD1 | 330 | WR-1 | [17 empty] | 100
175 | WR1R28 | 765kV BUS REACTOR(SWITCHABLE) WARDHA IN A'BAD2 | 330 | WR-1 | [17 empty] | 100
176 | WR1R29 | 765kV BUS REACTOR(SWITCHABLE) SOLAPUR IN PUNE | 240 | WR-1 |  | 2014-12-08 | 12:43 | 2014-12-08 | 17:26 |  |  |  | 0 | 0 | 0 | 4.72 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-30 | 7:04 | 2014-12-30 | 17:04 |  |  |  | 0 | 0 | 0 | 10 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 14.72 | [5 empty] | 100
177 | WR1R30 | 765kV BUS REACTOR(SWITCHABLE) SEONI IN WARDHA2 | 240 | WR-1 | [17 empty] | 100
178 | WR1R31 | 765kV BUS REACTOR1 KORBA | 240 | WR-1 | [17 empty] | 100
179 | WR1R32 | 765kV BUS REACTOR2 KORBA | 240 | WR-1 |  | 2014-11-24 | 16:45 | 2014-12-31 | 23:22 |  |  |  | 0 | 0 | 0 | 743.37 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  | 100 | SVRD
180 | WR1R33 | 765kV BUS REACTOR,AURANGABAD | 240 | WR-1 |  | 2014-12-01 | 06:45 | 2014-12-02 | 18:04 |  |  |  | 0 | 0 | 0 | 35.32 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-03 | 14:49 | 2014-12-03 | 20:19 |  |  |  | 0 | 0 | 0 | 5.5 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-03 | 05:59 | 2014-12-04 | 19:57 |  |  |  | 0 | 0 | 0 | 37.97 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-05 | 08:25 | 2014-12-05 | 17:10 |  |  |  | 0 | 0 | 0 | 8.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-06 | 11:09 | 2014-12-06 | 17:36 |  |  |  | 0 | 0 | 0 | 6.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-06 | 07:15 | 2014-12-06 | 18:03 |  |  |  | 0 | 0 | 0 | 10.8 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-08 | 07:02 | 2014-12-08 | 17:19 |  |  |  | 0 | 0 | 0 | 10.28 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-09 | 06:40 | 2014-12-09 | 17:42 |  |  |  | 0 | 0 | 0 | 11.03 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-09 | 05:44 | 2014-12-10 | 18:10 |  |  |  | 0 | 0 | 0 | 36.43 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-11 | 06:54 | 2014-12-11 | 17:46 |  |  |  | 0 | 0 | 0 | 10.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-12 | 06:44 | 2014-12-12 | 16:48 |  |  |  | 0 | 0 | 0 | 10.07 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-13 | 08:13 | 2014-12-13 | 20:24 |  |  |  | 0 | 0 | 0 | 12.18 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-14 | 8:50 | 2014-12-14 | 19:00 |  |  |  | 0 | 0 | 0 | 10.17 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-15 | 6:12 | 2014-12-15 | 19:18 |  |  |  | 0 | 0 | 0 | 13.1 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-16 | 8:00 | 2014-12-16 | 20:54 |  |  |  | 0 | 0 | 0 | 12.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-17 | 06:52 | 2014-12-17 | 17:17 |  |  |  | 0 | 0 | 0 | 10.42 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-17 | 07:02 | 2014-12-18 | 17:56 |  |  |  | 0 | 0 | 0 | 34.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-19 | 8:07 | 2014-12-19 | 17:19 |  |  |  | 0 | 0 | 0 | 9.2 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-20 | 7:43 | 2014-12-20 | 18:07 |  |  |  | 0 | 0 | 0 | 10.4 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-21 | 6:56 | 2014-12-21 | 19:41 |  |  |  | 0 | 0 | 0 | 12.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-22 | 6:29 | 2014-12-22 | 17:08 |  |  |  | 0 | 0 | 0 | 10.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-23 | 6:54 | 2014-12-23 | 18:06 |  |  |  | 0 | 0 | 0 | 11.2 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-24 | 8:52 | 2014-12-24 | 18:20 |  |  |  | 0 | 0 | 0 | 9.47 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-25 | 8:46 | 2014-12-25 | 17:52 |  |  |  | 0 | 0 | 0 | 9.1 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-26 | 6:46 | 2014-12-26 | 19:20 |  |  |  | 0 | 0 | 0 | 12.57 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-27 | 6:56 | 2014-12-27 | 18:11 |  |  |  | 0 | 0 | 0 | 11.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-28 | 7:06 | 2014-12-28 | 17:12 |  |  |  | 0 | 0 | 0 | 10.1 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-29 | 6:41 | 2014-12-29 | 16:28 |  |  |  | 0 | 0 | 0 | 9.78 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-30 | 6:06 | 2014-12-30 | 17:13 |  |  |  | 0 | 0 | 0 | 11.12 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-31 | 7:01 | 2014-12-31 | 17:12 |  |  |  | 0 | 0 | 0 | 10.18 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 414.91 | [5 empty] | 100
181 | WR1R34 | 400kV BUS REACTOR,AURANGABAD | 125 | WR-1 |  | 2014-12-22 | 9:20 | 2014-12-22 | 22:17 |  |  |  | 0 | 0 | 0 | 12.95 |  |  |  | FOR COMMISSIONING OF CSD RELAY & FOR FIRE FIGHTING WORKS |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-23 | 10:27 | 2014-12-23 | 22:06 |  |  |  | 0 | 0 | 0 | 11.65 |  |  |  | FOR FIRE FIGHTING WORK & COMMISSIONING OF CSD. |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-24 | 10:12 | 2014-12-24 | 20:32 |  |  |  | 0 | 0 | 0 | 10.33 |  |  |  | H/T FOR FIRE FIGHTING WORK & COMMISSIONING OF CSD. |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-28 | 8:55 | 2014-12-28 | 17:33 |  |  |  | 0 | 0 | 0 | 8.63 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-29 | 10:44 | 2014-12-29 | 20:41 |  |  |  | 0 | 0 | 0 | 9.95 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 53.51 | [5 empty] | 100
182 | WR1R35 | 765kV BUS REACTOR(SWITCHABLE)AT DURG PS IN CHAMPA1 | 240 | WR-1 |  | 2014-12-23 | 10:43 | 2014-12-24 | 13:35 |  |  |  | 0 | 0 | 0 | 26.87 |  |  |  | H/T FOR ERRECTION WORK OF SPARE REACTOR |  | 100 | SCSD
183 | WR1R36 | BUS REACTOR AT BHATAPARA_125MVAr | 125 | WR-1 | [17 empty] | 100
184 | WR1R37 | WARDHA I_765kV SWITCHABLE REACTOR AT SEONI | 240 | WR-1 |  | 2014-12-25 | 10:12 | 2014-12-25 | 18:36 |  |  |  | 0 | 0 | 0 | 8.4 |  |  |  | H/T FOR COMMISSIONING OF FIRE FIGHTING SYSTEM |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-26 | 9:30 | 2014-12-26 | 17:20 |  |  |  | 0 | 0 | 0 | 7.83 |  |  |  | H/T FOR COMMISSIONING OF FIRE FIGHTING SYSTEM |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-27 | 10:54 | 2014-12-27 | 18:25 |  |  |  | 0 | 0 | 0 | 7.52 |  |  |  | H/T FOR CSD COMMISSIONING AND FIRE FIGHTING SYSTEM. |  |  | SCSD
|  |  |  | WR-1 |  | 2014-12-29 | 11:41 | 2014-12-29 | 18:57 |  |  |  | 0 | 0 | 0 | 7.27 |  |  |  | H/T FOR COMMISSIONING OF FIRE FIGHTING SYSTEM. |  |  | SCSD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 31.02 | [5 empty] | 100
185 | WR1R38 | BUS REACTOR AT RAIGARH_125MVAr | 125 | WR-1 | [17 empty] | 100
186 | WR1R39 | PADGHE(PG) I_765kV SWITCHABLE REACTOR AT AURANGABAD (PG) | 125 | WR-1 |  | 2014-12-05 | 6:40 | 2014-12-06 | 20:49 |  |  |  | 0 | 0 | 0 | 38.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-10 | 21:03 | 2014-12-11 | 21:57 |  |  |  | 0 | 0 | 0 | 24.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-18 | 07:38 | 2014-12-19 | 0:00 |  |  |  | 0 | 0 | 0 | 16.37 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-20 | 9:27 | 2014-12-20 | 21:50 |  |  |  | 0 | 0 | 0 | 12.38 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-21 | 9:32 | 2014-12-21 | 19:58 |  |  |  | 0 | 0 | 0 | 10.43 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-22 | 7:05 | 2014-12-22 | 17:40 |  |  |  | 0 | 0 | 0 | 10.58 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-23 | 6:56 | 2014-12-23 | 17:29 |  |  |  | 0 | 0 | 0 | 10.55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-23 | 18:55 | 2014-12-23 | 19:06 |  |  |  | 0 | 0 | 0 | 0.18 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-24 | 9:43 | 2014-12-24 | 20:42 |  |  |  | 0 | 0 | 0 | 10.98 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-25 | 7:23 | 2014-12-25 | 21:02 |  |  |  | 0 | 0 | 0 | 13.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-26 | 8:29 | 2014-12-26 | 21:50 |  |  |  | 0 | 0 | 0 | 13.35 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-27 | 9:32 | 2014-12-27 | 21:09 |  |  |  | 0 | 0 | 0 | 11.62 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-28 | 7:54 | 2014-12-28 | 17:27 |  |  |  | 0 | 0 | 0 | 9.55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-29 | 7:25 | 2014-12-29 | 20:47 |  |  |  | 0 | 0 | 0 | 13.37 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-30 | 7:55 | 2014-12-30 | 20:41 |  |  |  | 0 | 0 | 0 | 12.77 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-31 | 8:35 | 2014-12-31 | 19:55 |  |  |  | 0 | 0 | 0 | 11.33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 220.16 | [5 empty] | 100
187 | WR1R40 | PADGHE(PG) II_765kV SWITCHABLE REACTOR AT AURANGABAD (PG) | 125 | WR-1 |  | 2014-12-05 | 07:03 | 2014-12-05 | 20:55 |  |  |  | 0 | 0 | 0 | 13.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION AND USED AS BR |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-06 | 6:47 | 2014-12-07 | 19:59 |  |  |  | 0 | 0 | 0 | 37.2 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-08 | 10:47 | 2014-12-08 | 19:43 |  |  |  | 0 | 0 | 0 | 8.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-10 | 11:04 | 2014-12-12 | 18:04 |  |  |  | 0 | 0 | 0 | 55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | LVRD
|  |  |  | WR-1 |  | 2014-12-15 | 7:33 | 2014-12-15 | 18:15 |  |  |  | 0 | 0 | 0 | 10.7 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-21 | 10:51 | 2014-12-21 | 20:27 |  |  |  | 0 | 0 | 0 | 9.6 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-22 | 9:41 | 2014-12-22 | 20:10 |  |  |  | 0 | 0 | 0 | 10.48 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-23 | 18:23 | 2014-12-23 | 18:39 |  |  |  | 0 | 0 | 0 | 0.27 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-25 | 7:10 | 2014-12-25 | 23:06 |  |  |  | 0 | 0 | 0 | 15.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
|  |  |  | WR-1 |  | 2014-12-29 | 11:45 | 2014-12-29 | 17:16 |  |  |  | 0 | 0 | 0 | 5.52 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION |  |  | SVRD
[6 empty] | Sub Total --> | [6 empty] | 0 | 0 | 0 | 167.5 | [5 empty] | 100
188 | WR1R41 | WARDHA I_765kV SWITCHABLE REACTOR AT DURG (PS) | 125 | WR-1 | [17 empty] | 100
189 | WR1R42 | WARDHA II_765kV SWITCHABLE REACTOR AT DURG (PS) | 125 | WR-1 | [17 empty] | 100
190 | WR1R43 | BOISAR II_400kV SWITCHABLE REACTOR AT AURANGABAD(PG) | 80 | WR-1 | [17 empty] | 100
191 | WR1R44 | BOISAR I_400kV SWITCHABLE REACTOR AT AURANGABAD(PG) | 80 | WR-1 | [17 empty] | 100
192 | WR1R45 | BUS REACTOR -2 AT RAIPUR | 125 | WR-1 | [17 empty] | 100
193 | WR1R46 | BUS REACTOR -2_AT WARDHA_765KV | 330 | WR-1 | [17 empty] | 100
194 | WR1R47 | KARAD_400kV_SWITCHABLE_LR AT SOLAPUR | 80 | WR-1 | [17 empty] | 100
195 | WR1R48 | BUS REACTOR_400kV_125MVAR AT SEONI | 125 | WR-1 |  | 2014-12-16 | 15:42 | 2014-12-16 | 20:30 |  |  |  | 0 | 0 | 0 | 4.8 |  |  |  | FOR CSD COMMISSIONING WORKS |  | 100 | SCSD
196 | WR1R49 | PARLI-1_400kV SWITCHABLE REACTOR AT PUNE | 50 | WR-1 | [17 empty] | 100
197 | WR1R50 | PARLI-2_400kV SWITCHABLE REACTOR AT PUNE | 50 | WR-1 | [17 empty] | 100
198 | WR1R51 | AURANGABAD-1_400kV SWITCHABLE REACTOR AT PUNE | 50 | WR-1 | [17 empty] | 100
199 | WR1R52 | AURANGABAD-2_400kV SWITCHABLE REACTOR AT PUNE | 50 | WR-1 | [17 empty] | 100
200 | WR1H1 | HVDC C.PUR BACK-TO-BACK POLE I | 500 | WR-1 |  | 2014-12-11 | 08:05 | 2014-12-11 | 17:57 |  |  |  | 9.87 | 0 | 0 | 0 |  |  |  | POLE TRIPPED DUE TO DEEP IN AUXILLARY POWER SUPPLY PROVIDED BY MSEDCL, VBE GATE UNIT FAILED. |  |  | SEFT
|  |  |  | WR-1 |  | 2014-12-22 | 15:49 | 2014-12-22 | 16:17 |  |  |  | 0.47 | 0 | 0 | 0 |  |  |  | POLE TRIPPED DUE TO MALOPERATION OF BUCHLOZ RELAY OF WEST SIDE Y PHASE CONV. TRANSFORMER. |  |  | SRMT
[6 empty] | Sub Total --> | [6 empty] | 10.34 | 0 | 0 | 0 | [5 empty] | 98.6102
201 | WR1H2 | HVDC C.PUR BACK-TO-BACK POLE II | 500 | WR-1 |  | 2014-12-12 | 09:44 | 2014-12-12 | 18:42 |  |  |  | 8.97 | 0 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR AMP WORKS. |  |  | OSPT
|  |  |  | WR-1 |  | 2014-12-13 | 09:28 | 2014-12-13 | 18:17 |  |  |  | 8.82 | 0 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR AMP WORKS. |  |  | OSPT
[6 empty] | Sub Total --> | [6 empty] | 17.79 | 0 | 0 | 0 | [5 empty] | 97.6089

## Element code list
TYPE | ELEMENT NAME | CODE | LENGTH
LINE | 220kV TARAPUR-BOISAR | WR1L1 | 20.56
LINE | 220kV KORBA(EAST)-BUDDHIPADAR III | WR1L2 | 184
LINE | 400kV KORBA-KORBA(WEST) | WR1L3 | 14
LINE | 400kV KORBA-BHILAI I | WR1L4 | 197
LINE | 400kV KORBA-BHILAI II | WR1L5 | 192
LINE | 400kV BHILAI-KORADI | WR1L6 | 272
LINE | 400kV KORADI-SATPURA | WR1L7 | 149
LINE | 400kV RAIPUR-BHILAI I | WR1L8 | 13
LINE | 400kV BHILAI-BHADRAVATI I | WR1L9 | 322
LINE | 400kV RAIPUR-BHADRAVATI I | WR1L10 | 333
LINE | 400kV RAIPUR-BHADRAVATI II | WR1L11 | 345.55
LINE | 400kV RAIPUR-BHADRAVATI III | WR1L12 | 345.55
LINE | 400kV BHADRAVATI-CHANDRAPUR I | WR1L13 | 20
LINE | 400kV BHADRAVATI-CHANDRAPUR II | WR1L14 | 20
LINE | 400kV BHADRAVATI-CHANDRAPUR III | WR1L15 | 22.42
LINE | 400kV BHADRAVATI-CHANDRAPUR IV | WR1L16 | 22.42
LINE | 400kV KOLHAPUR-MAPUSA I | WR1L17 | 150
LINE | 400kV KOLHAPUR-MAPUSA II | WR1L18 | 150
LINE | 400kV TARAPUR-PADGHE I | WR1L19 | 91.119
LINE | 400kV TARAPUR-PADGHE II | WR1L20 | 91.119
LINE | 400kV BOISAR-PADGHE | WR1L21 | 101
LINE | 400kV TARAPUR-BOISAR I | WR1L22 | 20.88
LINE | 400kV TARAPUR-BOISAR II | WR1L23 | 20.88
LINE | 400kV VAPI-BOISAR | WR1L24 | 91
LINE | 400kV MAHAN-VINDHYACHAL | WR1L25 | 19
LINE | 400kV KORBA-MAHAN | WR1L26 | 196
LINE | 400kV VINDHYACHAL-KORBA II | WR1L27 | 288.994
LINE | 400kV SATPURA-SEONI | WR1L28 | 1.5
LINE | 400kV BHILAI-SEONI | WR1L29 | 1.5
LINE | 400kV BHILAI-BHATAPARA | WR1L30 | 90.453
LINE | 400kV BHATAPARA-KORBA | WR1L31 | 123.73
LINE | 400kV KORBA-PATHADI | WR1L32 | 39.536
LINE | 400KV PATHADI-SIPAT | WR1L33 | 29.117
LINE | 400kV RAIPUR-SIPAT I | WR1L34 | 149.12
LINE | 765kV TAMNAR PS-KOTRA PS I | WR1L35 | 47.97
LINE | 765kV TAMNAR PS-KOTRA PS II | WR1L36 | 47.97
LINE | 765kV KOTRA PS-DURG PS I | WR1L37 | 239.84
LINE | 765kV KOTRA PS-DURG PS II | WR1L38 | 239.84
LINE | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | WR1L39 | 52.56
LINE | 400kV BHADRAVATI-DHARIWAL TPP | WR1L40 | 18.14
LINE | 400kV DHARIWAL TPP-PARLI | WR1L41 | 391
LINE | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | WR1L42 | 52.56
LINE | 400kV RAIPUR-RAIGARH I | WR1L43 | 217.02
LINE | 400kV RAIPUR-KWPCL | WR1L44 | 203.02
LINE | 400kV RAIGARH-KWPCL | WR1L45 | 14
LINE | 400kV RAIGARH-STERLITE I | WR1L46 | 99.46
LINE | 400kV SEL(STERLITE)-ROURKELA-I | WR1L47 | 113
LINE | 400kV RAIGARH-JHARSUGUDA I | WR1L48 | 114.46
LINE | 400kV JHARSUGUDA-ROURKELA I | WR1L49 | 142.45
LINE | 400KV RANCHI-SIPAT I | WR1L50 | 405.77
LINE | 400KV RANCHI-SIPAT II | WR1L51 | 405.77
LINE | 400KV RAIPUR-KSK I | WR1L52 | 134.74
LINE | 400kV DB POWER,CHAMPA-KSK MAHANADI | WR1L53 | 85.01
LINE | 400kV RAIGARH-DB POWER,CHAMPA | WR1L54 | 1.13
LINE | 400kV RAIPUR-RAIGARH IV | WR1L55 | 220.88
LINE | 400kV RAIGARH-JHARSUGUDA II | WR1L56 | 110.98
LINE | 400kV JHARSUGUDA-ROURKELA II | WR1L57 | 143.06
LINE | 400kV RAIGARH-STERLITE II | WR1L58 | 105
LINE | 400kV SEL(STERLITE)-ROURKELA-II | WR1L59 | 104.28
LINE | 765kV KORBA(PG)-BILASPUR | WR1L60 | 90
LINE | 765kV KORBA(PG)-RANCHI | WR1L61 | 303
LINE | 400KV RAIPUR-SIPAT II | WR1L62 | 149.12
LINE | 400kV RAIPUR-SIPAT III | WR1L63 | 162.04
LINE | 765kV BILASPUR-SIPAT I | WR1L64 | 21.51
LINE | 765kV SEONI-BILASPUR I | WR1L65 | 337.05
LINE | 765kV BILASPUR-SIPAT II | WR1L66 | 22.22
LINE | 765kV SEONI-BILASPUR II | WR1L67 | 338.33
LINE | 765kV SEONI-WARDHA I | WR1L68 | 267.89
LINE | 765kV SEONI-WARDHA II | WR1L69 | 260.76
LINE | 400kV WARDHA-AKOLA I | WR1L70 | 161.87
LINE | 400kV WARDHA-AKOLA II | WR1L71 | 161.87
LINE | 400kV AURANGABAD-AKOLA I | WR1L72 | 241.23
LINE | 400kV AURANGABAD-AKOLA II | WR1L73 | 289.97
LINE | 400kV BHADRAVATI-PARLI I | WR1L74 | 378.67
LINE | 400kV BHADRAVATI-PARLI II | WR1L75 | 378.67
LINE | 400kV PARLI(POWERGRID)-PARLI(MSPTCL) I | WR1L76 | 4.96
LINE | 400kV PARLI(POWERGRID)-PARLI(MSETCL) II | WR1L77 | 4.96
LINE | 400kV KORBA-RAIPUR III | WR1L78 | 211.86
LINE | 400kV KORBA-RAIPUR IV | WR1L79 | 212.83
LINE | 400kV WARDHA-PARLI I | WR1L80 | 336.94
LINE | 400kV WARDHA-PARLI II | WR1L81 | 336.94
LINE | 400kV KORBA-BALCO | WR1L82 | 7.45
LINE | 400kV BALCO-BIRSINGHPUR | WR1L83 | 219.19
LINE | 400kV WARDHA-MAUDA II | WR1L84 | 123.84
LINE | 400kV KORBA-VANDANA | WR1L85 | 14.77
LINE | 400KV VANDANA-BIRSINGHPUR | WR1L86 | 211.87
LINE | 400KV RAIPUR-WARDHA I | WR1L87 | 370.57
LINE | 400KV RAIPUR-WARDHA II | WR1L88 | 370.57
LINE | 400KV WARDHA-IEPL | WR1L89 | 52.62
LINE | 400KV IEPL-MAUDA | WR1L90 | 70.83
LINE | 400kV RAIPUR-DURG I | WR1L91 | 21.5
LINE | 400kV RAIPUR-DURG II | WR1L92 | 21.5
LINE | 400kV RAIGARH-KOTRA PS I | WR1L93 | 6.29
LINE | 400kV RAIGARH-KOTRA PS II | WR1L94 | 6.29
LINE | 765KV DURG PS - KORBA(PG) II | WR1L95 | 357.62
LINE | 400kV KSK-RAIGARH I | WR1L96 | 86.14
LINE | 400kV KSK-RAIGARH II | WR1L97 | 113.389
LINE | 400kV RAIGARH-ROURKELA II | WR1L98 | 212.46
LINE | 765kV WARDHA - AURANGABAD(PG) I | WR1L99 | 347.577
LINE | 765kV WARDHA - AURANGABAD(PG) II | WR1L100 | 347.577
LINE | 765kV KORBA(PG)- JHARSUGUDA I | WR1L101 | 149.789
LINE | 765kV KORBA(PG)- JHARSUGUDA II | WR1L102 | 149.789
LINE | 400 KV RAIPUR KSK II | WR1L103 | 161.82
LINE | 400kV KORBA-SIPAT | WR1L104 | 68.653
LINE | KSK-RKKML | WR1L105 | 82.248
LINE | RKKML-RAIGARH | WR1L106 | 3.896
LINE | 400KV RAIPUR-KSK II | WR1L107 | 161.82
LINE | 765kV DURG PS -WARDHA_1 | WR1L108 | 369.107
LINE | 765kV DURG PS -WARDHA_2 | WR1L109 | 369.107
LINE | 400kV RAIGARH-IBEUL | WR1L110 | 94.43
LINE | 400kV IBEUL-JHARSUGUDA | WR1L111 | 20.03
ICT | 400/220kV ICT1 RAIPUR | WR1T1 | 315
ICT | 400/220kV ICT2 RAIPUR | WR1T2 | 315
ICT | 400/220kV ICT1 MAPUSA | WR1T3 | 315
ICT | 400/220kV ICT2 MAPUSA | WR1T4 | 315
ICT | 400/220kV ICT1 BOISAR | WR1T5 | 315
ICT | 400/220kV ICT2 BOISAR | WR1T6 | 315
ICT | 400/220kV ICT1 BHATAPARA | WR1T7 | 315
ICT | 400/220kV ICT 1 RAIGARH | WR1T8 | 315
ICT | 400/220kV ICT 2 RAIGARH | WR1T9 | 315
ICT | 765/400kV ICT1 SEONI | WR1T10 | 1500
ICT | 765/400kV ICT2 SEONI | WR1T11 | 1500
ICT | 765/400kV ICT3 SEONI | WR1T12 | 1500
ICT | 400/220kV ICT1 SEONI | WR1T13 | 315
ICT | 765/400kV ICT1 WARDHA | WR1T14 | 1500
ICT | 765/400kV ICT2 WARDHA | WR1T15 | 1500
ICT | 765/400kV ICT3 WARDHA | WR1T16 | 1500
ICT | 765/400kV ICT1 BILASPUR | WR1T17 | 1500
ICT | 765/400kV ICT2 BILASPUR | WR1T18 | 1500
ICT | 400/220kV ICT2 BHATAPARA | WR1T19 | 315
ICT | 400/220kV ICT2 SEONI | WR1T20 | 315
ICT | 400/220kV ICT3-RAIPUR | WR1T21 | 315
ICT | 400/220kV ICT1 WARDHA | WR1T22 | 315
ICT | 400/220kV ICT2 WARDHA | WR1T23 | 315
ICT | 400/220kV ICT3 WARDHA | WR1T24 | 500
ICT | 400/220kV ICT1 SOLAPUR | WR1T25 | 315
ICT | 400/220kV ICT2 SOLAPUR | WR1T26 | 315
ICT | 400/220kV ICT1 PUNE | WR1T27 | 315
ICT | 400/220kV ICT2 PUNE | WR1T28 | 315
ICT | 400/220kV ICT3 PUNE | WR1T29 | 315
ICT | 765/400kV ICT3 BILASPUR | WR1T30 | 1500
ICT | 765/400kV ICT1-KOTRA PS | WR1T31 | 1500
ICT | 765/400kV ICT2-KOTRA PS | WR1T32 | 1500
ICT | 765/400kV ICT4-KOTRA PS | WR1T33 | 1500
ICT | 400/220kV ICT3 MAPUSA | WR1T34 | 315
ICT | 765/400kV ICT1-TAMNAR(POOLING) | WR1T35 | 1500
ICT | 765/400kV ICT2-TAMNAR(POOLING) | WR1T36 | 1500
ICT | 765/400kV ICT1-DURG PS | WR1T37 | 1500
ICT | 765/400kV ICT1-SOLAPUR | WR1T38 | 1500
ICT | 765/400kV ICT2-SOLAPUR | WR1T39 | 1500
ICT | 400/220kV ICT1-AURANGABAD | WR1T40 | 315
ICT | 400/220kV ICT2-AURANGABAD | WR1T41 | 315
ICT | 765/400kV ICT2-AURANGABAD | WR1T42 | 1500
ICT | 765/400kV ICT3-TAMNAR(POOLING) | WR1T43 | 1500
ICT | 765/400kV ICT3-KOTRA PS | WR1T44 | 1500
ICT | 765/400kV ICT1-AURANGABAD | WR1T45 | 1500
ICT | 765/400kV ICT2-KORBA(PG) | WR1T46 | 1500
ICT | 765/400kV ICT1-KORBA(PG) | WR1T47 | 1500
BR | 400kV BUS REACTOR RAIGARH | WR1R1 | 63
BR | 765kV BUS REACTOR SEONI | WR1R2 | 240
BR | 400kV BUS REACTOR(SWITCHABLE) RAIPUR IN KORBA3 | WR1R3 | 50
BR | 400kV BUS REACTOR WARDHA | WR1R4 | 50
BR | 400kV BUS REACTOR, SOLAPUR | WR1R5 | 63
BR | 400kV BUS REACTOR, PARLI | WR1R6 | 63
BR | 400kV BUS REACTOR, PUNE | WR1R7 | 50
BR | 765kV BUS REACTOR, WARDHA | WR1R8 | 240
BR | 765kV BUS REACTOR- BILASPUR | WR1R9 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) SEONI IN BINA | WR1R10 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) BILASPUR IN SEONI1 | WR1R11 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) BILASPUR IN SEONI2 | WR1R12 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) BILASPUR IN RANCHI | WR1R13 | 240
BR | 765kV BUS REACTOR- KOTRA | WR1R14 | 240
BR | 400kV BUS REACTOR- KOTRA | WR1R15 | 80
BR | 765kV BUS REACTOR(SWITCHABLE) KOTRA IN DURG1 | WR1R16 | 240
BR | 400kV BUS REACTOR BHADRAWATI | WR1R17 | 50
BR | 400kV BUS REACTOR RAIPUR | WR1R18 | 80
BR | 400kV BUS REACTOR MAPUSA | WR1R19 | 50
BR | 400kV BUS REACTOR KOLHAPUR | WR1R20 | 80
BR | 765kV BUS REACTOR(SWITCHABLE) KOTRA IN DURG2 | WR1R21 | 240
BR | 765kV BUS REACTOR- TAMNAR PS | WR1R22 | 240
BR | 765kV BUS REACTOR- DURG | WR1R23 | 240
BR | 765kV BUS REACTOR-SOLAPUR | WR1R24 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) SOLAPUR IN RAICHUR1 | WR1R25 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) SOLAPUR IN RAICHUR2 | WR1R26 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) WARDHA IN A'BAD1 | WR1R27 | 330
BR | 765kV BUS REACTOR(SWITCHABLE) WARDHA IN A'BAD2 | WR1R28 | 330
BR | 765kV BUS REACTOR(SWITCHABLE) SOLAPUR IN PUNE | WR1R29 | 240
BR | 765kV BUS REACTOR(SWITCHABLE) SEONI IN WARDHA2 | WR1R30 | 240
BR | 765kV BUS REACTOR1 KORBA | WR1R31 | 330
BR | 765kV BUS REACTOR2 KORBA | WR1R32 | 330
BR | 765kV BUS REACTOR,AURANGABAD | WR1R33 | 240
BR | 400kV BUS REACTOR,AURANGABAD | WR1R34 | 125
BR | 765kV BUS REACTOR(SWITCHABLE)AT DURG PS IN CHAMPA1 | WR1R35 | 240
BR | BUS REACTOR AT BHATAPARA_125MVAr | WR1R36 | 125
BR | WARDHA I_765kV SWITCHABLE REACTOR AT SEONI | WR1R37 | 240
BR | BUS REACTOR AT RAIGARH_125MVAr | WR1R38 | 125
BR | PADGHE(PG) I_765kV SWITCHABLE REACTOR AT AURANGABAD (PG) | WR1R39 | 240
BR | PADGHE(PG) II_765kV SWITCHABLE REACTOR AT AURANGABAD (PG) | WR1R40 | 240
BR | WARDHA I_765kV SWITCHABLE REACTOR AT DURG (PS) | WR1R41 | 240
BR | WARDHA II_765kV SWITCHABLE REACTOR AT DURG (PS) | WR1R42 | 240
BR | BOISAR II_400kV SWITCHABLE REACTOR AT AURANGABAD(PG) | WR1R43 | 80
BR | BOISAR I_400kV SWITCHABLE REACTOR AT AURANGABAD(PG) | WR1R44 | 80
BR | BUS REACTOR -2 AT RAIPUR | WR1R45 | 125
BR | BUS REACTOR -2_AT WARDHA_765KV | WR1R46
BR | KARAD_400kV_SWITCHABLE_LR AT SOLAPUR | WR1R47 | 80
BR | BUS REACTOR_400kV_125MVAR AT SEONI | WR1R48 | 125
BR | PARLI-1_400kV SWITCHABLE REACTOR AT PUNE | WR1R49 | 50
BR | PARLI-2_400kV SWITCHABLE REACTOR AT PUNE | WR1R50 | 50
BR | AURANGABAD-1_400kV SWITCHABLE REACTOR AT PUNE | WR1R51 | 50
BR | AURANGABAD-2_400kV SWITCHABLE REACTOR AT PUNE | WR1R52 | 50
HVDC | HVDC C.PUR BACK-TO-BACK POLE I | WR1H1 | 500
HVDC | HVDC C.PUR BACK-TO-BACK POLE II | WR1H2 | 500