## DEC-16
Standard of Performance data for the month of DEC- 2016
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., WESTERN REGION - I
744
SN | Unique ID of transmission Element | NAME OF LINE/ICT | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency | Category
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | WR1_L_001 | 400kV KORBA-KORBA(WEST) | 14 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 12:35 |  |  |  | 0 | 9.25 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA. | WRLDC |  | SBBU
|  | 400kV KORBA-KORBA(WEST) Total | [10 empty] | 0 | 9.25 | 0 | 0 | [5 empty] | 100%
2 | WR1_L_002 | 400kV KORBA-BHILAI I | 197 | WRTS-I | [16 empty] | WRLDC
|  | 400kV KORBA-BHILAI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
3 | WR1_L_003 | 400kV KORBA-BHILAI II | 192 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 11:42 |  |  |  |  | 8.37 | [5 empty] | LINE TRIPPED ON Y-E FAULT, FD-215 KMS FROM BHILAI,FC-1.611 KA. BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA | WRLDC |  | SBBU
|  | 400kV KORBA-BHILAI II Total | [10 empty] | 0 | 8.37 | 0 | 0 | [5 empty] | 100%
4 | WR1_L_004 | 400kV BHILAI-KORADI | 272 | WRTS-I |  | 2016-12-13 | 16:04 | 2016-12-13 | 17:51 |  |  |  | 0 | 1.78 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO BLAST OF LPG CYLINDERS & HOUSE FIRE AL LOC. 709-710 SPAN. (B-E, FC-19.3KA,FL-1.8KM FROM KORADI) | WRLDC |  | LMAC
|  | 400kV BHILAI-KORADI Total | [10 empty] | 0 | 1.78 | 0 | 0 | [5 empty] | 100%
5 | WR1_L_005 | 400kV KORADI-SATPURA | 149 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV KORADI-SATPURA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
6 | WR1_L_006 | 400kV RAIPUR-BHILAI I | 13 | WRTS-I |  | 2016-12-16 | 10:03 | 2016-12-16 | 21:00 |  |  |  | 10.95 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | 400kV RAIPUR-BHILAI I Total | [10 empty] | 10.95 | 0 | 0 | 0 | [5 empty] | 98.53%
7 | WR1_L_007 | 400kV BHILAI-BHADRAVATI I | 322 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV BHILAI-BHADRAVATI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
8 | WR1_L_008 | 400kV RAIPUR-BHADRAVATI I | 333 | WRTS-I |  | 2016-12-09 | 13:00 | 2016-12-09 | 16:00 |  |  |  | 3 | [6 empty] | EMERGENCY OUTAGE AVAILED BY B'WATI TO ATTAND BROKEN CONDUCTOR BETWEEN Y PHASE WAVETRAP AND LINE ISOLATOR. | WRLDC |  | OSFT
|  | 400kV RAIPUR-BHADRAVATI I Total | [10 empty] | 3 | 0 | 0 | 0 | [5 empty] | 99.6%
9 | WR1_L_009 | 400kV RAIPUR-BHADRAVATI II | 345.55 | WRTS-I | [16 empty] | WRLDC
|  | 400kV RAIPUR-BHADRAVATI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
10 | WR1_L_010 | 400kV RAIPUR-BHADRAVATI III | 345.55 | WRTS-I |  | 2016-12-13 | 12:27 | 2016-12-13 | 13:44 | [5 empty] | 1.28 |  |  |  |  | LINE TRIPPED ON Y PHASE TO E FAULT, FC = 2.0KA, FD =167KM FROM RAIPUR END. LINE WAS TRIPPED DUE TO SMOKE BY A FARMER IN VICINITY OF LINE | WRLDC |  | LMAC
|  | 400kV RAIPUR-BHADRAVATI III Total | [10 empty] | 0 | 0 | 1.28 | 0 | [5 empty] | 100%
11 | WR1_L_011 | 400kV BHADRAVATI-CHANDRAPUR I | 20 | WRTS-I | [16 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
12 | WR1_L_012 | 400kV BHADRAVATI-CHANDRAPUR II | 20 | WRTS-I | [16 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
13 | WR1_L_013 | 400kV BHADRAVATI-CHANDRAPUR III | 22.42 | WRTS-I | [16 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
14 | WR1_L_014 | 400kV BHADRAVATI-CHANDRAPUR IV | 22.42 | WRTS-I | [16 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
15 | WR1_L_015 | 400kV MAHAN-VINDHYACHAL | 19 | WRTS-I | [16 empty] | WRLDC
|  | 400kV MAHAN-VINDHYACHAL Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
16 | WR1_L_016 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 12:17 |  |  |  | 0 | 8.95 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA. LINE TRIPPED ON Y-E FAULT, FD-244.41 KMS FROM MAHAN,FC-1.837 KA. | WRLDC |  | SBBU
|  | 400kV KORBA-MAHAN Total | [10 empty] | 0 | 8.95 | 0 | 0 | [5 empty] | 100%
17 | WR1_L_017 | 400kV VINDHYACHAL-KORBA II | 288.994 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 8:06 |  |  |  | 0 | 4.77 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA. | WRLDC |  | SBBU
|  | 400kV VINDHYACHAL-KORBA II Total | [10 empty] | 0 | 4.77 | 0 | 0 | [5 empty] | 100%
18 | WR1_L_018 | 400kV SATPURA-SEONI | 1.507 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV SATPURA-SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
19 | WR1_L_019 | 400kV BHILAI-SEONI | 1.498 | WRTS-I | [16 empty] | WRLDC
|  | 400kV BHILAI-SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
20 | WR1_L_020 | 400kV BHILAI-BHATAPARA | 90.453 | WRTS-I | [16 empty] | WRLDC
|  | 400kV BHILAI-BHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
21 | WR1_L_021 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I | INSULATOR DE-CAPPING | 2016-12-15 | 10:35 | 2016-12-15 | 19:00 |  |  | 0.35069 | 8.42 |  |  |  | 2 | N | -1.6493 | LINE TRIPPED DUE INSULATOR DE-CAPPING AT LOC.NO: 213. | WRLDC |  | LHWT
21 | WR1_L_021 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I |  | 2016-12-15 | 19:00 | 2016-12-16 | 13:01 | [6 empty] | 18.02 |  |  |  | LINE UNABLE TO RESTORE DUE TO PROBLEM AT NTPC KORBA END. | WRLDC |  | GOMD
21 | WR1_L_021 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 7:08 |  |  |  |  | 3.8 | [5 empty] | LINE TRIPPED DUE TO BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA. | WRLDC |  | SBBU
|  | 400kV BHATAPARA-KORBA Total | [10 empty] | 8.42 | 3.8 | 0 | 18.02 | [5 empty] | 98.86%
22 | WR1_L_022 | 400kV KORBA-SIPAT | 68.653 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV KORBA-SIPAT Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
23 | WR1_L_023 | 400kV RAIPUR-SIPAT I | 149.12 | WRTS-I | [16 empty] | WRLDC
|  | 400kV RAIPUR-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
24 | WR1_L_024 | 400KV RAIPUR-SIPAT II | 149.12 | WRTS-I | [16 empty] | WRLDC
|  | 400KV RAIPUR-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
25 | WR1_L_025 | 400kV RAIPUR-SIPAT III | 162.04 | WRTS-I
|  | 400kV RAIPUR-SIPAT III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
26 | WR1_L_026 | 765kV BILASPUR-SIPAT I | 21.507 | WRTS-I |  | 2016-12-25 | 22:54 | 2016-12-26 | 6:38 | [6 empty] | 7.33 |  |  |  | OUTAGE AVAILED BY NTPC FOR REPLACEMENT OF B PHASE CT IN TIE BAY AND FOR SAFE LIFTING OF CT AT NTPC SIPAT END | WRLDC |  | OSPD
|  | 765kV BILASPUR-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 7.33 | [5 empty] | 100%
27 | WR1_L_027 | 765kV SEONI-BILASPUR I | 337.046 | WRTS-I
|  | 765kV SEONI-BILASPUR I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
28 | WR1_L_028 | 765kV BILASPUR-SIPAT II | 22.216 | WRTS-I | [16 empty] | WRLDC
|  | 765kV BILASPUR-SIPAT II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
29 | WR1_L_029 | 765kV SEONI-BILASPUR II | 338.33 | WRTS-I | [16 empty] | WRLDC
|  | 765kV SEONI-BILASPUR II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
30 | WR1_L_030 | 765kV SEONI-WARDHA I | 267.894 | WRTS-I | [16 empty] | WRLDC
|  | 765kV SEONI-WARDHA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
31 | WR1_L_031 | 765kV SEONI-WARDHA II | 260.763 | WRTS-I
|  | 765kV SEONI-WARDHA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
32 | WR1_L_032 | 400kV WARDHA-AKOLA I | 161.865 | WRTS-I |  | 2016-12-09 | 12:19 | 2016-12-09 | 17:22 | [6 empty] | 5.05 |  |  |  | H/T FOR QUATERLY MAINTENECE WORKS BY MSETCL AKOLA. | WRLDC |  | OSPD
32 | WR1_L_032 | 400kV WARDHA-AKOLA I | 161.865 | WRTS-I |  | 2016-12-10 | 14:36 | 2016-12-10 | 19:14 |  |  |  | 4.63 | [6 empty] | EMERGENCY OUTAGE AVAILED FOR RECTIFICATION WORKS OF 02 NOS. JUMPERS OPENED AT LOC.NO.193 | WRLDC |  | OSFT
32 | WR1_L_032 | 400kV WARDHA-AKOLA I | 161.865 | WRTS-I | DECAPPING OF INSULATOR | 2016-12-30 | 15:04 | 2016-12-30 | 20:04 |  |  | 0.20833 | 5 |  |  |  | 2 | N | -1.7917 | LINE TRIPPED DUE TO Y-PH TO EARTH FAULT DUE TO DECAPPING OF INSULATOR, FD- 77.15 KM & FC- 5.3 KA AT WARDHA END | WRLDC |  | LHWT
32 | WR1_L_032 | 400kV WARDHA-AKOLA I | 161.865 | WRTS-I |  | 2016-12-30 | 20:04 | 2016-12-31 | 10:50 | [5 empty] | 14.77 |  |  |  |  | LINE RECTIFICATION WORKS HAMPERED DUE TO ROW PROBLEM AT LOCATION. | WRLDC |  | LMAC
|  | 400kV WARDHA-AKOLA I Total | [10 empty] | 9.63 | 0 | 14.77 | 5.05 | [5 empty] | 98.68%
33 | WR1_L_033 | 400kV WARDHA-AKOLA II | 161.865 | WRTS-I | [16 empty] | WRLDC
|  | 400kV WARDHA-AKOLA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
34 | WR1_L_034 | 400kV AURANGABAD (PG) -AKOLA I | 289.966 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV AURANGABAD (PG) -AKOLA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
35 | WR1_L_035 | 400kV AURANGABAD (PG) -AKOLA II | 289.966 | WRTS-I
|  | 400kV AURANGABAD (PG) -AKOLA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
36 | WR1_L_036 | 400kV BHADRAVATI-PARLI I | 378.667 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV BHADRAVATI-PARLI I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
37 | WR1_L_037 | 400kV PARLI(PG)-PARLI(MSETCL) I | 4.958 | WRTS-I | [16 empty] | WRLDC
|  | 400kV PARLI(PG)-PARLI(MSETCL) I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
38 | WR1_L_038 | 400kV PARLI(PG)-PARLI(MSETCL) II | 4.958 | WRTS-I | [16 empty] | WRLDC
|  | 400kV PARLI(PG)-PARLI(MSETCL) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
39 | WR1_L_039 | 400kV KORBA-RAIPUR III | 212.83 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV KORBA-RAIPUR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
40 | WR1_L_040 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I |  | 2016-12-12 | 10:31 | 2016-12-12 | 20:22 |  |  |  | 0 | 0 | 0 | 9.85 |  |  |  | LINE H/T FOR AMP WORKS BY NTPC KORBA. | WRLDC |  | OSPD
40 | WR1_L_040 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 7:38 |  |  |  | 0 | 4.3 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA. INDICATION Y-E FAULT, FC-1.826 KA FROM RAIPUR. | WRLDC |  | SBBU
|  | 400kV KORBA-RAIPUR IV Total | [10 empty] | 0 | 4.3 | 0 | 9.85 | [5 empty] | 100%
41 | WR1_L_041 | 400kV WARDHA-PARLI I | 336.939 | WRTS-I |  | 2016-12-15 | 23:51 | 2016-12-16 | 0:37 |  |  |  |  | 0.77 | [5 empty] | LINE TRIPPED DUE TO SNAPPING OF OPGW PILOT WIRE. OPGW WORKS TAKEN UNDER MASTER COMMUNICATION PLAN. | WRLDC |  | OMSU
|  | 400kV WARDHA-PARLI I Total | [10 empty] | 0 | 0.77 | 0 | 0 | [5 empty] | 100%
42 | WR1_L_042 | 400kV WARDHA-PARLI II | 336.939 | WRTS-I
|  | 400kV WARDHA-PARLI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
43 | WR1_L_043 | 400kV WARDHA-MAUDA II | 123.45 | WRTS-I
|  | 400kV WARDHA-MAUDA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
44 | WR1_L_044 | 400kV KORBA-VANDANA | 14.768 | WRTS-I |  | 2016-12-18 | 3:20 | 2016-12-18 | 7:42 |  |  |  |  | 4.37 | [5 empty] | LINE TRIPPED DUE TO BUS SECTIONLIZER CT BLAST AT NTPC KORBA & BUS BAR PROTECTION OPERATED IN NTPC KORBA. | WRLDC |  | SBBU
|  | 400kV KORBA-VANDANA Total | [10 empty] | 0 | 4.37 | 0 | 0 | [5 empty] | 100%
45 | WR1_L_045 | 400kV VANDANA-BIRSINGHPUR | 211.874 | WRTS-I |  | 2016-12-18 | 7:58 | 2016-12-18 | 9:04 |  |  |  | 0 | 1.1 | 0 | 6.45 |  |  |  | H/T FOR CHARGING OF KORBA - VANDANA LINE BECAUSE VANDANA NOT HAVING SYNCHRONIZATION FACILITY DUE TO BLAST OF CT AT NTPC KORBA. | WRLDC |  | OMSU
|  | 400kV VANDANA-BIRSINGHPUR Total | [10 empty] | 0 | 1.1 | 0 | 6.45 | [5 empty] | 100%
46 | WR1_L_046 | 400kV RAIPUR-WARDHA I | 370.565 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-WARDHA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
47 | WR1_L_047 | 400kV RAIPUR-WARDHA II | 370.565 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-WARDHA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
48 | WR1_L_048 | 400kV RAIPUR-DURG I | 21.43 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-DURG I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
49 | WR1_L_049 | 400kV RAIPUR-DURG II | 21.43 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-DURG II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
50 | WR1_L_050 | 400kV RAIGARH-KOTRA PS I | 6.288 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIGARH-KOTRA PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
51 | WR1_L_051 | 400kV RAIGARH-KOTRA PS II | 6.288 | WRTS-I
|  | 400kV RAIGARH-KOTRA PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
52 | WR1_L_052 | 765kV TAMNAR PS-KOTRA PS I | 47.986 | WRTS-I | [16 empty] | WRLDC
|  | 765kV TAMNAR PS-KOTRA PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
53 | WR1_L_053 | 765kV TAMNAR PS-KOTRA PS II | 47.986 | WRTS-I | [16 empty] | WRLDC
|  | 765kV TAMNAR PS-KOTRA PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
54 | WR1_L_054 | 765kV KOTRA PS-DURG PS I | 239.843 | WRTS-I |  | 2016-11-24 | 10:17 | 2016-12-09 | 10:29 |  |  |  | 0 | 0 | 0 | 202.48 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. LR CONVERTED AS BR AT BOTH ENDS. |  |  | LVRD
54 | WR1_L_054 | 765kV KOTRA PS-DURG PS I | 239.843 | WRTS-I |  | 2016-12-14 | 17:47 | 2016-12-16 | 12:44 |  |  |  | 0 | 0 | 0 | 42.95 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
54 | WR1_L_054 | 765kV KOTRA PS-DURG PS I | 239.843 | WRTS-I |  | 2016-12-23 | 20:24 | 2016-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 195.6 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
|  | 765kV KOTRA PS-DURG PS I Total | [10 empty] | 0 | 0 | 0 | 441.03 | [5 empty] | 100%
55 | WR1_L_055 | 765kV KOTRA PS-DURG PS II | 239.843 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
|  | 765kV KOTRA PS-DURG PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
56 | WR1_L_056 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 52.563 | WRTS-I | [16 empty] | WRLDC
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
57 | WR1_L_057 | 400kV BHADRAVATI-DHARIWAL TPP II | 2.923 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV BHADRAVATI-DHARIWAL TPP II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
58 | WR1_L_058 | 400kV DHARIWAL TPP-PARLI II | 375.785 | WRTS-I | [16 empty] | WRLDC
|  | 400kV DHARIWAL TPP-PARLI II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
59 | WR1_L_059 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 52.563 | WRTS-I
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
60 | WR1_L_060 | 765KV DURG PS - D'JAIGARH | 357.62 | WRTS-I |  | 2016-12-09 | 11:29 | 2016-12-14 | 19:28 |  |  |  | 0 | 0 | 0 | 127.98 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR LILO OF 765KV DURG PS - D'JAIGARH LINE AT CHAMPA AS BOTH CIRCUIT IS ON SAME TOWER. | WRLDC |  | LCSD
|  | 765KV DURG PS - D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 127.98 | [5 empty] | 100%
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-02 | 1:24 | 2016-12-02 | 5:52 |  |  |  | 0 | 0 | 0 | 4.47 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-03 | 18:39 | 2016-12-04 | 7:42 |  |  |  | 0 | 0 | 0 | 13.05 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-04 | 19:40 | 2016-12-05 | 7:56 |  |  |  | 0 | 0 | 0 | 12.27 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-05 | 21:38 | 2016-12-06 | 7:42 |  |  |  | 0 | 0 | 0 | 10.07 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-07 | 19:25 | 2016-12-08 | 7:05 |  |  |  | 0 | 0 | 0 | 11.67 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-08 | 23:59 | 2016-12-09 | 6:44 |  |  |  | 0 | 0 | 0 | 6.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-10 | 22:14 | 2016-12-11 | 6:29 |  |  |  | 0 | 0 | 0 | 8.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-11 | 19:53 | 2016-12-12 | 8:23 |  |  |  | 0 | 0 | 0 | 12.5 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-12 | 19:34 | 2016-12-13 | 7:25 |  |  |  | 0 | 0 | 0 | 11.85 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-13 | 19:45 | 2016-12-14 | 7:57 |  |  |  | 0 | 0 | 0 | 12.2 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-14 | 21:37 | 2016-12-15 | 7:27 |  |  |  | 0 | 0 | 0 | 9.83 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-15 | 20:11 | 2016-12-16 | 6:25 |  |  |  | 0 | 0 | 0 | 10.23 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-16 | 19:37 | 2016-12-17 | 6:35 |  |  |  | 0 | 0 | 0 | 10.97 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-18 | 17:14 | 2016-12-19 | 6:07 |  |  |  | 0 | 0 | 0 | 12.88 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-19 | 19:28 | 2016-12-20 | 6:53 |  |  |  | 0 | 0 | 0 | 11.42 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-21 | 17:18 | 2016-12-22 | 6:08 |  |  |  | 0 | 0 | 0 | 12.83 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-22 | 18:00 | 2016-12-23 | 9:59 |  |  |  | 0 | 0 | 0 | 15.98 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-24 | 16:21 | 2016-12-24 | 18:21 |  |  |  | 0 | 2 | 0 | 0 |  |  |  | LINE TRIPPED DUE TO HANGING OF OPGW PILOT WIRE ON B PHASE CONDUCTOR DURING OPGW WORKS. OPGW WORKS TAKEN UP UNDER MASTER COMMUNICATION PLAN. | WRLDC |  | OMSU
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-25 | 17:03 | 2016-12-25 | 17:13 | [5 empty] | 0.17 |  |  |  |  | TRIPPED ON OVER VOLTAGE PROTECTION | WRLDC |  | GOVC
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-25 | 17:13 | 2016-12-26 | 6:48 | [6 empty] | 13.58 |  |  |  | LINE KEPT UN CHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-26 | 10:01 | 2016-12-26 | 11:14 |  |  |  |  | 1.22 | [5 empty] | LINE TRIPPED ON B PH EARTH FAULT DURING OPGW WORKS.OPGW WORKS TAKEN UP UNDER MASTER COMMUNICATION PLAN. | WRLDC |  | OMSU
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-27 | 6:02 | 2016-12-27 | 6:12 | [5 empty] | 0.17 |  |  |  |  | LINE TRIPPED ON OVER VOLTAGE PROTECTION | WRLDC |  | GOVC
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-27 | 6:12 | 2016-12-27 | 6:58 | [6 empty] | 0.77 |  |  |  | LINE KEPT UNCHARGED FOR SYSTEM CONSTRANT | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-28 | 18:42 | 2016-12-29 | 7:06 | [6 empty] | 12.4 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2016-12-30 | 21:32 | 2016-12-31 | 6:36 |  |  |  | 0 | 0 | 0 | 9.07 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE | WRLDC |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) I Total | [10 empty] | 0 | 3.22 | 0.34 | 223.04 | [5 empty] | 100%
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2016-11-30 | 20:27 | 2016-12-01 | 7:15 |  |  |  | 0 | 0 | 0 | 7.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. LR CONVERTED AS BR AT WARDHA | WRLDC |  | LVRD
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2016-12-02 | 23:57 | 2016-12-03 | 6:12 |  |  |  | 0 | 0 | 0 | 6.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2016-12-24 | 19:55 | 2016-12-25 | 7:39 |  |  |  | 0 | 0 | 0 | 11.73 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2016-12-27 | 17:15 | 2016-12-28 | 7:33 |  |  |  | 0 | 0 | 0 | 14.3 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2016-12-31 | 18:06 | 2016-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 5.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) II Total | [10 empty] | 0 | 0 | 0 | 45.43 | [5 empty] | 100%
63 | WR1_L_063 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 765kV DURG PS -WARDHA_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
64 | WR1_L_064 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2016-12-03 | 16:30 | 2016-12-03 | 17:00 |  |  |  | 0 | 0 | 0 | 0.5 |  |  |  | TRIPPED DURING CHECKING OF SPARE REACTOR SELECTION SCHEME. AT DURG END | WRLDC |  | SCSD
64 | WR1_L_064 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I | CONDUCTOR SNAPPED | 2016-12-05 | 3:43 | 2016-12-05 | 16:09 |  |  | 0.51806 | 24.43 | 0 | 0 | 0 | 2 | N | -1.4819 | LINE TRIPPED ON R-PH-BPH FAULT, FC=6.0KA, FD=174.79 KM FROM WARDHA END DUE TO MIDDLE PHASE CONDUCTOR SNAPPED BETWEEN LOC. 450-451. | WRLDC |  | LHWT
|  | 765kV DURG PS -WARDHA_2 Total | [10 empty] | 24.43 | 0 | 0 | 0.5 | [5 empty] | 96.72%
65 | WR1_L_065 | 400Kv PARLI-PUNE(GIS)_1 | 9.57 | WRTS-I |  | 2016-12-02 | 9:45 | 2016-12-02 | 20:28 |  |  |  | 10.72 | 0 | 0 | 0 |  |  |  | H/T FOR LINE DEFECT RECTIFICATION WORKS | WRLDC |  | OSPT
|  | 400Kv PARLI-PUNE(GIS)_1 Total | [10 empty] | 10.72 | 0 | 0 | 0 | [5 empty] | 98.56%
66 | WR1_L_066 | 400Kv PARLI-PUNE(GIS)_2 | 9.57 | WRTS-I |  | 2016-12-03 | 9:27 | 2016-12-03 | 18:13 |  |  |  | 8.77 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400Kv PARLI-PUNE(GIS)_2 Total | [10 empty] | 8.77 | 0 | 0 | 0 |  |  |  | H/T FOR LINE DEFECT RECTIFICATION WORKS |  | 98.82% | OSPT
67 | WR1_L_067 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 9.978 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC |  | OMSU
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
68 | WR1_L_068 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 9.978 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-01 | 0:41 | 2016-12-01 | 6:37 |  |  |  | 0 | 0 | 0 | 5.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-01 | 21:58 | 2016-12-02 | 5:51 |  |  |  | 0 | 0 | 0 | 7.88 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-02 | 21:51 | 2016-12-03 | 5:30 |  |  |  | 0 | 0 | 0 | 7.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-04 | 1:18 | 2016-12-04 | 7:43 |  |  |  | 0 | 0 | 0 | 6.42 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-04 | 20:13 | 2016-12-05 | 6:51 |  |  |  | 0 | 0 | 0 | 10.63 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-06 | 0:16 | 2016-12-06 | 6:20 |  |  |  | 0 | 0 | 0 | 6.07 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-06 | 22:16 | 2016-12-07 | 7:02 |  |  |  | 0 | 0 | 0 | 8.77 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-07 | 23:54 | 2016-12-08 | 6:37 |  |  |  | 0 | 0 | 0 | 6.72 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-09 | 0:20 | 2016-12-09 | 6:50 |  |  |  | 0 | 0 | 0 | 6.5 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-10 | 0:15 | 2016-12-10 | 6:06 |  |  |  | 0 | 0 | 0 | 5.85 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-10 | 21:53 | 2016-12-11 | 5:47 |  |  |  | 0 | 0 | 0 | 7.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-11 | 23:46 | 2016-12-12 | 5:56 |  |  |  | 0 | 0 | 0 | 6.17 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-12 | 21:40 | 2016-12-13 | 6:50 |  |  |  | 0 | 0 | 0 | 9.17 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-13 | 22:15 | 2016-12-14 | 7:02 |  |  |  | 0 | 0 | 0 | 8.78 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-14 | 21:38 | 2016-12-15 | 6:58 |  |  |  | 0 | 0 | 0 | 9.33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-16 | 0:03 | 2016-12-16 | 6:45 |  |  |  | 0 | 0 | 0 | 6.7 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-16 | 20:11 | 2016-12-17 | 6:10 |  |  |  | 0 | 0 | 0 | 9.98 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-17 | 21:15 | 2016-12-18 | 6:16 |  |  |  | 0 | 0 | 0 | 9.02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-18 | 20:05 | 2016-12-19 | 5:41 |  |  |  | 0 | 0 | 0 | 9.6 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-19 | 21:22 | 2016-12-20 | 6:56 |  |  |  | 0 | 0 | 0 | 9.57 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-21 | 20:51 | 2016-12-22 | 6:05 |  |  |  | 0 | 0 | 0 | 9.23 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-22 | 20:54 | 2016-12-23 | 6:46 |  |  |  | 0 | 0 | 0 | 9.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-23 | 20:54 | 2016-12-24 | 7:07 |  |  |  | 0 | 0 | 0 | 10.22 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-24 | 19:55 | 2016-12-25 | 7:02 |  |  |  | 0 | 0 | 0 | 11.12 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-25 | 17:15 | 2016-12-26 | 5:30 |  |  |  | 0 | 0 | 0 | 12.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-26 | 20:17 | 2016-12-27 | 5:32 |  |  |  | 0 | 0 | 0 | 9.25 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-27 | 20:36 | 2016-12-28 | 6:28 |  |  |  | 0 | 0 | 0 | 9.87 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-28 | 20:55 | 2016-12-29 | 7:07 |  |  |  | 0 | 0 | 0 | 10.2 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-29 | 20:07 | 2016-12-30 | 6:05 |  |  |  | 0 | 0 | 0 | 9.97 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-30 | 21:10 | 2016-12-31 | 6:23 |  |  |  | 0 | 0 | 0 | 9.22 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2016-12-31 | 22:04 | 2016-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 1.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
|  | 765kV PUNE(GIS)-SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 261.77 | [5 empty] | 100%
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-01 | 19:47 | 2016-12-02 | 5:32 |  |  |  | 0 | 0 | 0 | 9.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-06 | 22:07 | 2016-12-07 | 7:12 |  |  |  | 0 | 0 | 0 | 9.08 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-09 | 22:11 | 2016-12-10 | 5:51 |  |  |  | 0 | 0 | 0 | 7.66 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | GOVC
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-12 | 1:39 | 2016-12-12 | 6:01 |  |  |  | 0 | 0 | 0 | 4.36 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-12 | 21:44 | 2016-12-13 | 6:54 |  |  |  | 0 | 0 | 0 | 9.16 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-17 | 18:13 | 2016-12-18 | 7:05 |  |  |  | 0 | 0 | 0 | 12.86 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-23 | 19:10 | 2016-12-24 | 7:50 |  |  |  | 0 | 0 | 0 | 12.66 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-26 | 17:37 | 2016-12-27 | 5:50 |  |  |  | 0 | 0 | 0 | 12.21 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-29 | 17:30 | 2016-12-30 | 8:55 |  |  |  | 0 | 0 | 0 | 15.41 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2016-12-30 | 18:15 | 2016-12-31 | 0:08 |  |  |  | 0 | 0 | 0 | 5.88 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) III Total | [10 empty] | 0 | 0 | 0 | 99.03 | [5 empty] | 100%
71 | WR1_L_071 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2016-12-02 | 21:12 | 2016-12-03 | 5:01 |  |  |  | 0 | 0 | 0 | 7.81 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) IV Total | [10 empty] | 0 | 0 | 0 | 7.81 | [5 empty] | 100%
72 | WR1_L_072 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | 11.2 | WRTS-I | [16 empty] | WRLDC
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
73 | WR1_L_073 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | 11.2 | WRTS-I | [16 empty] | WRLDC
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
74 | WR1_L_074 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I |  | 2016-12-16 | 17:28 | 2016-12-24 | 7:10 |  |  |  | 0 | 0 | 0 | 181.7 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR LILO OF 765KV DURG PS - D'JAIGARH LINE AT CHAMPA AS BOTH CIRCUIT IS ON SAME TOWER. | WRLDC |  | LCSD
|  | 765kV DURG PS- CHAMPA_1 Total | [10 empty] | 0 | 0 | 0 | 181.7 | [5 empty] | 100%
75 | WR1_L_075 | 765kV CHAMPA- KOTRA PS | 96.33 | WRTS-I |  | 2016-12-09 | 11:03 | 2016-12-14 | 15:42 |  |  |  | 0 | 0 | 0 | 124.48 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR LILO OF 765KV DURG PS - D'JAIGARH LINE AT CHAMPA AS BOTH CIRCUIT IS ON SAME TOWER. | WRLDC |  | LCSD
|  | 765kV CHAMPA- KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 124.48 | [5 empty] | 100%
76 | WR1_L_076 | 765kV AURANGABAD(PG)-SOLAPUR I | 279.57 | WRTS-I |  | 2016-12-13 | 12:13 | 2016-12-13 | 13:28 |  |  |  | 0 | 1.25 | 0 | 0 |  |  |  | H/T REMOVING BALLOON OF POLITICAL PARTIES STRUCK UP ON THE TOWER AT LOC. NO. 102-103. | WRLDC |  | LMAC
76 | WR1_L_076 | 765kV AURANGABAD(PG)-SOLAPUR I | 279.57 | WRTS-I |  | 2016-12-30 | 7:54 | 2016-12-30 | 20:05 |  |  |  | 12.18 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
76 | WR1_L_076 | 765kV AURANGABAD(PG)-SOLAPUR I | 279.57 | WRTS-I |  | 2016-12-30 | 20:05 | 2016-12-30 | 21:42 |  |  |  | 0 | 0 | 0 | 1.61 |  |  |  | KEPT UNCHARGED AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
|  | 765kV AURANGABAD(PG)-SOLAPUR I Total | [10 empty] | 12.18 | 1.25 | 0 | 1.61 | [5 empty] | 98.36%
77 | WR1_L_077 | 765kV AURANGABAD(PG)-SOLAPUR II | 279.57 | WRTS-I |  | 2016-12-23 | 6:07 | 2016-12-23 | 9:11 |  |  |  | 3.06 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE AVAILED FOR ATTENDING Y PH 2 NOS. SUB CONDUCTORS OPEN AND HANGING OF JUMPER | WRLDC |  | OSFT
| WR1_L_077 | 765kV AURANGABAD(PG)-SOLAPUR II | 279.57 | WRTS-I |  | 2016-12-29 | 9:16 | 2016-12-29 | 19:54 |  |  |  | 10.63 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | 765kV AURANGABAD(PG)-SOLAPUR II Total | [10 empty] | 13.69 | 0 | 0 | 0 | [5 empty] | 98.16%
78 | WR1_L_078 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I
|  | 220kV KORBA(EAST)-BUDDHIPADAR III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
79 | WR1_L_079 | 400kV RAIPUR-RAIGARH I | 217.02 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-RAIGARH I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
80 | WR1_L_080 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I
|  | 400kV RAIGARH-ROURKELA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
81 | WR1_L_081 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I
|  | 400kV RAIGARH-IBEUL I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
82 | WR1_L_082 | 400kV IBEUL-JHARSUGUDA I | 20.03 | WRTS-I | [16 empty] | WRLDC
|  | 400kV IBEUL-JHARSUGUDA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
83 | WR1_L_083 | 400kV JHARSUGUDA-ROURKELA I | 142.448 | WRTS-I | [16 empty] | WRLDC
|  | 400kV JHARSUGUDA-ROURKELA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
84 | WR1_L_084 | 400kV RANCHI-SIPAT I | 405.772 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RANCHI-SIPAT I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
85 | WR1_L_085 | 400kV RANCHI-SIPAT II | 405.772 | WRTS-I |  | 2016-12-19 | 16:24 | 2016-12-19 | 17:00 |  |  |  | 0.6 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED BY ER2 FOR FSC TESTING AT RANCHI END | WRLDC |  | OSFT
|  | 400kV RANCHI-SIPAT II Total | [10 empty] | 0.6 | 0 | 0 | 0 | [5 empty] | 99.92%
86 | WR1_L_086 | 400kV RAIPUR-KSK III | 134.74 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-KSK III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
87 | WR1_L_087 | 400kV KSK-RKKML III | 82.248 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV KSK-RKKML III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
88 | WR1_L_088 | 400kV RKKML-RAIGARH III | 3.896 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RKKML-RAIGARH III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
89 | WR1_L_089 | 400kV RAIPUR-KSK IV | 161.82 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-KSK IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
90 | WR1_L_090 | 400kV KSK-RAIGARH IV | 113.389 | WRTS-I | [16 empty] | WRLDC
|  | 400kV KSK-RAIGARH IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
91 | WR1_L_091 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIGARH-JHARSUGUDA III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
92 | WR1_L_092 | 400kV JHARSUGUDA-ROURKELA III | 143.06 | WRTS-I | [16 empty] | WRLDC
|  | 400kV JHARSUGUDA-ROURKELA III Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
93 | WR1_L_093 | 400kV RAIGARH-STERLITE IV | 105 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIGARH-STERLITE IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
94 | WR1_L_094 | 400kV STERLITE-ROURKELA IV | 104.28 | WRTS-I | [16 empty] | WRLDC
|  | 400kV STERLITE-ROURKELA IV Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
95 | WR1_L_095 | 765kV D'JAIGARH-BILASPUR | 90 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 765kV D'JAIGARH-BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
96 | WR1_L_096 | 765kV D'JAIGARH-RANCHI I | 303 | WRTS-I |  | 2016-12-13 | 2:21 | 2016-12-13 | 2:31 |  |  |  | 12.16 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON AT DHARAMJAYGARH DUE TO LOOSE Y-PHASE LINK OF CVT SECONDARY CIRCUIT. | WRLDC |  | OMST
| WR1_L_096 | 765kV D'JAIGARH-RANCHI I | 303 | WRTS-I |  | 2016-12-13 | 2:31 | 2016-12-13 | 6:20 |  |  |  | 0 | 0 | 0 | 3.82 |  |  |  | LINE KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
| WR1_L_096 | 765kV D'JAIGARH-RANCHI I | 303 | WRTS-I |  | 2016-12-14 | 2:25 | 2016-12-14 | 2:35 |  |  |  | 12.16 | 0 | 0 | 0 |  |  |  | LINE TRIPPED ON AT DHARAMJAYGARH DUE TO LOOSE Y-PHASE LINK OF CVT SECONDARY CIRCUIT. |  |  | OMST
96 | WR1_L_096 | 765kV D'JAIGARH-RANCHI I | 303 | WRTS-I |  | 2016-12-14 | 2:35 | 2016-12-14 | 6:41 |  |  |  | 0 | 0 | 0 | 4.1 |  |  |  | LINE KEPT OUT AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
|  | 765kV D'JAIGARH-RANCHI I Total | [10 empty] | 24.32 | 0 | 0 | 7.92 | [5 empty] | 96.73%
97 | WR1_L_097 | 765kV D'JAIGARH- JHARSUGUDA I | 149.789 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | WRLDC
|  | 765kV D'JAIGARH- JHARSUGUDA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
98 | WR1_L_098 | 765kV D'JAIGARH- JHARSUGUDA II | 149.789 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  | OUTAGE AVAILED FOR CT & PT CONNECTION TO PMU PANEL AT D'JAIGARH | WRLDC
|  | 765kV D'JAIGARH- JHARSUGUDA II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
99 | WR1_L_099 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I | 39.383 | WRTS-I |  | 2016-12-20 | 9:26 | 2016-12-21 | 18:31 |  |  |  | 0 | 0 | 0 | 33.08 |  |  |  | LINE H/T FOR ERECTION OF CROSS ARM MEMBERS AT LOCATION MC05 (OLD 3/1) OF MULTI CIRCUIT LINE. | WRLDC |  | LCSD
99 | WR1_L_099 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I | 39.383 | WRTS-I |  | 2016-12-21 | 18:31 | 2016-12-22 | 6:21 |  |  |  | 0 | 0 | 0 | 11.83 |  |  |  | LINE KEPT UNCHARGED BY WRLDC FOR SYSTEM CONSTRAINT | WRLDC |  | LVRD
|  | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I Total | [10 empty] | 0 | 0 | 0 | 44.91 | [5 empty] | 100%
100 | WR1_L_100 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II | 39.383 | WRTS-I
|  | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-01 | 18:15 | 2016-12-02 | 7:16 |  |  |  | 0 | 0 | 0 | 13.02 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-03 | 18:20 | 2016-12-04 | 7:03 |  |  |  | 0 | 0 | 0 | 12.71 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-04 | 18:13 | 2016-12-05 | 7:56 |  |  |  | 0 | 0 | 0 | 13.71 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-05 | 17:16 | 2016-12-06 | 8:33 |  |  |  | 0 | 0 | 0 | 15.28 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-07 | 17:38 | 2016-12-08 | 7:18 |  |  |  | 0 | 0 | 0 | 13.66 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-09 | 18:06 | 2016-12-10 | 6:44 |  |  |  | 0 | 0 | 0 | 12.63 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-11 | 17:38 | 2016-12-12 | 8:24 |  |  |  | 0 | 0 | 0 | 14.76 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-13 | 16:15 | 2016-12-13 | 18:01 |  |  |  | 1.76 | 0 | 0 | 0 |  |  |  | H/T TO ATTEND OIL LEAKAGE FROM CVT AT KOLHAPUR | WRLDC |  | OSFT
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-13 | 18:01 | 2016-12-15 | 9:15 |  |  |  | 0 | 0 | 0 | 39.23 |  |  |  | LINE KEPT UNCHARGED FOR VR AS PER WRLDC INSTRUCTIONS | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-15 | 18:14 | 2016-12-16 | 7:33 |  |  |  | 0 | 0 | 0 | 13.31 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-17 | 16:48 | 2016-12-19 | 7:39 |  |  |  | 0 | 0 | 0 | 38.85 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-22 | 16:37 | 2016-12-23 | 9:22 |  |  |  | 0 | 0 | 0 | 16.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-24 | 16:43 | 2016-12-26 | 10:16 |  |  |  | 0 | 0 | 0 | 41.55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-27 | 16:12 | 2016-12-28 | 7:18 |  |  |  | 0 | 0 | 0 | 15.1 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-28 | 17:25 | 2016-12-29 | 8:42 |  |  |  | 0 | 0 | 0 | 15.28 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
101 | WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I | 156.039 | WRTS-I |  | 2016-12-30 | 16:53 | 2016-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 31.11 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
|  | 400kV KOLHAPUR (GIS)-MAPUSA I Total | [10 empty] | 1.76 | 0 | 0 | 306.95 | [5 empty] | 99.76%
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-11-30 | 18:32 | 2016-12-01 | 6:39 |  |  |  | 0 | 0 | 0 | 6.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-02 | 18:18 | 2016-12-03 | 6:45 |  |  |  | 0 | 0 | 0 | 12.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-06 | 16:41 | 2016-12-07 | 10:39 |  |  |  | 0 | 0 | 0 | 17.96 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-08 | 17:35 | 2016-12-09 | 7:10 |  |  |  | 0 | 0 | 0 | 13.58 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-10 | 18:22 | 2016-12-11 | 7:04 |  |  |  | 0 | 0 | 0 | 12.7 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-12 | 18:14 | 2016-12-13 | 7:49 |  |  |  | 0 | 0 | 0 | 13.58 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-16 | 17:19 | 2016-12-17 | 5:50 |  |  |  | 0 | 0 | 0 | 12.51 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-19 | 16:42 | 2016-12-22 | 8:38 |  |  |  | 0 | 0 | 0 | 63.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-23 | 16:17 | 2016-12-24 | 6:53 |  |  |  | 0 | 0 | 0 | 14.6 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. |  |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-26 | 17:09 | 2016-12-27 | 7:52 |  |  |  | 0 | 0 | 0 | 14.71 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-29 | 16:44 | 2016-12-30 | 8:11 |  |  |  | 0 | 0 | 0 | 15.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2016-12-31 | 16:36 | 2016-12-31 | 24:00 |  |  |  | 0 | 0 | 0 | 7.4 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | LVRD
|  | 400kV KOLHAPUR (GIS)-MAPUSA II Total | [10 empty] | 0 | 0 | 0 | 205.52 | [5 empty] | 100%
103 | WR1_L_103 | 400kV WARDHA-MAUDA I | 123.45 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC |  | 0
|  | 400kV WARDHA-MAUDA I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
104 | WR1_L_104 | 765kV D'JAIGARH-RANCHI II | 354 | WRTS-I |  | 2016-12-03 | 10:46 | 2016-12-03 | 20:35 |  |  |  | 9.82 | 1.2 | 0 | 0 |  |  |  | LINE OUTAGE AVAILED BY ER. | WRLDC |  | OSPT
|  | 765kV D'JAIGARH-RANCHI II Total | [10 empty] | 9.82 | 1.2 | 0 | 0 | [5 empty] | 98.68%
105 | WR1_L_105 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 | 14.373 | WRTS-I | [16 empty] | WRLDC
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
106 | WR1_L_106 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 | 14.373 | WRTS-I | [16 empty] | WRLDC
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
107 | WR1_L_107 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I | 14.387 | WRTS-I |  | 2016-12-03 | 10:15 | 2016-12-03 | 18:57 |  |  |  | 8.7 | 0 | 0 | 0 |  |  |  | H/T FOR LINE DEFECT RECTIFICATION WORKS | WRLDC |  | OSPT
|  | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I Total | [10 empty] | 8.7 | 0 | 0 | 0 | [5 empty] | 98.83%
108 | WR1_L_108 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II | 14.387 | WRTS-I |  | 2016-12-02 | 9:16 | 2016-12-02 | 20:11 |  |  |  | 10.92 | 0 | 0 | 0 |  |  |  | H/T FOR LINE DEFECT RECTIFICATION WORKS | WRLDC |  | OSPT
|  | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II Total | [10 empty] | 10.92 | 0 | 0 | 0 | [5 empty] | 98.53%
109 | WR1_L_109 | 400kV RAIPUR-RAIGARH II | 217.02 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV RAIPUR-RAIGARH II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
110 | WR1_L_110 | 400kV LARA(NTPC)-KOTRA PS I | 17.999 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | 400kV LARA(NTPC)-KOTRA PS I Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
111 | WR1_L_111 | 400kV LARA(NTPC)-KOTRA PS II | 17.999 | WRTS-I | [16 empty] | WRLDC
|  | 400kV LARA(NTPC)-KOTRA PS II Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
112 | WR1_L_112 | 400kV KORBA-BIRSINGHPUR | 226.642 | WRTS-I |  | 2016-12-18 | 19:07 | 2016-12-18 | 19:17 |  |  |  | 0 | 0.16 | 0 | 0 |  |  |  | LINE TRIPPED ONLY AT NTPC KORBA END DUE TO GROUP RELAY OPERATED. LINE HANGING FROM BIRSINGHPUR END. BUS SECTIONLIZER CT BLASTED AT NTPC KORBA | WRLDC |  | OMSU
112 | WR1_L_112 | 400kV KORBA-BIRSINGHPUR | 226.642 | WRTS-I |  | 2016-12-18 | 19:17 | 2016-12-19 | 20:10 |  |  |  | 0 | 0 | 0 | 24.88 |  |  |  | LINE UNABLE TO RESTORED AFTER OUTAGE DUE TO BUS SECTIONLIZER CT BLASTED AT NTPC KORBA. | WRLDC |  | GOMD
112 | WR1_L_112 | 400kV KORBA-BIRSINGHPUR | 226.642 | WRTS-I |  | 2016-12-20 | 12:11 | 2016-12-21 | 19:46 |  |  |  | 0 | 0 | 0 | 31.58 |  |  |  | LINE OUTAGE AVAILED BY NTPC KORBA (12/1882) FOR ATTENDING PROBLEM IN BUS SECTIONLIZER. BUS SECTIONLIZER CT BLASTED AT NTPC KORBA ON 18.12.16. | WRLDC |  | OSFD
|  | 400kV KORBA-BIRSINGHPUR Total | [10 empty] | 0 | 0.16 | 0 | 56.46 | [5 empty] | 100%
113 | WR1_T_001 | ICT1_400/220kv_RAIPUR | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
114 | WR1_T_002 | ICT2_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT2_400/220kv_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
115 | WR1_T_003 | ICT1_400/220kv_MAPUSA | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
116 | WR1_T_004 | ICT2_400/220kv_MAPUSA | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
117 | WR1_T_005 | ICT1_400/220kv_BAHATAPARA | 315 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT1_400/220kv_BAHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
118 | WR1_T_006 | ICT1_400/220kv_RAIGARH | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
119 | WR1_T_007 | ICT2_400/220kv_RAIGARH | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_400/220kv_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
120 | WR1_T_008 | ICT1_765/400kv_SEONI | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
121 | WR1_T_009 | ICT2_765/400kv_SEONI | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
122 | WR1_T_010 | ICT3_765/400kv_SEONI | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT3_765/400kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
123 | WR1_T_011 | ICT1_400/220kv_SEONI | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
124 | WR1_T_012 | ICT1_765/400kv_WARDHA | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
125 | WR1_T_013 | ICT2_765/400kv_WARDHA | 1500 | WRTS-I |  | 2016-12-01 | 9:54 | 2016-12-01 | 18:56 |  |  |  | 9.03 | [6 empty] | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | ICT2_765/400kv_WARDHA Total | [10 empty] | 9.03 | 0 | 0 | 0 | [5 empty] | 98.79%
126 | WR1_T_014 | ICT3_765/400kv_WARDHA | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT3_765/400kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
127 | WR1_T_015 | ICT1_765/400kv_BILASPUR | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
128 | WR1_T_016 | ICT2_765/400kv_BILASPUR | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
129 | WR1_T_017 | ICT2_400/220kv_BAHATAPARA | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_400/220kv_BAHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
130 | WR1_T_018 | ICT2_400/220kv_SEONI | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_400/220kv_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
131 | WR1_T_019 | ICT3_400/220kv_RAIPUR | 315 | WRTS-I |  | 2016-12-08 | 10:10 | 2016-12-08 | 17:53 |  |  |  | 7.71 | [6 empty] | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | ICT3_400/220kv_RAIPUR Total | [10 empty] | 7.71 | 0 | 0 | 0 | [5 empty] | 98.96%
132 | WR1_T_020 | ICT1_400/220kv_WARDHA | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
133 | WR1_T_021 | ICT2_400/220kv_WARDHA | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_400/220kv_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
134 | WR1_T_022 | ICT3_400/220kv_SOLAPUR | 500 | WRTS-I |  | 2016-12-13 | 11:50 | 2016-12-13 | 19:05 |  |  |  | 7.25 | 0 | 0 | 0 |  |  |  | OCC APPROVED OUTAGE AVAILED FOR AMP WORKS | WRLDC |  | OSPT
|  | ICT3_400/220kv_SOLAPUR Total | [10 empty] | 7.25 | 0 | 0 | 0 | [5 empty] | 99.03%
135 | WR1_T_023 | ICT1_400/220kv_SOLAPUR | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
136 | WR1_T_024 | ICT2_400/220kv_SOLAPUR | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_400/220kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
137 | WR1_T_025 | ICT1_400/220kv_PUNE | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/220kv_PUNE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
138 | WR1_T_026 | ICT2_400/220kv_PUNE | 315 | WRTS-I |  | 2016-12-16 | 11:16 | 2016-12-16 | 12:36 |  |  |  | 10.33 | 0 | 0 | 0 |  |  |  | EMERGENCY SHUTDOWN AVAILED ON IDEALLY CHARGED ICT 2 FOR ATTENDING HOSTPOT IN ISOLATOR DROPPER SIDE. | WRLDC |  | OSFT
|  | ICT2_400/220kv_PUNE Total | [10 empty] | 10.33 | 0 | 0 | 0 | [5 empty] | 98.61%
139 | WR1_T_027 | ICT3_400/220kv_PUNE | 315 | WRTS-I |  | 2016-12-19 | 9:10 | 2016-12-19 | 19:24 |  |  |  | 10.23 | [6 empty] | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | ICT3_400/220kv_PUNE Total | [10 empty] | 10.23 | 0 | 0 | 0 | [5 empty] | 98.62%
140 | WR1_T_028 | ICT3_765/400kv_BILASPUR | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT3_765/400kv_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
141 | WR1_T_029 | ICT1_765/400kv_KOTRA PS | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
142 | WR1_T_030 | ICT2_765/400kv_KOTRA PS | 1500 | WRTS-I
|  | ICT2_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
143 | WR1_T_031 | ICT4_765/400kv_KOTRA PS | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT4_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
144 | WR1_T_032 | ICT3_400/220kv_MAPUSA | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT3_400/220kv_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
145 | WR1_T_033 | ICT1_765/400kv_TAMNAR PS | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT1_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
146 | WR1_T_034 | ICT2_765/400kv_TAMNAR PS | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT2_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
147 | WR1_T_035 | ICT1_765/400kv_DURG PS | 1500 | WRTS-I
|  | ICT1_765/400kv_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
148 | WR1_T_036 | ICT1_765/400kv_SOLAPUR | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_765/400kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
149 | WR1_T_037 | ICT2_765/400kv_SOLAPUR | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT2_765/400kv_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
150 | WR1_T_038 | ICT1_400/200kv_AURANGABAD | 315 | WRTS-I |  | 2016-12-27 | 14:23 | 2016-12-27 | 19:32 |  |  |  | 5.15 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | ICT1_400/200kv_AURANGABAD Total | [10 empty] | 5.15 | 0 | 0 | 0 | [5 empty] | 99.31%
151 | WR1_T_039 | ICT2_400/200kv_AURANGABAD | 315 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT2_400/200kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
152 | WR1_T_040 | ICT2_765/400kv_AURANGABAD | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT2_765/400kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
153 | WR1_T_041 | ICT3_765/400kv_TAMNAR PS | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT3_765/400kv_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
154 | WR1_T_042 | ICT3_765/400kv_KOTRA PS | 1500 | WRTS-I |  | 2016-12-01 | 9:16 | 2016-12-01 | 14:02 |  |  |  | 0 | 0 | 0 | 4.76 |  |  |  | LINE H/T FOR CSD RELAY COMMISSIONING WORKS. | WRLDC |  | SCSD
|  | ICT3_765/400kv_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 4.76 | [5 empty] | 100%
155 | WR1_T_043 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT1_765/400kv_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
156 | WR1_T_044 | ICT2_765/400kv_D'JAIGARH | 1500 | WRTS-I
|  | ICT2_765/400kv_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
157 | WR1_T_045 | ICT1_765/400kv_D'JAIGARH | 1500 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_765/400kv_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
158 | WR1_T_046 | ICT1_400/200kv_BHADRAWATI | 315 | WRTS-I | [16 empty] | WRLDC
|  | ICT1_400/200kv_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
159 | WR1_T_047 | ICT1_765/400kv_PUNE(GIS) | 1500 | WRTS-I |  | 2016-12-05 | 9:32 | 2016-12-05 | 18:02 |  |  |  | 8.5 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
159 | WR1_T_047 | ICT1_765/400kv_PUNE(GIS) | 1500 | WRTS-I |  | 2016-12-06 | 11:08 | 2016-12-06 | 13:05 |  |  |  | 1.95 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | ICT1_765/400kv_PUNE(GIS) Total | [10 empty] | 10.45 | 0 | 0 | 0 | [5 empty] | 98.6%
160 | WR1_T_048 | ICT2_765/400kv_PUNE(GIS) | 1500 | WRTS-I |  | 2016-12-09 | 9:24 | 2016-12-09 | 17:11 |  |  |  | 7.78 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS |  |  | OSPT
|  | ICT2_765/400kv_PUNE(GIS) Total | [10 empty] | 7.78 | 0 | 0 | 0 | [5 empty] | 98.95%
161 | WR1_T_049 | ICT1_765/400kv_CHAMPA | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0
|  | ICT1_765/400kv_CHAMPA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
162 | WR1_T_050 | ICT2_765/400kv_CHAMPA | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT2_765/400kv_CHAMPA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
163 | WR1_R_001 | BUS REACTOR_400kV_63MVAR_RAIGARH | 63 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_63MVAR_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
164 | WR1_R_002 | BUS REACTOR_765kV_240MVAR_SEONI | 240 | WRTS-I |  | 2016-12-05 | 10:25 | 2016-12-05 | 12:34 |  |  |  | 0 | 0 | 0 | 2.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_SEONI Total | [10 empty] | 0 | 0 | 0 | 2.15 | [5 empty] | 100%
165 | WR1_R_003 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 50 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_400kV_KORBA 3_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
166 | WR1_R_004 | BUS REACTOR_400kV_50MVAR_WARDHA | 50 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_50MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-01 | 7:18 | 2016-12-01 | 17:21 |  |  |  | 0 | 0 | 0 | 10.05 |  |  |  | BUS REACTOR HAND TRIPPED FOR VOLTAGE REGULATION ON WRLDC INSTRUCTIONS | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-02 | 6:44 | 2016-12-02 | 18:14 |  |  |  | 0 | 0 | 0 | 11.5 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-03 | 6:54 | 2016-12-03 | 19:14 |  |  |  | 0 | 0 | 0 | 12.33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-05 | 9:05 | 2016-12-05 | 17:17 |  |  |  | 0 | 0 | 0 | 8.2 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-06 | 6:56 | 2016-12-06 | 17:00 |  |  |  | 0 | 0 | 0 | 10.06 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-08 | 7:08 | 2016-12-08 | 18:39 |  |  |  | 0 | 0 | 0 | 11.51 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-09 | 9:24 | 2016-12-09 | 19:16 |  |  |  | 0 | 0 | 0 | 9.86 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-10 | 6:38 | 2016-12-10 | 21:25 |  |  |  | 0 | 0 | 0 | 14.78 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-11 | 7:19 | 2016-12-11 | 17:41 |  |  |  | 0 | 0 | 0 | 10.36 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-16 | 9:30 | 2016-12-16 | 14:16 |  |  |  | 0 | 0 | 0 | 4.76 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-17 | 10:41 | 2016-12-17 | 13:14 |  |  |  | 0 | 0 | 0 | 2.55 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-19 | 7:33 | 2016-12-19 | 18:26 |  |  |  | 0 | 0 | 0 | 10.88 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-21 | 7:03 | 2016-12-21 | 17:20 |  |  |  | 0 | 0 | 0 | 10.28 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-22 | 10:36 | 2016-12-22 | 17:21 |  |  |  | 0 | 0 | 0 | 6.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-23 | 10:41 | 2016-12-23 | 16:11 |  |  |  | 0 | 0 | 0 | 5.5 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-24 | 9:20 | 2016-12-24 | 17:42 |  |  |  | 0 | 0 | 0 | 8.36 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-26 | 7:06 | 2016-12-26 | 17:15 |  |  |  | 0 | 0 | 0 | 10.15 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-27 | 11:39 | 2016-12-27 | 16:18 |  |  |  | 0 | 0 | 0 | 4.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-29 | 9:38 | 2016-12-29 | 16:35 |  |  |  | 0 | 0 | 0 | 6.95 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-30 | 7:46 | 2016-12-30 | 16:27 |  |  |  | 0 | 0 | 0 | 8.68 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I |  | 2016-12-31 | 7:23 | 2016-12-31 | 16:36 |  |  |  | 0 | 0 | 0 | 9.21 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | BUS REACTOR_400kV_63MVAR_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 187.37 | [5 empty] | 100%
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-01 | 7:20 | 2016-12-01 | 17:50 |  |  |  | 0 | 0 | 0 | 10.5 |  |  |  | BUS REACTOR HAND TRIPPED FOR VOLTAGE REGULATION ON WRLDC INSTRUCTIONS | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-02 | 6:43 | 2016-12-02 | 18:29 |  |  |  | 0 | 0 | 0 | 11.76 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-03 | 6:44 | 2016-12-03 | 19:26 |  |  |  | 0 | 0 | 0 | 12.7 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-05 | 9:05 | 2016-12-05 | 17:32 |  |  |  | 0 | 0 | 0 | 8.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-06 | 7:00 | 2016-12-06 | 16:47 |  |  |  | 0 | 0 | 0 | 9.78 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-07 | 6:14 | 2016-12-07 | 17:41 |  |  |  | 0 | 0 | 0 | 11.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-08 | 7:08 | 2016-12-08 | 18:40 |  |  |  | 0 | 0 | 0 | 11.53 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-09 | 7:47 | 2016-12-09 | 21:46 |  |  |  | 0 | 0 | 0 | 13.98 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-10 | 6:39 | 2016-12-10 | 21:30 |  |  |  | 0 | 0 | 0 | 14.85 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-11 | 7:20 | 2016-12-11 | 17:45 |  |  |  | 0 | 0 | 0 | 10.41 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-13 | 8:13 | 2016-12-13 | 18:16 |  |  |  | 0 | 0 | 0 | 10.05 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-14 | 6:17 | 2016-12-14 | 18:35 |  |  |  | 0 | 0 | 0 | 12.3 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-15 | 6:01 | 2016-12-15 | 18:24 |  |  |  | 0 | 0 | 0 | 12.38 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-16 | 9:31 | 2016-12-16 | 17:27 |  |  |  | 0 | 0 | 0 | 7.93 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-17 | 10:16 | 2016-12-17 | 17:39 |  |  |  | 0 | 0 | 0 | 7.38 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-18 | 7:45 | 2016-12-18 | 17:30 |  |  |  | 0 | 0 | 0 | 9.75 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-19 | 6:38 | 2016-12-19 | 17:19 |  |  |  | 0 | 0 | 0 | 10.68 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-21 | 7:02 | 2016-12-21 | 17:41 |  |  |  | 0 | 0 | 0 | 10.65 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-22 | 8:37 | 2016-12-22 | 17:20 |  |  |  | 0 | 0 | 0 | 8.71 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-23 | 5:57 | 2016-12-23 | 16:24 |  |  |  | 0 | 0 | 0 | 10.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-24 | 9:21 | 2016-12-24 | 17:41 |  |  |  | 0 | 0 | 0 | 8.33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-25 | 9:00 | 2016-12-25 | 17:20 |  |  |  | 0 | 0 | 0 | 8.33 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-26 | 7:05 | 2016-12-26 | 17:12 |  |  |  | 0 | 0 | 0 | 10.11 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-27 | 6:47 | 2016-12-27 | 16:47 |  |  |  | 0 | 0 | 0 | 10 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-29 | 8:19 | 2016-12-29 | 16:51 |  |  |  | 0 | 0 | 0 | 8.53 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-30 | 5:35 | 2016-12-30 | 16:34 |  |  |  | 0 | 0 | 0 | 10.98 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I |  | 2016-12-31 | 5:58 | 2016-12-31 | 16:47 |  |  |  | 0 | 0 | 0 | 10.81 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | BUS REACTOR_400kV_63MVAR_PARLI Total | [10 empty] | 0 | 0 | 0 | 282.78 | [5 empty] | 100%
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2016-12-16 | 9:31 | 2016-12-16 | 17:25 |  |  |  | 0 | 0 | 0 | 7.9 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2016-12-17 | 10:18 | 2016-12-17 | 17:45 |  |  |  | 0 | 0 | 0 | 7.45 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2016-12-19 | 9:24 | 2016-12-19 | 17:22 |  |  |  | 0 | 0 | 0 | 7.96 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2016-12-21 | 6:56 | 2016-12-21 | 17:28 |  |  |  | 0 | 0 | 0 | 10.53 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2016-12-30 | 9:46 | 2016-12-30 | 18:22 |  |  |  | 0 | 0 | 0 | 8.6 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | BUS REACTOR_400kV_50MVAR_PUNE Total | [10 empty] | 0 | 0 | 0 | 42.44 | [5 empty] | 100%
170 | WR1_R_008 | BUS REACTOR_765kV_240MVAR_WARDHA | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_765kV_240MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
171 | WR1_R_009 | BUS REACTOR_765kV_240MVAR_BILASPUR | 240 | WRTS-I |  | 2016-12-07 | 11:20 | 2016-12-10 | 1:39 |  |  |  | 0 | 0 | 0 | 62.32 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 62.32 | [5 empty] | 100%
172 | WR1_R_010 | SWITCHABLE LR_765kV_BINA_SEONI | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_BINA_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
173 | WR1_R_011 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 240 | WRTS-I |  | 2016-12-30 | 12:30 | 2016-12-30 | 14:00 |  |  |  | 0 | 0 | 0 | 1.5 |  |  |  | OUTAGE AVAILED FOR INTERCHANING OF SPARE UNIT WITH B PHASE UNIT TO ENSURE HEALTHINESS. |  |  | SCSD
|  | SWITCHABLE LR_765kV_SEONI 1_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 1.5 | [5 empty] | 100%
174 | WR1_R_012 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_765kV_SEONI 2_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
175 | WR1_R_013 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_D'GARH_BILASPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
176 | WR1_R_014 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_765kV_240MVAR_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
177 | WR1_R_015 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 80 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_80MVAR_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
178 | WR1_R_016 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_DURG 1_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
179 | WR1_R_017 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 50 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_50MVAR_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
180 | WR1_R_018 | BUS REACTOR_400kV_80MVAR_RAIPUR | 80 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_80MVAR_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
181 | WR1_R_019 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_50MVAR_MAPUSA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
182 | WR1_R_020 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2016-12-17 | 11:10 | 2016-12-17 | 13:48 |  |  |  | 0 | 0 | 0 | 2.63 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
|  | BUS REACTOR_400kV_80MVAR_KOLHAPUR Total | [10 empty] | 0 | 0 | 0 | 2.63 | [5 empty] | 100%
183 | WR1_R_021 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_DURG 2_KOTRA PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
184 | WR1_R_022 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_765kV_240MVAR_TAMNAR PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
185 | WR1_R_023 | BUS REACTOR_765kV_240MVAR_DURG PS | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_765kV_240MVAR_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
186 | WR1_R_024 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2016-12-10 | 16:01 | 2016-12-10 | 18:44 |  |  |  | 0 | 0 | 0 | 2.72 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 2.72 | [5 empty] | 100%
187 | WR1_R_025 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
188 | WR1_R_026 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
189 | WR1_R_027 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_765kV_A'BAD 1_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
190 | WR1_R_028 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 330 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_A'BAD 2_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
191 | WR1_R_029 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
192 | WR1_R_030 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 240 | WRTS-I |  | 2016-12-12 | 11:18 | 2016-12-12 | 17:34 |  |  |  | 6.26 | 0 | 0 | 0 |  |  |  | EMERGENCY OUTAGE AVAILED FOR ARRESTING OIL LEAKAGE FROM TOP INSPECTION WINDOW | WRLDC |  | OSFT
|  | SWITCHABLE LR_765kV_WARDHA 2_SEONI Total | [10 empty] | 6.26 | 0 | 0 | 0 | [5 empty] | 99.16%
193 | WR1_R_031 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
194 | WR1_R_032 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
195 | WR1_R_033 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2016-12-08 | 7:07 | 2016-12-08 | 17:54 |  |  |  | 0 | 0 | 0 | 10.78 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
195 | WR1_R_033 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2016-12-09 | 9:30 | 2016-12-09 | 19:02 |  |  |  | 0 | 0 | 0 | 9.53 |  |  |  | BUS REACTOR HAND TRIPPED FOR VOLTAGE REGULATION ON RLDC INSTRUCTION | WRLDC |  | SVRD
195 | WR1_R_033 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2016-12-17 | 10:17 | 2016-12-17 | 14:04 |  |  |  | 0 | 0 | 0 | 3.71 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
195 | WR1_R_033 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I |  | 2016-12-23 | 7:07 | 2016-12-23 | 16:52 |  |  |  | 0 | 0 | 0 | 9.75 |  |  |  | BUS REACTOR HAND TRIPPED FOR VOLTAGE REGULATION ON RLDC INSTRUCTION | WRLDC |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 33.77 | [5 empty] | 100%
196 | WR1_R_034 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_400kV_125MVAR_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
197 | WR1_R_035 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
198 | WR1_R_036 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 125 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_125MVAR_BHATAPARA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
199 | WR1_R_037 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 240 | WRTS-I |  | 2016-12-19 | 12:13 | 2016-12-19 | 18:51 |  |  |  | 6.63 | [6 empty] | EMERGENCY OUTAGE AVAILED FOR ATTENDING HEAVY OIL LEAKAGE IN R-PH LINE RECATOR FROM 02 NOS TOP INSPECTION WINDOW | WRLDC |  | OSFT
|  | SWITCHABLE LR_765kV_WARDHA 1_SEONI Total | [10 empty] | 6.63 | 0 | 0 | 0 | [5 empty] | 99.11%
200 | WR1_R_038 | BUS REACTOR_400kV_125MVAR_RAIGARH | 125 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_400kV_125MVAR_RAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
201 | WR1_R_039 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
202 | WR1_R_040 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
203 | WR1_R_041 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_WARDHA 1_DURG PS Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
204 | WR1_R_042 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I |  | 2016-12-02 | 10:26 | 2016-12-02 | 18:29 |  |  |  | 0 | 0 | 0 | 8.05 |  |  |  | H/T FOR BUSHING ERECTION OF UNDER CONSTRUCTION 765KV DURG-WARDHA # 3 LINE REACTOR TO ADJOINING PHASE AT DURG PS. | WRLDC |  | SCSD
204 | WR1_R_042 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I |  | 2016-12-03 | 9:44 | 2016-12-03 | 17:00 |  |  |  | 0 | 0 | 0 | 7.26 |  |  |  | H/T FOR BUSHING ERECTION OF UNDER CONSTRUCTION 765KV DURG-WARDHA # 3 LINE REACTOR TO ADJOINING PHASE AT DURG PS. | WRLDC |  | SCSD
204 | WR1_R_042 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I |  | 2016-12-13 | 14:41 | 2016-12-13 | 17:22 |  |  |  | 2.68 | 0 | 0 | 0 |  |  |  | H/T TO ATTEND OIL LEAKAGE FROM B PHASE. | WRLDC |  | OSFT
|  | SWITCHABLE LR_765kV_WARDHA 2_DURG PS Total | [10 empty] | 2.68 | 0 | 0 | 15.31 | [5 empty] | 99.64%
205 | WR1_R_043 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 80 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
206 | WR1_R_044 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 80 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
207 | WR1_R_045 | BUS REACTOR_400kV_125MVAR_RAIPUR | 125 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_400kV_125MVAR_RAIPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
208 | WR1_R_046 | BUS REACTOR_765kV_330MVAR_WARDHA | 330 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_765kV_330MVAR_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
209 | WR1_R_047 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 80 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_400kV_KARAD_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
210 | WR1_R_048 | BUS REACTOR_400kV_125MVAR_SEONI | 125 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_400kV_125MVAR_SEONI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
211 | WR1_R_049 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 50 | WRTS-I |  | 2016-12-30 | 14:08 | 2016-12-30 | 16:30 |  |  |  | 0 | 0 | 0 | 2.36 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE Total | [10 empty] | 0 | 0 | 0 | 2.36 | [5 empty] | 100%
212 | WR1_R_050 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 50 | WRTS-I |  | 2016-12-30 | 10:02 | 2016-12-30 | 16:33 |  |  |  | 0 | 0 | 0 | 6.51 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE Total | [10 empty] | 0 | 0 | 0 | 6.51 | [5 empty] | 100%
213 | WR1_R_051 | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE | 50 | WRTS-I |  | 2016-12-30 | 14:14 | 2016-12-30 | 16:37 |  |  |  | 0 | 0 | 0 | 2.38 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE Total | [10 empty] | 0 | 0 | 0 | 2.38 | [5 empty] | 100%
214 | WR1_R_052 | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE | 50 | WRTS-I |  | 2016-12-30 | 14:15 | 2016-12-30 | 16:41 |  |  |  | 0 | 0 | 0 | 2.43 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE Total | [10 empty] | 0 | 0 | 0 | 2.43 | [5 empty] | 100%
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-01 | 7:21 | 2016-12-01 | 17:53 |  |  |  | 0 | 0 | 0 | 10.53 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-02 | 6:45 | 2016-12-02 | 18:30 |  |  |  | 0 | 0 | 0 | 11.75 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-03 | 6:45 | 2016-12-03 | 19:27 |  |  |  | 0 | 0 | 0 | 12.7 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-05 | 9:32 | 2016-12-05 | 17:34 |  |  |  | 0 | 0 | 0 | 8.03 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-06 | 7:01 | 2016-12-06 | 16:49 |  |  |  | 0 | 0 | 0 | 9.8 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-07 | 6:15 | 2016-12-07 | 17:39 |  |  |  | 0 | 0 | 0 | 11.4 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-08 | 7:09 | 2016-12-08 | 18:41 |  |  |  | 0 | 0 | 0 | 11.53 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-09 | 7:48 | 2016-12-09 | 21:47 |  |  |  | 0 | 0 | 0 | 13.98 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-10 | 6:40 | 2016-12-10 | 21:31 |  |  |  | 0 | 0 | 0 | 14.85 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-11 | 7:21 | 2016-12-11 | 18:28 |  |  |  | 0 | 0 | 0 | 11.11 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-13 | 8:13 | 2016-12-13 | 18:17 |  |  |  | 0 | 0 | 0 | 10.06 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-14 | 6:19 | 2016-12-14 | 18:36 |  |  |  | 0 | 0 | 0 | 12.28 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-15 | 6:02 | 2016-12-15 | 18:25 |  |  |  | 0 | 0 | 0 | 12.38 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-16 | 9:32 | 2016-12-16 | 17:28 |  |  |  | 0 | 0 | 0 | 7.93 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-17 | 10:17 | 2016-12-17 | 17:40 |  |  |  | 0 | 0 | 0 | 7.38 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-18 | 7:46 | 2016-12-18 | 17:31 |  |  |  | 0 | 0 | 0 | 9.75 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-19 | 6:40 | 2016-12-19 | 17:19 |  |  |  | 0 | 0 | 0 | 10.65 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-21 | 7:03 | 2016-12-21 | 17:43 |  |  |  | 0 | 0 | 0 | 10.66 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-22 | 8:38 | 2016-12-22 | 17:21 |  |  |  | 0 | 0 | 0 | 8.71 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-23 | 5:58 | 2016-12-23 | 16:56 |  |  |  | 0 | 0 | 0 | 10.96 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-24 | 9:22 | 2016-12-24 | 17:43 |  |  |  | 0 | 0 | 0 | 8.35 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-25 | 9:01 | 2016-12-25 | 17:21 |  |  |  | 0 | 0 | 0 | 8.33 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-26 | 7:05 | 2016-12-26 | 17:12 |  |  |  | 0 | 0 | 0 | 10.11 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-27 | 6:48 | 2016-12-27 | 16:48 |  |  |  | 0 | 0 | 0 | 10 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-29 | 8:19 | 2016-12-29 | 16:52 |  |  |  | 0 | 0 | 0 | 8.55 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-30 | 5:35 | 2016-12-30 | 16:41 |  |  |  | 0 | 0 | 0 | 11.1 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
215 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I |  | 2016-12-31 | 5:58 | 2016-12-31 | 16:50 |  |  |  | 0 | 0 | 0 | 10.86 |  |  |  | H/T AS PER WRLDC INSTRUCTION FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | BUS REACTOR_400kV_125MVAR_PARLI Total | [10 empty] | 0 | 0 | 0 | 283.74 | [5 empty] | 100%
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-05 | 9:24 | 2016-12-05 | 17:26 |  |  |  | 0 | 0 | 0 | 8.03 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-06 | 14:26 | 2016-12-06 | 16:42 |  |  |  | 0 | 0 | 0 | 2.26 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-08 | 9:57 | 2016-12-08 | 17:40 |  |  |  | 0 | 0 | 0 | 7.71 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-10 | 7:47 | 2016-12-10 | 18:51 |  |  |  | 0 | 0 | 0 | 11.06 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-17 | 10:38 | 2016-12-17 | 13:18 |  |  |  | 0 | 0 | 0 | 2.66 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-22 | 10:36 | 2016-12-22 | 17:29 |  |  |  | 0 | 0 | 0 | 2.88 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-24 | 15:24 | 2016-12-24 | 17:14 |  |  |  | 0 | 0 | 0 | 1.83 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-26 | 10:29 | 2016-12-26 | 17:10 |  |  |  | 0 | 0 | 0 | 6.68 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-29 | 9:34 | 2016-12-29 | 13:15 |  |  |  | 0 | 0 | 0 | 3.68 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
216 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2016-12-31 | 11:10 | 2016-12-31 | 15:57 |  |  |  | 0 | 0 | 0 | 4.78 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION | WRLDC |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 51.57 | [5 empty] | 100%
217 | WR1_R_055 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 240 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
218 | WR1_R_056 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | BUS REACTOR_400kV_80MVAR_DHULE Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
219 | WR1_R_057 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | 330 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_A'BAD 3_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
220 | WR1_R_058 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | 330 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_A'BAD 4_WARDHA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
221 | WR1_R_059 | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH | 330 | WRTS-I |  | 2016-12-18 | 1:18 | 2016-12-18 | 2:24 |  |  |  | 1.1 | 0 | 0 | 0 |  |  |  | TRIPPED DUE TO MALOPERATION OF CVT SELETION RELAY. | WRLDC |  | SRMT
221 | WR1_R_059 | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH | 330 | WRTS-I |  | 2016-12-30 | 17:24 | 2016-12-30 | 18:15 |  |  |  | 0.85 | 0 | 0 | 0 |  |  |  | H/T FOR CHECKING FLUCTUATION IN LINE REACTOR B- PH CURRENT AT D'JAYAGARH |  |  | OSFT
|  | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH Total | [10 empty] | 1.95 | 0 | 0 | 0 | [5 empty] | 99.74%
222 | WR1_R_060 | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH | 330 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
223 | WR1_R_061 | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR | 240 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
224 | WR1_R_062 | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR | 240 | WRTS-I |  | 2016-12-01 | 12:43 | 2016-12-01 | 18:26 |  |  |  | 5.72 | 0 | 0 | 0 |  |  |  | H/T FOR AMP WORKS | WRLDC |  | OSPT
|  | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR Total | [10 empty] | 5.72 | 0 | 0 | 0 | [5 empty] | 99.23%
225 | WR1_R_063 | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
226 | WR1_R_064 | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
227 | WR1_R_065 | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) | 125 | WRTS-I |  | 2016-12-17 | 11:07 | 2016-12-17 | 13:12 |  |  |  | 0 | 0 | 0 | 2.08 |  |  |  | H/T AS PER WRLDC INSTRUCTIONS FOR VOLTAGE REGULATION. | WRLDC |  | SVRD
|  | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) Total | [10 empty] | 0 | 0 | 0 | 2.08 | [5 empty] | 100%
228 | WR1_R_066 | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD | 80 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
229 | WR1_R_067 | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD | 80 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
230 | WR1_R_068 | BUS REACTOR_765kV_240MVAR_CHAMPA | 240 | WRTS-I | [16 empty] | WRLDC
|  | BUS REACTOR_765kV_240MVAR_CHAMPA Total | [19 empty] | 100%
231 | WR1_R_069 | BUS REACTOR_400kV_80MVAR_CHAMPA | 80 | WRTS-I |  | 2016-12-18 | 9:44 | 2016-12-20 | 20:55 |  |  |  | 0 | 0 | 0 | 59.18 |  |  |  | B/R H/T FOR BUS BAR INTEGRATION WORK OF UPCOMING 400 KV HVDC BAYS AT CHAMPA ALONG WITH S/D OF 400KV BUS 1A & 2A. | WRLDC |  | SCSD
|  | BUS REACTOR_400kV_80MVAR_CHAMPA Total | [10 empty] | 0 | 0 | 0 | 59.18 | [5 empty] | 100%
232 | WR1_R_070 | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH | 330 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
233 | WR1_R_071 | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRLDC
|  | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
234 | WR1_P_001 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I |  | 2016-12-02 | 6:35 | 2016-12-11 | 10:05 |  |  |  |  | 0 | 0 | 219.5 |  |  |  | REPLACEMENT OF WEST SIDE R PHASE CONVERTOR TRANSFORMER AFTER S1 BUSHING FAILURE AT BHADRAWATI UNDER SYSTEM STRENGTHEING SCHEME AS APPROVED IN 19th WRPC BOARD MEETING. | WRLDC |  | SCSD
234 | WR1_P_001 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I |  | 2016-12-19 | 22:39 | 2016-12-19 | 23:42 |  |  |  | 1.05 | [6 empty] | POLE TRIPPED ON VALVE COOLING INLET TEMP VERY HIGH. | WRLDC |  | OMST
|  | HVDC_POLE1_BHADRAWATI Total | [10 empty] | 1.05 | 0 | 0 | 219.5 | [5 empty] | 99.86%
235 | WR1_P_002 | HVDC_POLE2_BHADRAWATI | 500 | WRTS-I | [16 empty] | WRLDC
|  | HVDC_POLE2_BHADRAWATI Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%
236 | WR1_T_051 | ICT4_765/400kv_CHAMPA | 1500 | WRTS-I |  | 2016-12-22 | 12:53 | 2016-12-22 | 14:11 |  |  |  | 1.3 | 0 | 0 | 0 |  |  |  | ICT TRIPPED DUE TO MAL-OPERATION OF PRV OF SPARE ICT OPERATED | WRLDC |  | SRMT
|  | ICT5_765/400kv_CHAMPA Total | [10 empty] | 1.3 | 0 | 0 | 0 | [5 empty] | 99.83%
237 | WR1_T_052 | ICT5_765/400kv_CHAMPA | 1500 | WRTS-I | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | WRLDC
|  | ICT5_765/400kv_CHAMPA Total | [10 empty] | 0 | 0 | 0 | 0 | [5 empty] | 100%

## Element list
SN | Element Name | TYPE | LENGTH | Jurisidiction | DOCO | Type of conductor | Configuration | PGCIL Code | SN
1 | 400kV KORBA-KORBA(WEST) | LINE | 14 | CG(O&M) | 1983-01-25 | Twin | ACSR Moose | WR1_L_001 | 1
2 | 400kV KORBA-BHILAI I | LINE | 197 | CG(O&M) | 1984-01-01 | Twin | ACSR Moose | WR1_L_002 | 2
3 | 400kV KORBA-BHILAI II | LINE | 192 | CG(O&M) | 1984-01-01 | Twin | ACSR Moose | WR1_L_003 | 3
4 | 400kV BHILAI-KORADI | LINE | 272 | MH(O&M) | 1984-05-01 | Twin | ACSR Moose | WR1_L_004 | 4
5 | 400kV KORADI-SATPURA | LINE | 149 | MH(O&M) | 1987-04-18 | Twin | ACSR Moose | WR1_L_005 | 5
6 | 400kV RAIPUR-BHILAI I | LINE | 13 | CG(O&M) | 1989-03-28 | Twin | ACSR Moose | WR1_L_006 | 6
7 | 400kV BHILAI-BHADRAVATI I | LINE | 322 | WR1-LINE | 1990-01-22 | Twin | ACSR Moose | WR1_L_007 | 7
8 | 400kV RAIPUR-BHADRAVATI I | LINE | 333 | WR1-LINE | 1989-03-28 | Twin | ACSR Moose | WR1_L_008 | 8
9 | 400kV RAIPUR-BHADRAVATI II | LINE | 345.55 | WR1-LINE | 2005-06-01 | Twin | ACSR Moose | WR1_L_009 | 9
10 | 400kV RAIPUR-BHADRAVATI III | LINE | 345.55 | WR1-LINE | 2005-06-01 | Twin | ACSR Moose | WR1_L_010 | 10
11 | 400kV BHADRAVATI-CHANDRAPUR I | LINE | 20 | MH(O&M) | 1989-03-28 | Twin | ACSR Moose | WR1_L_011 | 11
12 | 400kV BHADRAVATI-CHANDRAPUR II | LINE | 20 | MH(O&M) | 1989-03-28 | Twin | ACSR Moose | WR1_L_012 | 12
13 | 400kV BHADRAVATI-CHANDRAPUR III | LINE | 22.42 | MH(O&M) | 2006-05-01 | Twin | ACSR Moose | WR1_L_013 | 13
14 | 400kV BHADRAVATI-CHANDRAPUR IV | LINE | 22.42 | MH(O&M) | 2006-05-01 | Twin | ACSR Moose | WR1_L_014 | 14
15 | 400kV MAHAN-VINDHYACHAL | LINE | 19 | CG(O&M) | 1988-07-24 | Twin | ACSR Moose | WR1_L_015 | 15
16 | 400kV KORBA-MAHAN | LINE | 196 | CG(O&M) | 1988-07-24 | Twin | ACSR Moose | WR1_L_016 | 16
17 | 400kV VINDHYACHAL-KORBA II | LINE | 288.994 | CG(O&M) | 2007-06-01 | Twin | ACSR Moose | WR1_L_017 | 17
18 | 400kV SATPURA-SEONI | LINE | 1.507 | MH(O&M) | 2007-11-01 | Twin | ACSR Moose | WR1_L_018 | 18
19 | 400kV BHILAI-SEONI | LINE | 1.498 | MH(O&M) | 2007-11-01 | Twin | ACSR Moose | WR1_L_019 | 19
20 | 400kV BHILAI-BHATAPARA | LINE | 90.453 | CG(O&M) | 2000-01-01 | Twin | ACSR Moose | WR1_L_020 | 20
21 | 400kV BHATAPARA-KORBA | LINE | 123.73 | CG(O&M) | 2000-01-01 | Twin | ACSR Moose | WR1_L_021 | 21
22 | 400kV KORBA-SIPAT | LINE | 68.653 | CG(O&M) | 2014-09-03 | Twin | ACSR Moose | WR1_L_022 | 22
23 | 400kV RAIPUR-SIPAT I | LINE | 149.12 | CG(O&M) | 2008-08-01 | Twin | ACSR Moose | WR1_L_023 | 23
24 | 400KV RAIPUR-SIPAT II | LINE | 149.12 | CG(O&M) | 2008-08-01 | Twin | ACSR Moose | WR1_L_024 | 24
25 | 400kV RAIPUR-SIPAT III | LINE | 162.04 | CG(O&M) | 1990-02-08 | Twin | ACSR Moose | WR1_L_025 | 25
26 | 765kV BILASPUR-SIPAT I | LINE | 21.507 | CG(O&M) | 2013-04-01 | Quad | Bersimis | WR1_L_026 | 26
27 | 765kV SEONI-BILASPUR I | LINE | 337.046 | WR1-LINE | 2013-04-01 | Quad | Bersimis | WR1_L_027 | 27
28 | 765kV BILASPUR-SIPAT II | LINE | 22.216 | CG(O&M) | 2013-04-01 | Quad | Bersimis | WR1_L_028 | 28
29 | 765kV SEONI-BILASPUR II | LINE | 338.33 | WR1-LINE | 2013-04-01 | Quad | Bersimis | WR1_L_029 | 29
30 | 765kV SEONI-WARDHA I | LINE | 267.894 | MH(O&M) | 2009-04-01 | Quad | Bersimis | WR1_L_030 | 30
31 | 765kV SEONI-WARDHA II | LINE | 260.763 | MH(O&M) | 2012-03-01 | Quad | Bersimis | WR1_L_031 | 31
32 | 400kV WARDHA-AKOLA I | LINE | 161.865 | MH(O&M) | 2009-04-01 | Twin | ACSR Moose | WR1_L_032 | 32
33 | 400kV WARDHA-AKOLA II | LINE | 161.865 | MH(O&M) | 2009-04-01 | Twin | ACSR Moose | WR1_L_033 | 33
34 | 400kV AURANGABAD (PG) -AKOLA I | LINE | 289.966 | MH(O&M) | 2009-12-01 | Twin | ACSR Moose | WR1_L_034 | 34
35 | 400kV AURANGABAD (PG) -AKOLA II | LINE | 289.966 | MH(O&M) | 2009-12-01 | Twin | ACSR Moose | WR1_L_035 | 35
36 | 400kV BHADRAVATI-PARLI I | LINE | 378.667 | MH(O&M) | 2011-06-01 | Twin | ACSR Moose | WR1_L_036 | 36
37 | 400kV PARLI(PG)-PARLI(MSETCL) I | LINE | 4.958 | MH(O&M) | 2011-06-01 | Twin | ACSR Moose | WR1_L_037 | 37
38 | 400kV PARLI(PG)-PARLI(MSETCL) II | LINE | 4.958 | MH(O&M) | 2011-06-01 | Twin | ACSR Moose | WR1_L_038 | 38
39 | 400kV KORBA-RAIPUR III | LINE | 212.83 | CG(O&M) | 2011-07-01 | Twin | ACSR Moose | WR1_L_039 | 39
40 | 400kV KORBA-RAIPUR IV | LINE | 212.83 | CG(O&M) | 2011-07-01 | Twin | ACSR Moose | WR1_L_040 | 40
41 | 400kV WARDHA-PARLI I | LINE | 336.939 | MH(O&M) | 2011-08-01 | Quad | ACSR Moose | WR1_L_041 | 41
42 | 400kV WARDHA-PARLI II | LINE | 336.939 | MH(O&M) | 2011-08-01 | Quad | ACSR Moose | WR1_L_042 | 42
43 | 400kV WARDHA-MAUDA II | LINE | 123.45 | MH(O&M) | 2012-06-01 | Quad | ACSR Moose | WR1_L_043 | 43
44 | 400kV KORBA-VANDANA | LINE | 14.768 | CG(O&M) | 2012-04-01 | Twin | ACSR Moose | WR1_L_044 | 44
45 | 400kV VANDANA-BIRSINGHPUR | LINE | 211.874 | CG(O&M) | 2012-04-01 | Twin | ACSR Moose | WR1_L_045 | 45
46 | 400kV RAIPUR-WARDHA I | LINE | 370.565 | WR1-LINE | 2013-01-01 | Quad | ACSR Moose | WR1_L_046 | 46
47 | 400kV RAIPUR-WARDHA II | LINE | 370.565 | WR1-LINE | 2013-01-01 | Quad | ACSR Moose | WR1_L_047 | 47
48 | 400kV RAIPUR-DURG I | LINE | 21.43 | CG(O&M) | 2013-04-01 | Twin | ACSR Moose | WR1_L_048 | 48
49 | 400kV RAIPUR-DURG II | LINE | 21.43 | CG(O&M) | 2013-04-01 | Twin | ACSR Moose | WR1_L_049 | 49
50 | 400kV RAIGARH-KOTRA PS I | LINE | 6.288 | CG(O&M) | 2013-05-01 | Twin | ACSR Moose | WR1_L_050 | 50
51 | 400kV RAIGARH-KOTRA PS II | LINE | 6.288 | CG(O&M) | 2013-05-01 | Twin | ACSR Moose | WR1_L_051 | 51
52 | 765kV TAMNAR PS-KOTRA PS I | LINE | 47.986 | CG(O&M) | 2013-11-01 | Hexa | Zebra | WR1_L_052 | 52
53 | 765kV TAMNAR PS-KOTRA PS II | LINE | 47.986 | CG(O&M) | 2013-11-01 | Hexa | Zebra | WR1_L_053 | 53
54 | 765kV KOTRA PS-DURG PS I | LINE | 239.843 | CG(O&M) | 2014-02-01 | Hexa | Zebra | WR1_L_054 | 54
55 | 765kV KOTRA PS-DURG PS II | LINE | 239.843 | CG(O&M) | 2014-02-01 | Hexa | Zebra | WR1_L_055 | 55
56 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | LINE | 52.563 | MH(O&M) | 2014-04-29 | Quad | ACSR Moose | WR1_L_056 | 56
57 | 400kV BHADRAVATI-DHARIWAL TPP II | LINE | 2.923 | MH(O&M) | 2014-04-21 | Twin | ACSR Moose | WR1_L_057 | 57
58 | 400kV DHARIWAL TPP-PARLI II | LINE | 375.785 | MH(O&M) | 2014-04-21 | Twin | ACSR Moose | WR1_L_058 | 58
59 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | LINE | 52.563 | MH(O&M) | 2014-04-30 | Quad | ACSR Moose | WR1_L_059 | 59
60 | 765KV DURG PS - D'JAIGARH | LINE | 357.62 | CG(O&M) | 2014-05-24 | Quad | Bersimis | WR1_L_060 | 60
61 | 765kV WARDHA - AURANGABAD(PG) I | LINE | 347.577 | MH(O&M) | 2014-07-08 | Quad | Bersimis | WR1_L_061 | 61
62 | 765kV WARDHA - AURANGABAD(PG) II | LINE | 347.577 | MH(O&M) | 2014-07-08 | Quad | Bersimis | WR1_L_062 | 62
63 | 765kV DURG PS -WARDHA_1 | LINE | 369.107 | WR1-LINE | 2014-11-17 | Hexa | zebra | WR1_L_063 | 63
64 | 765kV DURG PS -WARDHA_2 | LINE | 369.107 | WR1-LINE | 2014-11-17 | Hexa | Zebra | WR1_L_064 | 64
65 | 400Kv PARLI-PUNE(GIS)_1 | LINE | 9.57 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_065 | 65
66 | 400Kv PARLI-PUNE(GIS)_2 | LINE | 9.57 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_066 | 66
67 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | LINE | 9.978 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_067 | 67
68 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | LINE | 9.978 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_068 | 68
69 | 765kV PUNE(GIS)-SOLAPUR | LINE | 269.842 | MH(O&M) | 2015-03-02 | Quad | Bersimis | WR1_L_069 | 69
70 | 765kV WARDHA - AURANGABAD(PG) III | LINE | 355 | MH(O&M) | 2015-04-01 | Hexa | zebra | WR1_L_070 | 70
71 | 765kV WARDHA - AURANGABAD(PG) IV | LINE | 355 | MH(O&M) | 2015-04-01 | Hexa | zebra | WR1_L_071 | 71
72 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | LINE | 11.2 | MH(O&M) | 2015-04-03 | Twin | ACSR Moose | WR1_L_072 | 72
73 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | LINE | 11.2 | MH(O&M) | 2015-04-03 | Twin | ACSR Moose | WR1_L_073 | 73
74 | 765kV DURG PS- CHAMPA_1 | LINE | 149.15 | CG(O&M) | 2015-05-30 | Hexa | zebra | WR1_L_074 | 74
75 | 765kV CHAMPA- KOTRA PS | LINE | 96.33 | CG(O&M) | 2015-05-31 | Quad | Bersimis | WR1_L_075 | 75
76 | 765kV AURANGABAD(PG)-SOLAPUR I | LINE | 279.57 | MH(O&M) | 2015-10-07 | Hexa | zebra | WR1_L_076 | 76
77 | 765kV AURANGABAD(PG)-SOLAPUR II | LINE | 279.57 | MH(O&M) | 2015-10-07 | Hexa | zebra | WR1_L_077 | 77
78 | 220kV KORBA(EAST)-BUDDHIPADAR III | LINE | 184 | WR1-IR1 | 1999-09-01 | Single | AAAC Zebra | WR1_L_078 | 78
79 | 400kV RAIPUR-RAIGARH I | LINE | 217.02 | WR1-IR2 | 2003-04-01 | Twin | ACSR Moose | WR1_L_079 | 79
80 | 400kV RAIGARH-ROURKELA II | LINE | 212.46 | WR1-IR2 | 2014-07-03 | Twin | ACSR Moose | WR1_L_080 | 80
81 | 400kV RAIGARH-IBEUL I | LINE | 94.43 | WR1-IR2 | 2014-11-13 | Twin | ACSR Moose | WR1_L_081 | 81
82 | 400kV IBEUL-JHARSUGUDA I | LINE | 20.03 | WR1-IR2 | 2014-11-13 | Twin | ACSR Moose | WR1_L_082 | 82
83 | 400kV JHARSUGUDA-ROURKELA I | LINE | 142.448 | WR1-IR2 | 2003-04-01 | Twin | ACSR Moose | WR1_L_083 | 83
84 | 400kV RANCHI-SIPAT I | LINE | 405.772 | WR1-IR3 | 2009-01-01 | Twin | ACSR Moose | WR1_L_084 | 84
85 | 400kV RANCHI-SIPAT II | LINE | 405.772 | WR1-IR3 | 2009-01-01 | Twin | ACSR Moose | WR1_L_085 | 85
86 | 400kV RAIPUR-KSK III | LINE | 134.74 | WR1-IR4 | 2014-07-01 | Twin | ACSR Moose | WR1_L_086 | 86
87 | 400kV KSK-RKKML III | LINE | 82.248 | WR1-IR4 | 2014-10-11 | Twin | ACSR Moose | WR1_L_087 | 87
88 | 400kV RKKML-RAIGARH III | LINE | 3.896 | WR1-IR4 | 2014-10-11 | Twin | ACSR Moose | WR1_L_088 | 88
89 | 400kV RAIPUR-KSK IV | LINE | 161.82 | WR1-IR4 | 2014-07-25 | Twin | ACSR Moose | WR1_L_089 | 89
90 | 400kV KSK-RAIGARH IV | LINE | 113.389 | WR1-IR4 | 2014-07-25 | Twin | ACSR Moose | WR1_L_090 | 90
91 | 400kV RAIGARH-JHARSUGUDA III | LINE | 110.98 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_091 | 91
92 | 400kV JHARSUGUDA-ROURKELA III | LINE | 143.06 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_092 | 92
93 | 400kV RAIGARH-STERLITE IV | LINE | 105 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_093 | 93
94 | 400kV STERLITE-ROURKELA IV | LINE | 104.28 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_094 | 94
95 | 765kV D'JAIGARH-BILASPUR | LINE | 90 | WR1-IR5 | 2014-04-01 | Quad | Bersimis | WR1_L_095 | 95
96 | 765kV D'JAIGARH-RANCHI I | LINE | 303 | WR1-IR5 | 2014-04-01 | Quad | Bersimis | WR1_L_096 | 96
97 | 765kV D'JAIGARH- JHARSUGUDA I | LINE | 149.789 | WR1-IR6 | 2014-07-31 | Quad | Bersimis | WR1_L_097 | 97
98 | 765kV D'JAIGARH- JHARSUGUDA II | LINE | 149.789 | WR1-IR6 | 2014-07-31 | Quad | Bersimis | WR1_L_098 | 98
99 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I | LINE | 39.383 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_099 | 99
100 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II | LINE | 39.383 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_100 | 100
101 | 400kV KOLHAPUR (GIS)-MAPUSA I | LINE | 156.039 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_101 | 101
102 | 400kV KOLHAPUR (GIS)-MAPUSA II | LINE | 156.039 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_102 | 102
103 | 400kV WARDHA-MAUDA I | LINE | 123.45 |  | 2015-12-05 | Quad | ACSR Moose | WR1_L_103 | 103
104 | 765kV D'JAIGARH-RANCHI II | LINE | 354 | WR1-IR7 | 2015-12-26 | Quad | Bersimis | WR1_L_104 | 104
105 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 | LINE | 14.373 |  |  |  |  | WR1_L_105 | 105
106 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 | LINE | 14.373 |  |  |  |  | WR1_L_106 | 106
107 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I | LINE | 14.387 |  |  |  |  | WR1_L_107 | 107
108 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II | LINE | 14.387 |  |  |  |  | WR1_L_108 | 108
109 | 400kV RAIPUR-RAIGARH II | LINE | 217.02 |  |  |  |  | WR1_L_109 | 109
110 | 400kV LARA(NTPC)-KOTRA PS I | LINE | 17.999 | MH(O&M) | 2016-05-05 | Twin | ACSR Moose | WR1_L_110 | 110
111 | 400kV LARA(NTPC)-KOTRA PS II | LINE | 17.999 | MH(O&M) | 2016-05-05 | Twin | ACSR Moose | WR1_L_111 | 111
112 | 400kV KORBA-BIRSINGHPUR | LINE | 226.642 | CG(O&M) | 2012-03-01 | Twin | ACSR Moose | WR1_L_112 | 112
113 | ICT1_400/220kv_RAIPUR | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_001 | 113
114 | ICT2_400/220kv_RAIPUR | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_002 | 114
115 | ICT1_400/220kv_MAPUSA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_003 | 115
116 | ICT2_400/220kv_MAPUSA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_004 | 116
117 | ICT1_400/220kv_BAHATAPARA | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_005 | 117
118 | ICT1_400/220kv_RAIGARH | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_006 | 118
119 | ICT2_400/220kv_RAIGARH | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_007 | 119
120 | ICT1_765/400kv_SEONI | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_008 | 120
121 | ICT2_765/400kv_SEONI | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_009 | 121
122 | ICT3_765/400kv_SEONI | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_010 | 122
123 | ICT1_400/220kv_SEONI | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_011 | 123
124 | ICT1_765/400kv_WARDHA | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_012 | 124
125 | ICT2_765/400kv_WARDHA | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_013 | 125
126 | ICT3_765/400kv_WARDHA | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_014 | 126
127 | ICT1_765/400kv_BILASPUR | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_015 | 127
128 | ICT2_765/400kv_BILASPUR | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_016 | 128
129 | ICT2_400/220kv_BAHATAPARA | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_017 | 129
130 | ICT2_400/220kv_SEONI | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_018 | 130
131 | ICT3_400/220kv_RAIPUR | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_019 | 131
132 | ICT1_400/220kv_WARDHA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_020 | 132
133 | ICT2_400/220kv_WARDHA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_021 | 133
134 | ICT3_400/220kv_SOLAPUR | ICT | 500 | MH(O&M) | 2015-11-02 | 500 | 500 | WR1_T_022 | 134
135 | ICT1_400/220kv_SOLAPUR | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_023 | 135
136 | ICT2_400/220kv_SOLAPUR | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_024 | 136
137 | ICT1_400/220kv_PUNE | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_025 | 137
138 | ICT2_400/220kv_PUNE | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_026 | 138
139 | ICT3_400/220kv_PUNE | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_027 | 139
140 | ICT3_765/400kv_BILASPUR | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_028 | 140
141 | ICT1_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_029 | 141
142 | ICT2_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_030 | 142
143 | ICT4_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_031 | 143
144 | ICT3_400/220kv_MAPUSA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_032 | 144
145 | ICT1_765/400kv_TAMNAR PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_033 | 145
146 | ICT2_765/400kv_TAMNAR PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_034 | 146
147 | ICT1_765/400kv_DURG PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_035 | 147
148 | ICT1_765/400kv_SOLAPUR | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_036 | 148
149 | ICT2_765/400kv_SOLAPUR | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_037 | 149
150 | ICT1_400/200kv_AURANGABAD | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_038 | 150
151 | ICT2_400/200kv_AURANGABAD | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_039 | 151
152 | ICT2_765/400kv_AURANGABAD | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_040 | 152
153 | ICT3_765/400kv_TAMNAR PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_041 | 153
154 | ICT3_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_042 | 154
155 | ICT1_765/400kv_AURANGABAD | ICT | 1500 | MH(O&M) | 2014-07-01 | 1500 | 1500 | WR1_T_043 | 155
156 | ICT2_765/400kv_D'JAIGARH | ICT | 1500 | CG(O&M) | 2014-06-19 | 1500 | 1500 | WR1_T_044 | 156
157 | ICT1_765/400kv_D'JAIGARH | ICT | 1500 | CG(O&M) | 2014-07-09 | 1500 | 1500 | WR1_T_045 | 157
158 | ICT1_400/200kv_BHADRAWATI | ICT | 315 | MH(O&M) | 2015-03-19 | 315 | 315 | WR1_T_046 | 158
159 | ICT1_765/400kv_PUNE(GIS) | ICT | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | WR1_T_047 | 159
160 | ICT2_765/400kv_PUNE(GIS) | ICT | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | WR1_T_048 | 160
161 | ICT1_765/400kv_CHAMPA | ICT | 1500 | CG(O&M) | 2015-06-13 | 1500 | 1500 | WR1_T_049 | 161
162 | ICT2_765/400kv_CHAMPA | ICT | 1500 | CG(O&M) |  | 1500 | 1500 | WR1_T_050 | 162
163 | BUS REACTOR_400kV_63MVAR_RAIGARH | BR | 63 | CG(O&M) | 2013-04-01 | 63 | 63 | WR1_R_001 | 163
164 | BUS REACTOR_765kV_240MVAR_SEONI | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_002 | 164
165 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | BR | 50 | CG(O&M) | 2013-04-01 | 50 | 50 | WR1_R_003 | 165
166 | BUS REACTOR_400kV_50MVAR_WARDHA | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_004 | 166
167 | BUS REACTOR_400kV_63MVAR_SOLAPUR | BR | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | WR1_R_005 | 167
168 | BUS REACTOR_400kV_63MVAR_PARLI | BR | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | WR1_R_006 | 168
169 | BUS REACTOR_400kV_50MVAR_PUNE | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_007 | 169
170 | BUS REACTOR_765kV_240MVAR_WARDHA | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_008 | 170
171 | BUS REACTOR_765kV_240MVAR_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_009 | 171
172 | SWITCHABLE LR_765kV_BINA_SEONI | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_010 | 172
173 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_011 | 173
174 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_012 | 174
175 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_013 | 175
176 | BUS REACTOR_765kV_240MVAR_KOTRA PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_014 | 176
177 | BUS REACTOR_400kV_80MVAR_KOTRA PS | BR | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | WR1_R_015 | 177
178 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_016 | 178
179 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_017 | 179
180 | BUS REACTOR_400kV_80MVAR_RAIPUR | BR | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | WR1_R_018 | 180
181 | BUS REACTOR_400kV_50MVAR_MAPUSA | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_019 | 181
182 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | BR | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | WR1_R_020 | 182
183 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_021 | 183
184 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_022 | 184
185 | BUS REACTOR_765kV_240MVAR_DURG PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_023 | 185
186 | BUS REACTOR_765kV_240MVAR_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_024 | 186
187 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_025 | 187
188 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_026 | 188
189 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | BR | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | WR1_R_027 | 189
190 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | BR | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | WR1_R_028 | 190
191 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_029 | 191
192 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | BR | 240 | MH(O&M) | 2014-04-01 | 240 | 240 | WR1_R_030 | 192
193 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | BR | 330 | CG(O&M) | 2014-04-01 | 240 | 240 | WR1_R_031 | 193
194 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | BR | 330 | CG(O&M) | 2014-04-18 | 240 | 240 | WR1_R_032 | 194
195 | BUS REACTOR_765kV_240MVAR_AURANGABAD | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_033 | 195
196 | BUS REACTOR_400kV_125MVAR_AURANGABAD | BR | 125 | MH(O&M) | 2014-04-30 | 125 | 125 | WR1_R_034 | 196
197 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | BR | 240 | CG(O&M) | 2014-05-26 | 240 | 240 | WR1_R_035 | 197
198 | BUS REACTOR_400kV_125MVAR_BHATAPARA | BR | 125 | CG(O&M) | 2014-07-26 | 125 | 125 | WR1_R_036 | 198
199 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | BR | 240 | MH(O&M) | 2014-05-02 | 240 | 240 | WR1_R_037 | 199
200 | BUS REACTOR_400kV_125MVAR_RAIGARH | BR | 125 | CG(O&M) | 2014-08-01 | 125 | 125 | WR1_R_038 | 200
201 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | BR | 240 | MH(O&M) | 2014-08-02 | 240 | 240 | WR1_R_039 | 201
202 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | BR | 240 | MH(O&M) | 2014-08-07 | 240 | 240 | WR1_R_040 | 202
203 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | BR | 240 | CG(O&M) | 2014-08-21 | 240 | 240 | WR1_R_041 | 203
204 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | BR | 240 | CG(O&M) | 2014-08-29 | 240 | 240 | WR1_R_042 | 204
205 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | BR | 80 | MH(O&M) | 2014-10-01 | 80 | 80 | WR1_R_043 | 205
206 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | BR | 80 | MH(O&M) | 2014-10-02 | 80 | 80 | WR1_R_044 | 206
207 | BUS REACTOR_400kV_125MVAR_RAIPUR | BR | 125 | CG(O&M) | 2014-10-02 | 125 | 125 | WR1_R_045 | 207
208 | BUS REACTOR_765kV_330MVAR_WARDHA | BR | 330 | MH(O&M) | 2014-11-03 | 330 | 330 | WR1_R_046 | 208
209 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | BR | 80 | MH(O&M) | 2014-11-26 | 80 | 80 | WR1_R_047 | 209
210 | BUS REACTOR_400kV_125MVAR_SEONI | BR | 125 | MH(O&M) | 2014-12-13 | 125 | 125 | WR1_R_048 | 210
211 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_049 | 211
212 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_050 | 212
213 | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_051 | 213
214 | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_052 | 214
215 | BUS REACTOR_400kV_125MVAR_PARLI | BR | 125 | MH(O&M) | 2015-01-10 | 125 | 125 | WR1_R_053 | 215
216 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | BR | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | WR1_R_054 | 216
217 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | BR | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | WR1_R_055 | 217
218 | BUS REACTOR_400kV_80MVAR_DHULE | BR | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | WR1_R_056 | 218
219 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | BR | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | WR1_R_057 | 219
220 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | BR | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | WR1_R_058 | 220
221 | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH | BR | 330 | CG(O&M) | 2015-09-14 | 330 | 330 | WR1_R_059 | 221
222 | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH | BR | 330 | CG(O&M) | 2015-09-15 | 330 | 330 | WR1_R_060 | 222
223 | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR | BR | 240 | MH(O&M) | 2015-10-07 | 240 | 240 | WR1_R_061 | 223
224 | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR | BR | 240 | MH(O&M) | 2015-10-07 | 240 | 240 | WR1_R_062 | 224
225 | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH | BR | 330 | CG(O&M) | 2015-10-17 | 330 | 330 | WR1_R_063 | 225
226 | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH | BR | 330 | CG(O&M) | 2015-10-17 | 330 | 330 | WR1_R_064 | 226
227 | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) | BR | 125 | MH(O&M) | 2015-11-12 | 125 | 125 | WR1_R_065 | 227
228 | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD | BR | 80 | MH(O&M) |  | 80 | 80 | WR1_R_066 | 228
229 | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD | BR | 80 | MH(O&M) |  | 80 | 80 | WR1_R_067 | 229
230 | BUS REACTOR_765kV_240MVAR_CHAMPA | BR | 240 |  |  | 240 | 240 | WR1_R_068 | 230
231 | BUS REACTOR_400kV_80MVAR_CHAMPA | BR | 80 |  |  | 80 | 80 | WR1_R_069 | 231
232 | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH | BR | 330 |  |  |  |  | WR1_R_070 | 232
233 | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH | BR | 330 |  |  |  |  | WR1_R_071 | 233
234 | HVDC_POLE1_BHADRAWATI | HVDC | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | WR1_P_001 | 234
235 | HVDC_POLE2_BHADRAWATI | HVDC | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | WR1_P_002 | 235

## Sheet1 (2)
Total Element Nos. | To be included | Element having tripping
1 | 1 | 9 | 4
2 | 2 | 10 | 6
3 | 3 | 12 | 8
4 | 4 | 16 | 9
5 | 5 | 21 | 10
6 | 6 | 25 | 11
7 | 7 | 27 | 12
8 | 8 | 31 | 13
9 | FALSE | 34 | 14
10 | FALSE | 35 | 15
11 | 11 | 36 | 16
12 | FALSE | 42 | 20
13 | 13 | 43 | 21
14 | 14 | 45 | 22
15 | 15 | 51 | 24
16 | FALSE | 53 | 25
17 | 17 | 54 | 26
18 | 18 | 55 | 27
19 | 19 | 57 | 28
20 | 20 | 59 | 32
21 | FALSE | 61 | 33
22 | 22 | 62 | 34
23 | 23 | 63 | 35
24 | 24 | 64 | 37
25 | FALSE | 69 | 38
26 | 26 | 70 | 39
27 | FALSE | 71 | 40
28 | 28 | 74 | 41
29 | 29 | 75 | 42
30 | 30 | 76 | 43
31 | FALSE | 77 | 44
32 | 32 | 79 | 45
33 | 33 | 80 | 46
34 | FALSE | 81 | 47
35 | FALSE | 91 | 49
36 | FALSE | 93 | 50
37 | 37 | 95 | 51
38 | 38 | 99 | 52
39 | 39 | 100 | 53
40 | 40 | 101 | 54
41 | 41 | 102 | 55
42 | FALSE | 103 | 58
43 | FALSE | 107 | 59
44 | 44 | 108 | 61
45 | FALSE | 109 | 65
46 | 46 | 112 | 66
47 | 47 | 114 | 69
48 | 48 | 117 | 70
49 | 49 | 142 | 74
50 | 50 | 147 | 75
51 | FALSE | 152 | 77
52 | 52 | 155 | 78
53 | FALSE | 156 | 79
54 | FALSE | 159 | 80
55 | FALSE | 160 | 84
56 | 56 | 161 | 86
57 | FALSE | 162 | 87
58 | 58 | 167 | 90
59 | FALSE | 168 | 93
60 | 60 | 171 | 94
61 | FALSE | 173 | 95
62 | FALSE | 174 | 96
63 | FALSE | 184 | 98
64 | FALSE | 215 | 99
65 | 65 | 216 | 101
66 | 66 | 217 | 107
67 | 67 | 230 | 108
68 | 68 | 231 | 109
69 | FALSE |  | 110
70 | FALSE |  | 111
71 | FALSE |  | 112
72 | 72 |  | 113
73 | 73 |  | 114
74 | FALSE |  | 115
75 | FALSE |  | 116
76 | FALSE |  | 117
77 | FALSE |  | 118
78 | 78 |  | 119
79 | FALSE |  | 120
80 | FALSE |  | 121
81 | FALSE |  | 122
82 | 82 |  | 123
83 | 83 |  | 125
84 | 84 |  | 126
85 | 85 |  | 127
86 | 86 |  | 132
87 | 87 |  | 133
88 | 88 |  | 134
89 | 89 |  | 135
90 | 90 |  | 137
91 | FALSE |  | 138
92 | 92 |  | 139
93 | FALSE |  | 143
94 | 94 |  | 144
95 | FALSE |  | 146
96 | 96 |  | 147
97 | 97 |  | 148
98 | 98 |  | 149
99 | FALSE |  | 150
100 | FALSE |  | 151
101 | FALSE |  | 152
102 | FALSE |  | 154
103 | FALSE |  | 155
104 | 104 |  | 156
105 | 105 |  | 157
106 | 106 |  | 158
107 | FALSE |  | 160
108 | FALSE |  | 161
109 | FALSE |  | 163
110 | 110 |  | 164
111 | 111 |  | 165
112 | FALSE |  | 166
113 | 113 |  | 167
114 | FALSE |  | 171
115 | 115 |  | 173
116 | 116 |  | 175
117 | FALSE |  | 176
118 | 118 |  | 177
119 | 119 |  | 178
120 | 120 |  | 179
121 | 121 |  | 180
122 | 122 |  | 181
123 | 123 |  | 184
124 | 124 |  | 185
125 | 125 |  | 186
126 | 126 |  | 187
127 | 127 |  | 188
128 | 128 |  | 189
129 | 129 |  | 190
130 | 130 |  | 192
131 | 131 |  | 193
132 | 132 |  | 195
133 | 133 |  | 197
134 | 134 |  | 198
135 | 135 |  | 200
136 | 136 |  | 201
137 | 137 |  | 202
138 | 138 |  | 203
139 | 139 |  | 204
140 | 140 |  | 205
141 | 141 |  | 206
142 | FALSE |  | 207
143 | 143 |  | 208
144 | 144 |  | 209
145 | 145 |  | 211
146 | 146 |  | 214
147 | FALSE |  | 215
148 | 148 |  | 218
149 | 149 |  | 220
150 | 150 |  | 222
151 | 151 |  | 223
152 | FALSE |  | 224
153 | 153 |  | 225
154 | 154 |  | 226
155 | FALSE |  | 227
156 | FALSE |  | 229
157 | 157 |  | 230
158 | 158 |  | 231
159 | FALSE |  | 232
160 | FALSE |  | 233
161 | FALSE |  | 234
162 | FALSE |  | 235
163 | 163 |  | 236
164 | 164
165 | 165
166 | 166
167 | FALSE
168 | FALSE
169 | 169
170 | 170
171 | FALSE
172 | 172
173 | FALSE
174 | FALSE
175 | 175
176 | 176
177 | 177
178 | 178
179 | 179
180 | 180
181 | 181
182 | 182
183 | 183
184 | FALSE
185 | 185
186 | 186
187 | 187
188 | 188
189 | 189
190 | 190
191 | 191
192 | 192
193 | 193
194 | 194
195 | 195
196 | 196
197 | 197
198 | 198
199 | 199
200 | 200
201 | 201
202 | 202
203 | 203
204 | 204
205 | 205
206 | 206
207 | 207
208 | 208
209 | 209
210 | 210
211 | 211
212 | 212
213 | 213
214 | 214
215 | FALSE
216 | FALSE
217 | FALSE
218 | 218
219 | 219
220 | 220
221 | 221
222 | 222
223 | 223
224 | 224
225 | 225
226 | 226
227 | 227
228 | 228
229 | 229
230 | FALSE
231 | FALSE
232 | 232
233 | 233
234 | 234
235 | 235

## Sheet4
146
147
150 |  |  |  | 0.97951 | 23.5083
151 |  |  |  |  | 10
152 | 0 | 0 | 0 | 1900-01-05 10:03 | 0 | 0 | 0 | 154.05 | 0 | 0 | 0 | 154.05
153 | 0 | 0 | 0 | 0.29306 | 0 | 0 | 0 | 7.0333 | 0 | 0 | 0 | 7.0333
155 | 0 | 0 | 0 | 0.47569 | 0 | 0 | 0 | 11.4167 | 0 | 0 | 0 | 11.4167
156 | 0 | 0 | 0 | 1900-01-01 07:18 | 0 | 0 | 0 | 55.3 | 0 | 0 | 0 | 55.3
157 | 0 | 0 | 0 | 0.37222 | 0 | 0 | 0 | 8.9333 | 0 | 0 | 0 | 8.9333
160 | 0 | 0 | 0 | 0.675 | 0 | 0 | 0 | 16.2 | 0 | 0 | 0 | 16.2
161 | 0 | 0 | 0 | 1900-01-01 16:41 | 0 | 0 | 0 | 64.6833 | 0 | 0 | 0 | 64.6833
162 | 0 | 0 | 0 | 0.69306 | 0 | 0 | 0 | 16.6333 | 0 | 0 | 0 | 16.6333
163 | 0 | 0 | 0 | 0.47222 | 0 | 0 | 0 | 11.3333 | 0 | 0 | 0 | 11.3333
164 | 0 | 0 | 0 | 1900-01-02 11:31 | 0 | 0 | 0 | 83.5167 | 0 | 0 | 0 | 83.5167
165 | 0.15764 | 0 | 0 | 0 | 3.7833 | 0 | 0 | 0 | 3.7833 | 0 | 0 | 0
166 | 0.24028 | 0 | 0 | 0 | 5.7667 | 0 | 0 | 0 | 5.7667 | 0 | 0 | 0
167 | 0 | 0 | 0 | 1899-12-31 13:43 | 0 | 0 | 0 | 37.7167 | 0 | 0 | 0 | 37.7167
168 | 0 | 0 | 0 | 1899-12-31 13:25 | 0 | 0 | 0 | 37.4167 | 0 | 0 | 0 | 37.4167
169 | 0.084722 | 0 | 0 | 0 | 2.0333 | 0 | 0 | 0 | 2.0333 | 0 | 0 | 0
170 | 0.091667 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0
174 | 0.091667 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0
175 | 0 | 0 | 0 | 1899-12-31 09:40 | 0 | 0 | 0 | 33.6667 | 0 | 0 | 0 | 33.6667
177 | 0 | 0 | 0 | 0.49514 | 0 | 0 | 0 | 11.8833 | 0 | 0 | 0 | 11.8833
178 | 0 | 0 | 0 | 0.51528 | 0 | 0 | 0 | 12.3667 | 0 | 0 | 0 | 12.3667
180 | 0.44097 | 0 | 0 | 0 | 10.5833 | 0 | 0 | 0 | 10.5833 | 0 | 0 | 0
181 | 0.079861 | 0 | 0 | 0 | 1.9167 | 0 | 0 | 0 | 1.9167 | 0 | 0 | 0
182 | 0.13125 | 0 | 0 | 0 | 3.15 | 0 | 0 | 0 | 3.15 | 0 | 0 | 0
183 | 0 | 0 | 0.0069444 | 0 | 0 | 0 | 0.16667 | 0 | 0 | 0 | 0.16667 | 0
185 | 0 | 0 | 0 | 1899-12-31 12:53 | 0 | 0 | 0 | 36.8833 | 0 | 0 | 0 | 36.8833
187 | 0 | 0 | 0 | 0.91528 | 0 | 0 | 0 | 21.9667 | 0 | 0 | 0 | 21.9667
189 | 0 | 0 | 0 | 0.8875 | 0 | 0 | 0 | 21.3 | 0 | 0 | 0 | 21.3
190 | 0 | 0 | 0 | 1899-12-31 02:20 | 0 | 0 | 0 | 26.3333 | 0 | 0 | 0 | 26.3333
191 | 0.81944 | 0 | 0 | 0 | 19.6667 | 0 | 0 | 0 | 19.6667 | 0 | 0 | 0
193 | 0 | 0 | 0 | 0.17431 | 0 | 0 | 0 | 4.1833 | 0 | 0 | 0 | 4.1833
194 | 0 | 0 | 0 | 1899-12-31 23:03 | 0 | 0 | 0 | 47.05 | 0 | 0 | 0 | 47.05
195 | 0 | 0 | 0 | 0.73403 | 0 | 0 | 0 | 17.6167 | 0 | 0 | 0 | 17.6167
196 | 0.094444 | 0 | 0 | 0 | 2.2667 | 0 | 0 | 0 | 2.2667 | 0 | 0 | 0
197 | 0 | 0.10833 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 | 2.6 | 0 | 0
199 | 0 | 0 | 0 | 1899-12-31 08:07 | 0 | 0 | 0 | 32.1167 | 0 | 0 | 0 | 32.1167
200 | 0 | 0 | 0 | 1900-01-02 11:10 | 0 | 0 | 0 | 83.1667 | 0 | 0 | 0 | 83.1667
201 | 0 | 0 | 0 | 0.33611 | 0 | 0 | 0 | 8.0667 | 0 | 0 | 0 | 8.0667
202 | 0 | 0 | 0 | 0.35833 | 0 | 0 | 0 | 8.6 | 0 | 0 | 0 | 8.6
205 | 0 | 0 | 0 | 0.32917 | 0 | 0 | 0 | 7.9 | 0 | 0 | 0 | 7.9
206 | 0 | 0 | 0 | 0.25903 | 0 | 0 | 0 | 6.2167 | 0 | 0 | 0 | 6.2167
207 | 0 | 0 | 0 | 1900-01-03 13:05 | 0 | 0 | 0 | 109.0833 | 0 | 0 | 0 | 109.0833
208 | 0.10764 | 0 | 0 | 0 | 2.5833 | 0 | 0 | 0 | 2.5833 | 0 | 0 | 0
210 | 0 | 0 | 0 | 0.34306 | 0 | 0 | 0 | 8.2333 | 0 | 0 | 0 | 8.2333
212 | 0 | 0 | 0 | 0.38125 | 0 | 0 | 0 | 9.15 | 0 | 0 | 0 | 9.15
217 | 0 | 0 | 0 | 0.80903 | 0 | 0 | 0 | 19.4167 | 0 | 0 | 0 | 19.4167
219 | 0 | 0 | 0 | 0.67569 | 0 | 0 | 0 | 16.2167 | 0 | 0 | 0 | 16.2167
220 | 0 | 0 | 0 | 0.40764 | 0 | 0 | 0 | 9.7833 | 0 | 0 | 0 | 9.7833
221 | 0 | 0 | 0 | 0.39931 | 0 | 0 | 0 | 9.5833 | 0 | 0 | 0 | 9.5833
222 | 0 | 0 | 0.032639 | 0 | 0 | 0 | 0.78333 | 0 | 0 | 0 | 0.78333 | 0
223 | 0 | 0 | 0 | 0.25069 | 0 | 0 | 0 | 6.0167 | 0 | 0 | 0 | 6.0167
224 | 0 | 0 | 0 | 0.27361 | 0 | 0 | 0 | 6.5667 | 0 | 0 | 0 | 6.5667
225 | 0 | 0 | 0 | 0.5625 | 0 | 0 | 0 | 13.5 | 0 | 0 | 0 | 13.5
226 | 0 | 0 | 0 | 0.67292 | 0 | 0 | 0 | 16.15 | 0 | 0 | 0 | 16.15
227 | 0 | 0 | 0 | 0.42431 | 0 | 0 | 0 | 10.1833 | 0 | 0 | 0 | 10.1833
228 | 0 | 0 | 0 | 0.60764 | 0 | 0 | 0 | 14.5833 | 0 | 0 | 0 | 14.5833
229 | 0 | 0 | 0 | 0.31806 | 0 | 0 | 0 | 7.6333 | 0 | 0 | 0 | 7.6333
230 | 0 | 0 | 0 | 0.52083 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 12.5
233 | 0 | 0 | 0 | 0.45278 | 0 | 0 | 0 | 10.8667 | 0 | 0 | 0 | 10.8667
237 | 0 | 0 | 0 | 1900-01-01 11:45 | 0 | 0 | 0 | 59.75 | 0 | 0 | 0 | 59.75
| 0 | 0 | 0 | 0.63472 | 0 | 0 | 0 | 15.2333 | 0 | 0 | 0 | 15.2333
| 0 | 0 | 0 | 0.50069 | 0 | 0 | 0 | 12.0167 | 0 | 0 | 0 | 12.0167
| 0 | 0 | 0 | 0.24167 | 0 | 0 | 0 | 5.8 | 0 | 0 | 0 | 5.8
| 0 | 0 | 0 | 0.62014 | 0 | 0 | 0 | 14.8833 | 0 | 0 | 0 | 14.8833
| 0.043056 | 0 | 0 | 0 | 1.0333 | 0 | 0 | 0 | 1.0333 | 0 | 0 | 0
| 0 | 0 | 0 | 1900-01-17 20:26 | 0 | 0 | 0 | 452.4333 | 0 | 0 | 0 | 452.4333
| 0 | 0 | 0 | 0.59167 | 0 | 0 | 0 | 14.2 | 0 | 0 | 0 | 14.2
| 0 | 0 | 0 | 0.45417 | 0 | 0 | 0 | 10.9 | 0 | 0 | 0 | 10.9
| 0 | 0 | 0 | 1900-01-03 02:54 | 0 | 0 | 0 | 98.9 | 0 | 0 | 0 | 98.9
| 0 | 0 | 0 | 0.39931 | 0 | 0 | 0 | 9.5833 | 0 | 0 | 0 | 9.5833
| 0 | 0 | 0 | 0.052778 | 0 | 0 | 0 | 1.2667 | 0 | 0 | 0 | 1.2667
| 0 | 0 | 0 | 0.64444 | 0 | 0 | 0 | 15.4667 | 0 | 0 | 0 | 15.4667
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.10417 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0
| 0 | 0.016667 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0.4 | 0 | 0
| 0 | 0 | 0 | 0.58889 | 0 | 0 | 0 | 14.1333 | 0 | 0 | 0 | 14.1333
| 0 | 0 | 0 | 0.71806 | 0 | 0 | 0 | 17.2333 | 0 | 0 | 0 | 17.2333
| 0.32083 | 0 | 0 | 0 | 7.7 | 0 | 0 | 0 | 7.7 | 0 | 0 | 0
| 0 | 0 | 0 | 0.035417 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0 | 0.85
| 0 | 0 | 0 | 0.059028 | 0 | 0 | 0 | 1.4167 | 0 | 0 | 0 | 1.4167
| 0 | 0 | 0 | 0.65417 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 15.7
| 0.70278 | 0 | 0 | 0 | 16.8667 | 0 | 0 | 0 | 16.8667 | 0 | 0 | 0
| 0 | 0 | 0 | 1899-12-31 14:20 | 0 | 0 | 0 | 38.3333 | 0 | 0 | 0 | 38.3333
| 0 | 0 | 0 | 1899-12-31 07:50 | 0 | 0 | 0 | 31.8333 | 0 | 0 | 0 | 31.8333
| 0 | 0 | 0 | 0.21944 | 0 | 0 | 0 | 5.2667 | 0 | 0 | 0 | 5.2667
| 0 | 0 | 0 | 1900-01-06 15:09 | 0 | 0 | 0 | 183.15 | 0 | 0 | 0 | 183.15
| 0.035417 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0
| 0 | 0 | 0 | 1900-01-01 11:15 | 0 | 0 | 0 | 59.25 | 0 | 0 | 0 | 59.25
| 0 | 0 | 0 | 0.24167 | 0 | 0 | 0 | 5.8 | 0 | 0 | 0 | 5.8
| 0.57986 | 0 | 0 | 0 | 13.9167 | 0 | 0 | 0 | 13.9167 | 0 | 0 | 0
| 0 | 0 | 0 | 0.30694 | 0 | 0 | 0 | 7.3667 | 0 | 0 | 0 | 7.3667
| 0.38542 | 0 | 0 | 0 | 9.25 | 0 | 0 | 0 | 9.25 | 0 | 0 | 0
| 0 | 0 | 0 | 1900-01-01 22:29 | 0 | 0 | 0 | 70.4833 | 0 | 0 | 0 | 70.4833
| 0 | 0 | 0 | 1900-01-02 16:56 | 0 | 0 | 0 | 88.9333 | 0 | 0 | 0 | 88.9333
| 0 | 0.061111 | 0 | 0 | 0 | 1.4667 | 0 | 0 | 0 | 1.4667 | 0 | 0
| 0 | 0.16944 | 0 | 0 | 0 | 4.0667 | 0 | 0 | 0 | 4.0667 | 0 | 0
| 0 | 0.11597 | 0 | 0 | 0 | 2.7833 | 0 | 0 | 0 | 2.7833 | 0 | 0
| 0 | 0.10764 | 0 | 0 | 0 | 2.5833 | 0 | 0 | 0 | 2.5833 | 0 | 0
| 0 | 0.11944 | 0 | 0 | 0 | 2.8667 | 0 | 0 | 0 | 2.8667 | 0 | 0
| 0 | 0.20139 | 0 | 0 | 0 | 4.8333 | 0 | 0 | 0 | 4.8333 | 0 | 0
| 0.35278 | 0 | 0 | 0 | 8.4667 | 0 | 0 | 0 | 8.4667 | 0 | 0 | 0
| 0.25486 | 0 | 0 | 0 | 6.1167 | 0 | 0 | 0 | 6.1167 | 0 | 0 | 0
| 0.225 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0
| 0.0125 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0
| 0 | 0.070833 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 1.7 | 0 | 0
| 0 | 0 | 0 | 1899-12-31 10:33 | 0 | 0 | 0 | 34.55 | 0 | 0 | 0 | 34.55
| 0.015278 | 0 | 0 | 0 | 0.36667 | 0 | 0 | 0 | 0.36667 | 0 | 0 | 0
| 0 | 0 | 0 | 1899-12-31 11:53 | 0 | 0 | 0 | 35.8833 | 0 | 0 | 0 | 35.8833
| 0 | 0 | 0 | 1899-12-31 06:49 | 0 | 0 | 0 | 30.8167 | 0 | 0 | 0 | 30.8167
| 0.35278 | 0 | 0 | 0 | 8.4667 | 0 | 0 | 0 | 8.4667 | 0 | 0 | 0
| 0.71736 | 0 | 0 | 0 | 17.2167 | 0 | 0 | 0 | 17.2167 | 0 | 0 | 0
| 0.21944 | 0 | 0 | 0 | 5.2667 | 0 | 0 | 0 | 5.2667 | 0 | 0 | 0
| 0 | 0 | 0 | 0.325 | 0 | 0 | 0 | 7.8 | 0 | 0 | 0 | 7.8
| 0 | 0 | 0 | 0.77361 | 0 | 0 | 0 | 18.5667 | 0 | 0 | 0 | 18.5667
| 0 | 0 | 0 | 1899-12-31 08:44 | 0 | 0 | 0 | 32.7333 | 0 | 0 | 0 | 32.7333
| 0 | 0 | 0.43611 | 0 | 0 | 0 | 10.4667 | 0 | 0 | 0 | 10.4667 | 0
| 0.45694 | 0 | 0 | 0 | 10.9667 | 0 | 0 | 0 | 10.9667 | 0 | 0 | 0
| 0.21528 | 0 | 0 | 0 | 5.1667 | 0 | 0 | 0 | 5.1667 | 0 | 0 | 0
| 0 | 0 | 0 | 1900-01-01 22:05 | 0 | 0 | 0 | 70.0833 | 0 | 0 | 0 | 70.0833
| 0 | 0 | 0 | 1899-12-31 14:07 | 0 | 0 | 0 | 38.1167 | 0 | 0 | 0 | 38.1167
| 0.088889 | 0 | 0 | 0 | 2.1333 | 0 | 0 | 0 | 2.1333 | 0 | 0 | 0
| 0.059722 | 0 | 0 | 0 | 1.4333 | 0 | 0 | 0 | 1.4333 | 0 | 0 | 0
| 1899-12-31 01:33 | 0 | 0 | 0 | 25.55 | 0 | 0 | 0 | 25.55 | 0 | 0 | 0
| 0.40486 | 0 | 0 | 0 | 9.7167 | 0 | 0 | 0 | 9.7167 | 0 | 0 | 0
| 0 | 0 | 0.53542 | 0 | 0 | 0 | 12.85 | 0 | 0 | 0 | 12.85 | 0
| 0.22083 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0 | 5.3 | 0 | 0 | 0
| 0 | 0 | 0 | 1899-12-31 10:13 | 0 | 0 | 0 | 34.2167 | 0 | 0 | 0 | 34.2167
| 0.027778 | 0 | 0 | 0 | 0.66667 | 0 | 0 | 0 | 0.66667 | 0 | 0 | 0
| 0 | 0 | 0 | 0.11111 | 0 | 0 | 0 | 2.6667 | 0 | 0 | 0 | 2.6667
| 0 | 0 | 0 | 1900-01-01 06:13 | 0 | 0 | 0 | 54.2167 | 0 | 0 | 0 | 54.2167
| 0.095833 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0
| 0 | 0 | 0 | 1900-01-02 16:31 | 0 | 0 | 0 | 88.5167 | 0 | 0 | 0 | 88.5167
| 0 | 0 | 0 | 0.37986 | 0 | 0 | 0 | 9.1167 | 0 | 0 | 0 | 9.1167
| 0.38472 | 0 | 0 | 0 | 9.2333 | 0 | 0 | 0 | 9.2333 | 0 | 0 | 0
| 0.10556 | 0 | 0 | 0 | 2.5333 | 0 | 0 | 0 | 2.5333 | 0 | 0 | 0
| 0 | 0 | 0 | 1900-01-02 20:57 | 0 | 0 | 0 | 92.95 | 0 | 0 | 0 | 92.95
| 0.0875 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0.12222 | 0 | 0 | 0 | 2.9333 | 0 | 0 | 0 | 2.9333
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.080556 | 0 | 0 | 0 | 1.9333 | 0 | 0 | 0 | 1.9333 | 0 | 0 | 0
| 0 | 0 | 0 | 1899-12-31 07:19 | 0 | 0 | 0 | 31.3167 | 0 | 0 | 0 | 31.3167
| 0 | 0 | 0 | 0.26806 | 0 | 0 | 0 | 6.4333 | 0 | 0 | 0 | 6.4333
| 0 | 0 | 0 | 1899-12-31 08:00 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 32
| 0 | 0 | 0 | 1899-12-31 09:54 | 0 | 0 | 0 | 33.9 | 0 | 0 | 0 | 33.9
| 0 | 0 | 0 | 0.39236 | 0 | 0 | 0 | 9.4167 | 0 | 0 | 0 | 9.4167
| 0 | 0 | 0 | 1900-01-01 08:03 | 0 | 0 | 0 | 56.05 | 0 | 0 | 0 | 56.05
| 0 | 0 | 0 | 1900-01-02 15:24 | 0 | 0 | 0 | 87.4 | 0 | 0 | 0 | 87.4
| 0 | 0 | 0 | 1900-01-02 14:44 | 0 | 0 | 0 | 86.7333 | 0 | 0 | 0 | 86.7333
| 0 | 0 | 0 | 0.17222 | 0 | 0 | 0 | 4.1333 | 0 | 0 | 0 | 4.1333
| 0 | 0 | 0 | 1900-01-01 13:08 | 0 | 0 | 0 | 61.1333 | 0 | 0 | 0 | 61.1333
| 0 | 0 | 0 | 1900-01-02 12:49 | 0 | 0 | 0 | 84.8167 | 0 | 0 | 0 | 84.8167
| 0 | 0 | 0 | 0.25139 | 0 | 0 | 0 | 6.0333 | 0 | 0 | 0 | 6.0333
| 0.12569 | 0 | 0 | 0 | 3.0167 | 0 | 0 | 0 | 3.0167 | 0 | 0 | 0
| 0 | 1899-12-31 01:20 | 0 | 0 | 0 | 25.3333 | 0 | 0 | 0 | 25.3333 | 0 | 0
| 0 | 0 | 0 | 0.49722 | 0 | 0 | 0 | 11.9333 | 0 | 0 | 0 | 11.9333
| 0 | 0 | 0 | 0.27639 | 0 | 0 | 0 | 6.6333 | 0 | 0 | 0 | 6.6333
| 0.06875 | 0 | 0 | 0 | 1.65 | 0 | 0 | 0 | 1.65 | 0 | 0 | 0
| 0 | 0 | 0 | 1899-12-31 16:53 | 0 | 0 | 0 | 40.8833 | 0 | 0 | 0 | 40.8833
| 0 | 0 | 0 | 0.63333 | 0 | 0 | 0 | 15.2 | 0 | 0 | 0 | 15.2
| 0 | 0 | 0 | 1899-12-31 07:22 | 0 | 0 | 0 | 31.3667 | 0 | 0 | 0 | 31.3667
| 0 | 0 | 0 | 0.46458 | 0 | 0 | 0 | 11.15 | 0 | 0 | 0 | 11.15
| 0 | 0 | 0 | 0.45139 | 0 | 0 | 0 | 10.8333 | 0 | 0 | 0 | 10.8333
| 0 | 0 | 0.10972 | 0 | 0 | 0 | 2.6333 | 0 | 0 | 0 | 2.6333 | 0
| 0 | 0 | 1899-12-31 05:18 | 0 | 0 | 0 | 29.3 | 0 | 0 | 0 | 29.3 | 0
| 0 | 0 | 0 | 1899-12-31 03:46 | 0 | 0 | 0 | 27.7667 | 0 | 0 | 0 | 27.7667
| 0 | 0 | 0 | 0.93958 | 0 | 0 | 0 | 22.55 | 0 | 0 | 0 | 22.55
| 0 | 0 | 0 | 0.11667 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 | 2.8
| 0 | 0 | 0 | 0.020833 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0.5

## Sheet3
| Element having tripping | To be included
1 | 1 | #VALUE!
2 | 2 | #VALUE!
3 | 3 | #VALUE!
4 | 5 | #VALUE!
5 | 7 | #VALUE!
6 | 17 | #VALUE!
7 | 18 | #VALUE!
8 | 19 | #VALUE!
9 | 23 | #VALUE!
10 | 29 | #VALUE!
11 | 30 | #VALUE!
12 | 31 | #VALUE!
13 | 36 | #VALUE!
14 | 48 | #VALUE!
15 | 56 | #VALUE!
16 | 57 | #VALUE!
17 | 60 | #VALUE!
18 | 62 | #VALUE!
19 | 63 | #VALUE!
20 | 64 | #VALUE!
21 | 67 | #VALUE!
22 | 68 | #VALUE!
23 | 71 | #VALUE!
24 | 72 | #VALUE!
25 | 73 | #VALUE!
26 | 76 | #VALUE!
27 | 81 | #VALUE!
28 | 82 | #VALUE!
29 | 83 | #VALUE!
30 | 85 | #VALUE!
31 | 88 | #VALUE!
32 | 89 | #VALUE!
33 | 91 | #VALUE!
34 | 92 | #VALUE!
35 | 97 | #VALUE!
36 | 100 | #VALUE!
37 | 102 | #VALUE!
38 | 103 | #VALUE!
39 | 104 | #VALUE!
40 | 105 | #VALUE!
41 | 106 | #VALUE!
42 | 124 | #VALUE!
43 | 128 | #VALUE!
44 | 129 | #VALUE!
45 | 130 | #VALUE!
46 | 131 | #VALUE!
47 | 136 | #VALUE!
48 | 140 | #VALUE!
49 | 141 | #VALUE!
50 | 142 | #VALUE!
51 | 145 | #VALUE!
52 | 153 | #VALUE!
53 | 159 | #VALUE!
54 | 162 | #VALUE!
55 | 168 | #VALUE!
56 | 169 | #VALUE!
57 | 170 | #VALUE!
58 | 172 | #VALUE!
59 | 174 | #VALUE!
60 | 182 | #VALUE!
61 | 183 | #VALUE!
62 | 191 | #VALUE!
63 | 194 | #VALUE!
64 | 196 | #VALUE!
65 | 199 | #VALUE!
66 | 210 | #VALUE!
67 | 212 | #VALUE!
68 | 213 | #VALUE!
69 | 216 | #VALUE!
70 | 217 | #VALUE!
71 | 219 | #VALUE!
72 | 221 | #VALUE!
73 | 228 | #VALUE!
74 |  | #VALUE!
75 |  | #VALUE!
76 |  | #VALUE!
77 |  | #VALUE!
78 |  | #VALUE!
79 |  | #VALUE!
80 |  | #VALUE!
81 |  | #VALUE!
82 |  | #VALUE!
83 |  | #VALUE!
84 |  | #VALUE!
85 |  | #VALUE!
86 |  | #VALUE!
87 |  | #VALUE!
88 |  | #VALUE!
89 |  | #VALUE!
90 |  | #VALUE!
91 |  | #VALUE!
92 |  | #VALUE!
93 |  | #VALUE!
94 |  | #VALUE!
95 |  | #VALUE!
96 |  | #VALUE!
97 |  | #VALUE!
98 |  | #VALUE!
99 |  | #VALUE!
100 |  | #VALUE!
101 |  | #VALUE!
102 |  | #VALUE!
103 |  | #VALUE!
104 |  | #VALUE!
105 |  | #VALUE!
106 |  | #VALUE!
107 |  | #VALUE!
108 |  | #VALUE!
109 |  | #VALUE!
110 |  | #VALUE!
111 |  | #VALUE!
112 |  | #VALUE!
113 |  | #VALUE!
114 |  | #VALUE!
115 |  | #VALUE!
116 |  | #VALUE!
117 |  | #VALUE!
118 |  | #VALUE!
119 |  | #VALUE!
120 |  | #VALUE!
121 |  | #VALUE!
122 |  | #VALUE!
123 |  | #VALUE!
124 |  | #VALUE!
125 |  | #VALUE!
126 |  | #VALUE!
127 |  | #VALUE!
128 |  | #VALUE!
129 |  | #VALUE!
130 |  | #VALUE!
131 |  | #VALUE!
132 |  | #VALUE!
133 |  | #VALUE!
134 |  | #VALUE!
135 |  | #VALUE!
136 |  | #VALUE!
137 |  | #VALUE!
138 |  | #VALUE!
139 |  | #VALUE!
140 |  | #VALUE!
141 |  | #VALUE!
142 |  | #VALUE!
143 |  | #VALUE!
144 |  | #VALUE!
145 |  | #VALUE!
146 |  | #VALUE!
147 |  | #VALUE!
148 |  | #VALUE!
149 |  | #VALUE!
150 |  | #VALUE!
151 |  | #VALUE!
152 |  | #VALUE!
153 |  | #VALUE!
154 |  | #VALUE!
155 |  | #VALUE!
156 |  | #VALUE!
157 |  | #VALUE!
158 |  | #VALUE!
159 |  | #VALUE!
160 |  | #VALUE!
161 |  | #VALUE!
162 |  | #VALUE!
163 |  | #VALUE!
164 |  | #VALUE!
165 |  | #VALUE!
166 |  | #VALUE!
167 |  | #VALUE!
168 |  | #VALUE!
169 |  | #VALUE!
170 |  | #VALUE!
171 |  | #VALUE!
172 |  | #VALUE!
173 |  | #VALUE!
174 |  | #VALUE!
175 |  | #VALUE!
176 |  | #VALUE!
177 |  | #VALUE!
178 |  | #VALUE!
179 |  | #VALUE!
180 |  | #VALUE!
181 |  | #VALUE!
182 |  | #VALUE!
183 |  | #VALUE!
184 |  | #VALUE!
185 |  | #VALUE!
186 |  | #VALUE!
187 |  | #VALUE!
188 |  | #VALUE!
189 |  | #VALUE!
190 |  | #VALUE!
191 |  | #VALUE!
192 |  | #VALUE!
193 |  | #VALUE!
194 |  | #VALUE!
195 |  | #VALUE!
196 |  | #VALUE!
197 |  | #VALUE!
198 |  | #VALUE!
199 |  | #VALUE!
200 |  | #VALUE!
201 |  | #VALUE!
202 |  | #VALUE!
203 |  | #VALUE!
204 |  | #VALUE!
205 |  | #VALUE!
206 |  | #VALUE!
207 |  | #VALUE!
208 |  | #VALUE!
209 |  | #VALUE!
210 |  | #VALUE!
211 |  | #VALUE!
212 |  | #VALUE!
213 |  | #VALUE!
214 |  | #VALUE!
215 |  | #VALUE!
216 |  | #VALUE!
217 |  | #VALUE!
218 |  | #VALUE!
219 |  | #VALUE!
220 |  | #VALUE!
221 |  | #VALUE!
222 |  | #VALUE!
223 |  | #VALUE!
224 |  | #VALUE!
225 |  | #VALUE!
226 |  | #VALUE!
227 |  | #VALUE!
228 |  | #VALUE!
229 |  | #VALUE!
230 |  | #VALUE!
231 |  | #VALUE!
232 |  | #VALUE!
233 |  | #VALUE! | 46940.496
234 |  | #VALUE!
235 |  | #VALUE!
236 |  | #VALUE!
1
2
2
3
4
4
5
5
5
6
7
7
7
8
8
8
9
10
11
12
13
13
13
14
14
14
15
15
16
16
17
18
19
19
20
20
20
21
22
22
23
24
25
26
27
28
28
29
29
30
30
30
30
31
31
31
32
33
34
34
35
35
36
36
36
37
38
39
39
39
40
41
42
43
43
44
44
45
46
47
48
48
48
49
49
49
50
50
51
51
52
53
53
54
54
54
55
55
56
56
57
57
58
59
60
60
60
60
60
60
60
60
61
62
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
63
64
64
64
64
64
64
64
64
64
65
65
65
65
65
66
66
67
68
69
70
71
71
71
71
71
71
71
71
71
71
71
71
71
71
72
72
72
72
72
72
72
72
72
72
73
73
73
73
73
73
74
74
75
76
77
78
78
78
79
80
80
80
81
82
82
82
82
83
83
83
84
85
86
86
87
87
88
88
89
89
90
91
92
93
94
95
95
96
97
97
98
99
100
101
102
103
103
103
103
103
103
103
103
103
103
103
103
104
104
104
104
104
104
104
104
104
104
104
104
104
104
105
105
105
105
106
106
107
107
107
108
108
108
109
109
110
110
110
111
112
112
113
113
113
114
115
116
117
118
119
120
121
122
123
124
125
126
126
127
127
128
129
130
131
132
133
134
135
136
137
138
139
139
140
140
141
142
143
144
145
148
149
154
158
158
159
159
159
171
171
171
172
173
176
176
179
184
186
186
186
188
188
192
198
203
204
209
211
211
213
213
214
215
216
216
218
218
218
231
232
234
235
236

## Sheet2
9 |  |  |  |  | 1
10 |  |  |  |  | 2
12 |  |  |  |  | 3
16 |  |  |  |  | 4
21 | 0 | 0 | 0 | 0 | 5
25 |  |  |  |  | 6
27 |  |  |  |  | 7
31 |  |  |  |  | 8
34 |  |  |  |  | 11
35 |  |  |  |  | 13
36 |  |  |  |  | 14
42 |  |  |  |  | 15
43 |  |  |  |  | 17
45 |  |  |  |  | 18
51 |  |  |  |  | 19
53 |  |  |  |  | 20
54 |  |  |  |  | 22
55 |  |  |  |  | 23
57 |  |  |  |  | 24
59 |  |  |  |  | 26
61 |  |  |  |  | 28
62 |  |  |  |  | 29
63 |  |  |  |  | 30
64 |  |  |  |  | 32
69 |  |  |  |  | 33
70 |  |  |  |  | 37
71 |  |  |  |  | 38
74 |  |  |  |  | 39
75 |  |  |  |  | 40
76 |  |  |  |  | 41
77 |  |  |  |  | 44
79 |  |  |  |  | 46
80 |  |  |  |  | 47
81 |  |  |  |  | 48
91 |  |  |  |  | 49
93 |  |  |  |  | 50
95 |  |  |  |  | 52
99 |  |  |  |  | 56
100 |  |  |  |  | 58
101 |  |  |  |  | 60
102 |  |  |  |  | 65
103 |  |  |  |  | 66
107 |  |  |  |  | 67
108 |  |  |  |  | 68
109 |  |  |  |  | 72
112 |  |  |  |  | 73
114 |  |  |  |  | 78
117 |  |  |  |  | 82
142 |  |  |  |  | 83
147 |  |  |  |  | 84
152 |  |  |  |  | 85
155 |  |  |  |  | 86
156 |  |  |  |  | 87
159 |  |  |  |  | 88
160 |  |  |  |  | 89
161 |  |  |  |  | 90
162 |  |  |  |  | 92
167 |  |  |  |  | 94
168 |  |  |  |  | 96
171 |  |  |  |  | 97
173 |  |  |  |  | 98
174 |  |  |  |  | 104
184 |  |  |  |  | 105
215 |  |  |  |  | 106
216 |  |  |  |  | 110
217 |  |  |  |  | 111
230 |  |  |  |  | 113
231 |  |  |  |  | 115
116
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
143
144
145
146
148
149
150
151
153
154
157
158
163
164
165
166
169
170
172
175
176
177
178
179
180
181
182
183
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
218
219
220
221
222
223
224
225
226
227
228
229
232
233
234
235