## SOP
Standard of Performance data for the Month of March-2019
Name of Transmiossion License : POWER GRID CORPORATION OF INDIA LTD., WESTERN REGION-I
744
ANNEXURE-A
Sl.No | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) | [5 empty] | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by WRLDC
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available |  | Deemed Available
1 | WR1_L_001 | 400kV KORBA-KORBA(WEST) | 14 | WRTS-I
|  | 400kV KORBA-KORBA(WEST) Total | [21 empty] | 100%
2 | WR1_L_002 | 400kV KORBA-BHILAI I | 197 | WRTS-I | [18 empty] | WRLDC
|  | 400kV KORBA-BHILAI I Total | [21 empty] | 100%
3 | WR1_L_003 | 400kV KORBA-BHILAI II | 192 | WRTS-I | [18 empty] | WRLDC
|  | 400kV KORBA-BHILAI II Total | [21 empty] | 100%
4 | WR1_L_004 | 400kV BHILAI-KORADI | 272 | WRTS-I | [18 empty] | WRLDC
|  | 400kV BHILAI-KORADI Total | [21 empty] | 100%
5 | WR1_L_005 | 400kV KORADI-SATPURA | 149 | WRTS-I |  | 2019-03-28 | 10:35 | 2019-03-28 | 20:28 |  |  |  | 9.8833 | 0 | 0 | 0 | For AMP work | OSPT |  |  |  | For AMP work | WRLDC
|  | 400kV KORADI-SATPURA Total | [10 empty] | 9.8833 | [10 empty] | 98.67%
6 | WR1_L_006 | 400kV RAIPUR-BHILAI I | 13 | WRTS-I
|  | 400kV RAIPUR-BHILAI I Total | [21 empty] | 100%
7 | WR1_L_007 | 400kV BHILAI-BHADRAVATI I | 322 | WRTS-I |  | 2019-03-29 | 9:42 | 2019-03-29 | 20:58 |  |  |  | 11.2667 | 0 | 0 | 0 | For AMP of Line equipments at Bhilai SS and Line AMP works. | OSPT |  |  |  | For AMP of Line equipments at Bhilai SS and Line AMP works.
|  | 400kV BHILAI-BHADRAVATI I Total | [10 empty] | 11.2667 | [10 empty] | 98.49%
8 | WR1_L_008 | 400kV RAIPUR-BHADRAVATI I | 333 | WRTS-I |  | 2019-03-27 | 10:55 | 2019-03-27 | 22:37 |  |  |  | 11.7 | 0 | 0 | 0 | Line AMP works | OSPT |  |  |  | Line AMP works
[6 empty] | 2019-03-30 | 11:51 | 2019-03-30 | 11:51 |  |  |  | 0 | 0 | 0 | 0 | Line A/R s on B phase to E fault, FC-1.6KA,FL-211.57Km from Bhadrawati end | LART
[6 empty] | 2019-03-30 | 11:51 | 2019-03-30 | 11:51 |  |  |  | 11.7 | 0 | 0 | 0 | Line A/R s on B phase to E fault, FC-1.6KA,FL-211.57Km from Bhadrawati end | LART
[6 empty] | 2019-03-30 | 11:51 | 2019-03-30 | 11:51 |  |  |  | 11.7 | 0 | 0 | 0 | Line A/R s on B phase to E fault, FC-1.6KA,FL-211.57Km from Bhadrawati end | LART
[6 empty] | 2019-03-30 | 11:51 | 2019-03-30 | 11:51 |  |  |  | 11.7 | 0 | 0 |  |  | 0 |  |  |  | Line A/R s on B phase to E fault, FC-1.6KA,FL-211.57Km from Bhadrawati end
|  | 400kV RAIPUR-BHADRAVATI I Total | [10 empty] | 11.7 | [10 empty] | 98.43%
9 | WR1_L_009 | 400kV RAIPUR-BHADRAVATI II | 345.55 | WRTS-I |  | 2019-03-14 | 9:20 | 2019-03-14 | 20:19 |  |  |  | 10.9833 | 0 | 0 | 0 | For lineAMP works, 400kV Raipur-Bhadrawti-III A/R to be keep on Non-auto mode. | OSPT |  |  |  | For lineAMP works, 400kV Raipur-Bhadrawti-III A/R to be keep on Non-auto mode.
|  | 400kV RAIPUR-BHADRAVATI II Total | [10 empty] | 10.9833 | [10 empty] | 98.52%
10 | WR1_L_010 | 400kV RAIPUR-BHADRAVATI III | 345.55 | WRTS-I |  | 2019-03-14 | 18:02 | 2019-03-14 | 18:44 |  |  |  | 0 | 0 | 0.7 | 0 | Line tripped on R-G fault , due to burning of crop residue below the line conductor by farmers. Photographs attached | LMAC |  |  |  | Line tripped on R-G fault , due to burning of crop residue below the line conductor by farmers. Photographs attached | WRLDC
|  | 400kV RAIPUR-BHADRAVATI III Total | [10 empty] | 0 | [10 empty] | 100%
11 | WR1_L_011 | 400kV BHADRAVATI-CHANDRAPUR I | 20 | WRTS-I | [18 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR I Total | [21 empty] | 100%
12 | WR1_L_012 | 400kV BHADRAVATI-CHANDRAPUR II | 20 | WRTS-I | [18 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR II Total | [21 empty] | 100%
13 | WR1_L_013 | 400kV BHADRAVATI-CHANDRAPUR III | 22.42 | WRTS-I | [18 empty] | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR III Total | [21 empty] | 100%
14 | WR1_L_014 | 400kV BHADRAVATI-CHANDRAPUR IV | 22.42 | WRTS-I |  | 2019-03-29 | 13:22 | 2019-03-29 | 14:14 |  |  |  | 0 | 0.86667 | 0 | 0 | Line tripped at Bhadrawati end only on receipt of DT from chandrapur MSETCL end while tracing DC earthfault. | OMSU |  |  |  | Line tripped at Bhadrawati end only on receipt of DT from chandrapur MSETCL end while tracing DC earthfault. | WRLDC
|  | 400kV BHADRAVATI-CHANDRAPUR IV Total | [10 empty] | 0 | [10 empty] | 100%
15 | WR1_L_015 | 400kV MAHAN-VINDHYACHAL | 19 | WRTS-I | [18 empty] | WRLDC
|  | 400kV MAHAN-VINDHYACHAL Total | [21 empty] | 100%
16 | WR1_L_016 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2019-03-18 | 10:53 | 2019-03-18 | 19:53 |  |  |  | 0 | 0 | 0 | 9 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end. Bay Belongs to NTPC | OSPD |  |  |  | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end. Bay Belongs to NTPC | WRLDC
[6 empty] | 2019-03-19 | 8:53 | 2019-03-19 | 19:39 |  |  |  | 0 | 0 | 0 | 10.7667 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end | OSPD
[6 empty] | 2019-03-20 | 8:57 | 2019-03-20 | 16:50 |  |  |  | 0 | 0 | 0 | 7.8833 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end | OSPD
[6 empty] | 2019-03-26 | 8:43 | 2019-03-26 | 19:25 |  |  |  | 0 | 0 | 0 | 10.7 | Line outage availed by Sipat (NTPC) for planned maintenance work. Bay belongs to NTPC | OSPD
[6 empty] | 2019-03-19 | 8:53 | 2019-03-19 | 19:39 |  |  |  | 0 | 0 | 0 | 10.7667 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end | OSPD
[6 empty] | 2019-03-20 | 8:57 | 2019-03-20 | 16:50 |  |  |  | 0 | 0 | 0 | 7.8833 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end | OSPD
[6 empty] | 2019-03-26 | 8:43 | 2019-03-26 | 19:25 |  |  |  | 0 | 0 | 0 | 10.7 | Line outage availed by Sipat (NTPC) for planned maintenance work. Bay belongs to NTPC | OSPD
[6 empty] | 2019-03-19 | 8:53 | 2019-03-19 | 19:39 |  |  |  | 0 | 0 | 0 | 10.7667 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end | OSPD
[6 empty] | 2019-03-20 | 8:57 | 2019-03-20 | 16:50 |  |  |  | 0 | 0 | 0 | 7.8833 | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end | OSPD
[6 empty] | 2019-03-26 | 8:43 | 2019-03-26 | 19:25 |  |  |  | 0 | 0 | 0 | 10.7 | Line outage availed by Sipat (NTPC) for planned maintenance work. Bay belongs to NTPC | OSPD
[6 empty] | 2019-03-19 | 8:53 | 2019-03-19 | 19:39 |  |  |  | 0 | 0 | 0 |  |  | 10.7667 |  |  |  | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end
[6 empty] | 2019-03-20 | 8:57 | 2019-03-20 | 16:50 |  |  |  | 0 | 0 | 0 |  |  | 7.8833 |  |  |  | Outage availed by NTPC Korba for erection of new LR of Mahan line at Korba NTPC end
[6 empty] | 2019-03-26 | 8:43 | 2019-03-26 | 19:25 |  |  |  | 0 | 0 | 0 |  |  | 10.7 |  |  |  | Line outage availed by Sipat (NTPC) for planned maintenance work. Bay belongs to NTPC
|  | 400kV KORBA-MAHAN Total | [10 empty] | 0 | [10 empty] | 100%
17 | WR1_L_017 | 400kV VINDHYACHAL-KORBA II | 288.994 | WRTS-I |  | 2019-03-04 | 10:54 | 2019-03-04 | 11:35 |  |  |  | 0.68333 | 0 | 0 | 0 | Outage availed by NTPC Korba For Bay PM and Shunt reactor PM and LA replacement work at Korba end. Line charged after taking out LR from service. | OSPT |  |  |  | Outage availed by NTPC Korba For Bay PM and Shunt reactor PM and LA replacement work at Korba end. Line charged after taking out LR from service.
[6 empty] | 2019-03-05 | 17:35 | 2019-03-05 | 18:17 |  |  |  | 0.7 | 0 | 0 | 0 | Outage availed by NTPC Korba For Bay PM and Shunt reactor PM and LA replacement work at Korba end. Line outage facilitated for taking LR in service at Korba(NTPC) end. | OSPT
[6 empty] | 2019-03-21 | 18:04 | 2019-03-21 | 20:19 |  |  |  | 0 | 0 | 2.25 | 0 | Line tripped on B-E fault during heavy wind, rain and thunderstorm. | LNCC
[6 empty] | 2019-03-05 | 17:35 | 2019-03-05 | 18:17 |  |  |  | 1.3833 | 0 | 0 | 0 | Outage availed by NTPC Korba For Bay PM and Shunt reactor PM and LA replacement work at Korba end. Line outage facilitated for taking LR in service at Korba(NTPC) end. | OSPT
[6 empty] | 2019-03-21 | 18:04 | 2019-03-21 | 20:19 |  |  |  | 0 | 0 | 2.25 | 0 | Line tripped on B-E fault during heavy wind, rain and thunderstorm. | LNCC
[6 empty] | 2019-03-05 | 17:35 | 2019-03-05 | 18:17 |  |  |  | 1.3833 | 0 | 0 | 0 | Outage availed by NTPC Korba For Bay PM and Shunt reactor PM and LA replacement work at Korba end. Line outage facilitated for taking LR in service at Korba(NTPC) end. | OSPT
[6 empty] | 2019-03-21 | 18:04 | 2019-03-21 | 20:19 |  |  |  | 0 | 0 | 2.25 | 0 | Line tripped on B-E fault during heavy wind, rain and thunderstorm. | LNCC
[6 empty] | 2019-03-05 | 17:35 | 2019-03-05 | 18:17 |  |  |  | 1.3833 | 0 | 0 |  |  | 0 |  |  |  | Outage availed by NTPC Korba For Bay PM and Shunt reactor PM and LA replacement work at Korba end. Line outage facilitated for taking LR in service at Korba(NTPC) end.
[6 empty] | 2019-03-21 | 18:04 | 2019-03-21 | 20:19 |  |  |  | 0 | 0 | 2.25 |  |  | 0 |  |  |  | Line tripped on B-E fault during heavy wind, rain and thunderstorm.
|  | 400kV VINDHYACHAL-KORBA II Total | [10 empty] | 1.3833 | [10 empty] | 99.81%
18 | WR1_L_018 | 400kV SATPURA-SEONI | 1.507 | WRTS-I
|  | 400kV SATPURA-SEONI Total | [21 empty] | 100%
19 | WR1_L_019 | 400kV BHILAI-SEONI | 1.498 | WRTS-I |  | 2019-03-02 | 10:16 | 2019-03-19 | 20:35 |  |  |  | 0 | 0 | 0 | 418.3167 | Outage availed by MPPTCL for LILO work of 400KV Bhilai -Seoni line at 400/132KV S/s Kirnapur | OSPD |  |  |  | Outage availed by MPPTCL for LILO work of 400KV Bhilai -Seoni line at 400/132KV S/s Kirnapur
|  | 400kV BHILAI-SEONI Total | [10 empty] | 0 | [10 empty] | 100%
20 | WR1_L_020 | 400kV BHILAI-BHATAPARA | 90.453 | WRTS-I
|  | 400kV BHILAI-BHATAPARA Total | [21 empty] | 100%
21 | WR1_L_021 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I | [18 empty] | WRLDC
|  | 400kV BHATAPARA-KORBA Total | [21 empty] | 100%
22 | WR1_L_022 | 400kV KORBA-SIPAT | 68.653 | WRTS-I
|  | 400kV KORBA-SIPAT Total | [21 empty] | 100%
23 | WR1_L_023 | 400kV RAIPUR-SIPAT I | 149.12 | WRTS-I |  | 2019-03-19 | 9:02 | 2019-03-19 | 20:21 |  |  |  | 0 | 11.3167 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections of Line. Ckt-2 A/R in Non-auto mode required. | OMSU |  |  |  | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections of Line. Ckt-2 A/R in Non-auto mode required.
[6 empty] | 2019-03-20 | 8:56 | 2019-03-20 | 19:25 |  |  |  | 0 | 10.4833 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections of Line. Ckt-2 A/R in Non-auto mode required. | OMSU
[6 empty] | 2019-03-20 | 8:56 | 2019-03-20 | 19:25 |  |  |  | 0 | 10.4833 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections of Line. Ckt-2 A/R in Non-auto mode required. | OMSU
[6 empty] | 2019-03-20 | 8:56 | 2019-03-20 | 19:25 |  |  |  | 0 | 10.4833 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections of Line. Ckt-2 A/R in Non-auto mode required. | OMSU
[6 empty] | 2019-03-20 | 8:56 | 2019-03-20 | 19:25 |  |  |  | 0 | 10.4833 | 0 |  |  | 0 |  |  |  | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections of Line. Ckt-2 A/R in Non-auto mode required.
|  | 400kV RAIPUR-SIPAT I Total | [10 empty] | 0 | [10 empty] | 100%
24 | WR1_L_024 | 400KV RAIPUR-SIPAT II | 149.12 | WRTS-I |  | 2019-03-23 | 8:30 | 2019-03-23 | 21:08 |  |  |  | 0 | 12.6333 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. Ckt-1 A/R in Non-auto mode required. | OMSU |  |  |  | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. Ckt-1 A/R in Non-auto mode required.
[6 empty] | 2019-03-24 | 9:21 | 2019-03-24 | 21:28 |  |  |  | 0 | 12.1167 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. Ckt-1 A/R in Non-auto mode required. | OMSU
[6 empty] | 2019-03-24 | 9:21 | 2019-03-24 | 21:28 |  |  |  | 0 | 12.1167 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. Ckt-1 A/R in Non-auto mode required. | OMSU
[6 empty] | 2019-03-24 | 9:21 | 2019-03-24 | 21:28 |  |  |  | 0 | 12.1167 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. Ckt-1 A/R in Non-auto mode required. | OMSU
[6 empty] | 2019-03-24 | 9:21 | 2019-03-24 | 21:28 |  |  |  | 0 | 12.1167 | 0 |  |  | 0 |  |  |  | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. Ckt-1 A/R in Non-auto mode required.
|  | 400KV RAIPUR-SIPAT II Total | [10 empty] | 0 | [10 empty] | 100%
25 | WR1_L_025 | 400kV RAIPUR-SIPAT III | 162.04 | WRTS-I
|  | 400kV RAIPUR-SIPAT III Total | [21 empty] | 100%
26 | WR1_L_026 | 765kV BILASPUR-SIPAT I | 21.507 | WRTS-I |  | 2019-03-26 | 8:57 | 2019-03-27 | 21:26 |  |  |  | 0 | 0 | 0 | 36.4833 | Line outage availed by Sipat (NTPC) for planned maintenance work. Bay belongs to NTPC | OSPD |  |  |  | Line outage availed by Sipat (NTPC) for planned maintenance work. Bay belongs to NTPC
|  | 765kV BILASPUR-SIPAT I Total | [10 empty] | 0 | [10 empty] | 100%
27 | WR1_L_027 | 765kV SEONI-BILASPUR I | 337.046 | WRTS-I | [18 empty] | WRLDC
|  | 765kV SEONI-BILASPUR I Total | [21 empty] | 100%
28 | WR1_L_028 | 765kV BILASPUR-SIPAT II | 22.216 | WRTS-I |  | 2019-03-13 | 8:54 | 2019-03-14 | 1:54 |  |  |  | 0 | 0 | 0 | 17 | For construction works of new Rajnandgaon line. | LCSD |  |  |  | For construction works of new Rajnandgaon line.
[6 empty] | 2019-03-14 | 1:54 | 2019-03-14 | 6:30 |  |  |  | 0 | 4.6 | 0 | 0 | Charging Code issued, but line did not charged due to Isolator alignment problem in main bay and LR isolator at NTPC Sipat end | OMSU
[6 empty] | 2019-03-14 | 1:54 | 2019-03-14 | 6:30 |  |  |  | 0 | 4.6 | 0 | 0 | Charging Code issued, but line did not charged due to Isolator alignment problem in main bay and LR isolator at NTPC Sipat end | OMSU
[6 empty] | 2019-03-14 | 1:54 | 2019-03-14 | 6:30 |  |  |  | 0 | 4.6 | 0 | 0 | Charging Code issued, but line did not charged due to Isolator alignment problem in main bay and LR isolator at NTPC Sipat end | OMSU
[6 empty] | 2019-03-14 | 1:54 | 2019-03-14 | 6:30 |  |  |  | 0 | 4.6 | 0 |  |  | 0 |  |  |  | Charging Code issued, but line did not charged due to Isolator alignment problem in main bay and LR isolator at NTPC Sipat end
|  | 765kV BILASPUR-SIPAT II Total | [10 empty] | 0 | [10 empty] | 100%
29 | WR1_L_029 | 765kV SEONI-BILASPUR II | 338.33 | WRTS-I
|  | 765kV SEONI-BILASPUR II Total | [21 empty] | 100%
30 | WR1_L_030 | 765kV SEONI-WARDHA I | 267.894 | WRTS-I
|  | 765kV SEONI-WARDHA I Total | [21 empty] | 100%
31 | WR1_L_031 | 765kV SEONI-WARDHA II | 260.763 | WRTS-I
|  | 765kV SEONI-WARDHA II Total | [21 empty] | 100%
32 | WR1_L_032 | 400kV WARDHA-AKOLA I | 161.865 | WRTS-I | [18 empty] | WRLDC
|  | 400kV WARDHA-AKOLA I Total | [21 empty] | 100%
33 | WR1_L_033 | 400kV WARDHA-AKOLA II | 161.865 | WRTS-I | [18 empty] | WRLDC
|  | 400kV WARDHA-AKOLA II Total | [21 empty] | 100%
34 | WR1_L_034 | 400kV AURANGABAD (PG) -AKOLA I | 289.966 | WRTS-I
|  | 400kV AURANGABAD (PG) -AKOLA I Total | [21 empty] | 100%
35 | WR1_L_035 | 400kV AURANGABAD (PG) -AKOLA II | 289.966 | WRTS-I | [18 empty] | WRLDC
|  | 400kV AURANGABAD (PG) -AKOLA II Total | [21 empty] | 100%
36 | WR1_L_036 | 400kV BHADRAVATI-PARLI I | 378.667 | WRTS-I
|  | 400kV BHADRAVATI-PARLI I Total | [21 empty] | 100%
37 | WR1_L_037 | 400kV PARLI(PG)-PARLI(MSETCL) I | 4.958 | WRTS-I
|  | 400kV PARLI(PG)-PARLI(MSETCL) I Total | [21 empty] | 100%
38 | WR1_L_038 | 400kV PARLI(PG)-PARLI(MSETCL) II | 4.958 | WRTS-I
|  | 400kV PARLI(PG)-PARLI(MSETCL) II Total | [21 empty] | 100%
39 | WR1_L_039 | 400kV KORBA-RAIPUR III | 212.83 | WRTS-I
|  | 400kV KORBA-RAIPUR III Total | [21 empty] | 100%
40 | WR1_L_040 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I | [18 empty] | WRLDC
|  | 400kV KORBA-RAIPUR IV Total | [21 empty] | 100%
41 | WR1_L_041 | 400kV WARDHA-PARLI I | 336.939 | WRTS-I | [18 empty] | WRLDC
|  | 400kV WARDHA-PARLI I Total | [21 empty] | 100%
42 | WR1_L_042 | 400kV WARDHA-PARLI II | 336.939 | WRTS-I
|  | 400kV WARDHA-PARLI II Total | [21 empty] | 100%
43 | WR1_L_043 | 400kV WARDHA-MAUDA II | 123.45 | WRTS-I
|  | 400kV WARDHA-MAUDA II Total | [21 empty] | 100%
44 | WR1_L_044 | 400kV KORBA-VANDANA | 14.768 | WRTS-I
|  | 400kV KORBA-VANDANA Total | [21 empty] | 100%
45 | WR1_L_045 | 400kV VANDANA-BIRSINGHPUR | 211.874 | WRTS-I
|  | 400kV VANDANA-BIRSINGHPUR Total | [21 empty] | 100%
46 | WR1_L_046 | 400kV RAIPUR-WARDHA I | 370.565 | WRTS-I |  | 2019-03-31 | 13:35 | 2019-03-31 | 13:35 |  |  |  | 0 | 0 | 0 | 0 | Line A/R successful at both ends on B phase to E fault, FC-5.0 KA,FL-72.9 Km from Wardha end & B-phase to E fault M1: FD-304.6km, FC-1.4kA; M2: FD-339.1km FC-1.43kA from Raipur end. | LART |  |  |  | Line A/R successful at both ends on B phase to E fault, FC-5.0 KA,FL-72.9 Km from Wardha end & B-phase to E fault M1: FD-304.6km, FC-1.4kA; M2: FD-339.1km FC-1.43kA from Raipur end.
|  | 400kV RAIPUR-WARDHA I Total | [10 empty] | 0 | [10 empty] | 100%
47 | WR1_L_047 | 400kV RAIPUR-WARDHA II | 370.565 | WRTS-I
|  | 400kV RAIPUR-WARDHA II Total | [21 empty] | 100%
48 | WR1_L_048 | 400kV RAIPUR-DURG I | 21.43 | WRTS-I
|  | 400kV RAIPUR-DURG I Total | [21 empty] | 100%
49 | WR1_L_049 | 400kV RAIPUR-DURG II | 21.43 | WRTS-I
|  | 400kV RAIPUR-DURG II Total | [21 empty] | 100%
50 | WR1_L_050 | 400kV RAIGARH-KOTRA PS I | 6.288 | WRTS-I |  | 2019-03-05 | 20:34 | 2019-03-05 | 20:56 |  |  |  | 0 | 0 | 0 | 0.36667 | Line hand tripped and idle charged from Raigarh end for fault level control. | LPRD |  |  |  | Line hand tripped and idle charged from Raigarh end for fault level control.
|  | 400kV RAIGARH-KOTRA PS I Total | [10 empty] | 0 | [10 empty] | 100%
51 | WR1_L_051 | 400kV RAIGARH-KOTRA PS II | 6.288 | WRTS-I |  | 2019-03-05 | 20:35 | 2019-03-05 | 20:57 |  |  |  | 0 | 0 | 0 | 0.36667 | Line hand tripped and idle charged from Raigarh end for fault level control. | LPRD |  |  |  | Line hand tripped and idle charged from Raigarh end for fault level control.
|  | 400kV RAIGARH-KOTRA PS II Total | [10 empty] | 0 | [10 empty] | 100%
52 | WR1_L_052 | 765kV TAMNAR PS-KOTRA PS I | 47.986 | WRTS-I
|  | 765kV TAMNAR PS-KOTRA PS I Total | [21 empty] | 100%
53 | WR1_L_053 | 765kV TAMNAR PS-KOTRA PS II | 47.986 | WRTS-I
|  | 765kV TAMNAR PS-KOTRA PS II Total | [21 empty] | 100%
54 | WR1_L_054 | 765kV KOTRA PS-DURG PS I | 239.843 | WRTS-I |  | 2019-03-01 | 0:00 | 2019-03-12 | 9:40 |  |  |  | 0 | 0 | 0 | 273.6667 | Line is H/T as per WRLDC instructions for voltage regulation and LR is converted to BR at Kotra end. | LVRD |  |  |  | Line is H/T as per WRLDC instructions for voltage regulation and LR is converted to BR at Kotra end. | WRLDC
|  | 765kV KOTRA PS-DURG PS I Total | [10 empty] | 0 | [10 empty] | 100%
55 | WR1_L_055 | 765kV KOTRA PS-DURG PS II | 239.843 | WRTS-I |  | 2019-03-21 | 18:25 | 2019-03-31 | 24:00 |  |  |  | 0 | 0 | 0 | 245.5833 | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at Kotra end. | LVRD |  |  |  | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at Kotra end.
|  | 765kV KOTRA PS-DURG PS II Total | [10 empty] | 0 | [10 empty] | 100%
56 | WR1_L_056 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 52.563 | WRTS-I |  | 2019-03-05 | 9:30 | 2019-03-05 | 11:59 |  |  |  | 0 | 2.4833 | 0 | 0 | Line tripped upon receival of DT from Aurangabad (Waluj), due to Bus tripped end Aurangabad (Waluj-MSETCL). | SBBU |  |  |  | Line tripped upon receival of DT from Aurangabad (Waluj), due to Bus tripped end Aurangabad (Waluj-MSETCL).
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II Total | [10 empty] | 0 | [10 empty] | 100%
57 | WR1_L_057 | 400kV BHADRAVATI-DHARIWAL TPP II | 2.923 | WRTS-I
|  | 400kV BHADRAVATI-DHARIWAL TPP II Total | [21 empty] | 100%
58 | WR1_L_058 | 400kV DHARIWAL TPP-PARLI II | 375.785 | WRTS-I
|  | 400kV DHARIWAL TPP-PARLI II Total | [21 empty] | 100%
59 | WR1_L_059 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 52.563 | WRTS-I
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I Total | [21 empty] | 100%
60 | WR1_L_060 | 765KV DURG PS - D'JAIGARH | 357.62 | WRTS-I
|  | 765KV DURG PS - D'JAIGARH Total | [21 empty] | 100%
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I | [18 empty] | WRLDC
|  | 765kV WARDHA - AURANGABAD(PG) I Total | [21 empty] | 100%
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2019-03-15 | 21:54 | 2019-03-22 | 6:38 |  |  |  | 0 | 0 | 0 | 152.7333 | Line H/T as per WRLDC instructions for voltage regulation and LR converted to BR at Wardha end. | LVRD |  |  |  | Line H/T as per WRLDC instructions for voltage regulation and LR converted to BR at Wardha end. | WRLDC
[6 empty] | 2019-03-28 | 20:38 | 2019-03-31 | 24:00 |  |  |  | 0 | 0 | 0 | 75.3667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Wardha end | LVRD
[6 empty] | 2019-03-28 | 20:38 | 2019-03-31 | 24:00 |  |  |  | 0 | 0 | 0 | 75.3667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Wardha end | LVRD
[6 empty] | 2019-03-28 | 20:38 | 2019-03-31 | 24:00 |  |  |  | 0 | 0 | 0 | 75.3667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Wardha end | LVRD
[6 empty] | 2019-03-28 | 20:38 | 2019-03-31 | 24:00 |  |  |  | 0 | 0 | 0 |  |  | 75.3667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Wardha end
|  | 765kV WARDHA - AURANGABAD(PG) II Total | [10 empty] | 0 | [10 empty] | 100%
63 | WR1_L_063 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2019-03-16 | 22:26 | 2019-03-29 | 6:12 |  |  |  | 0 | 0 | 0 | 295.7667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg end (At 22:50 Hrs) | LVRD |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg end (At 22:50 Hrs) | WRLDC
|  | 765kV DURG PS -WARDHA_1 Total | [10 empty] | 0 | [10 empty] | 100%
64 | WR1_L_064 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2019-03-04 | 17:43 | 2019-03-15 | 5:55 |  |  |  | 0 | 0 | 0 | 252.2 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg end. | LVRD |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg end. | WRLDC
|  | 765kV DURG PS -WARDHA_2 Total | [10 empty] | 0 | [10 empty] | 100%
65 | WR1_L_065 | 400Kv PARLI-PUNE(GIS)_1 | 9.57 | WRTS-I |  | 2019-03-01 | 12:32 | 2019-03-01 | 18:59 |  |  |  | 6.45 | 0 | 0 | 0 | For Line AMP works, Both circuits outage required being M/c Towers. A/R of 400kV Parli-Pune(GIS)-2 to be keep on Non-auto mode during this period. | OSPT |  |  |  | For Line AMP works, Both circuits outage required being M/c Towers. A/R of 400kV Parli-Pune(GIS)-2 to be keep on Non-auto mode during this period. | WRLDC
|  | 400Kv PARLI-PUNE(GIS)_1 Total | [10 empty] | 6.45 | [10 empty] | 99.13%
66 | WR1_L_066 | 400Kv PARLI-PUNE(GIS)_2 | 9.57 | WRTS-I |  | 2019-03-02 | 9:44 | 2019-03-02 | 19:06 |  |  |  | 9.3667 | 0 | 0 | 0 | For Line AMP works, Both circuits outage required being M/c Towers. A/R of 400kV Parli - Pune (GIS) - 1 to be keep on Non-auto mode during this period. | OSPT |  |  |  | For Line AMP works, Both circuits outage required being M/c Towers. A/R of 400kV Parli - Pune (GIS) - 1 to be keep on Non-auto mode during this period.
[6 empty] | 2019-03-25 | 17:35 | 2019-03-25 | 18:27 |  |  |  | 0 | 0.86667 | 0 | 0 | Line tripped on R-phase to Earth fault, FD=23.36kk, FC=11.7kA from Parli end & FD=239.8km, FC=1.88kA from Pune-GIS end. Fauly is in Adani section | OMSU
[6 empty] | 2019-03-25 | 17:35 | 2019-03-25 | 18:27 |  |  |  | 9.3667 | 0.86667 | 0 | 0 | Line tripped on R-phase to Earth fault, FD=23.36kk, FC=11.7kA from Parli end & FD=239.8km, FC=1.88kA from Pune-GIS end. Fauly is in Adani section | OMSU
[6 empty] | 2019-03-25 | 17:35 | 2019-03-25 | 18:27 |  |  |  | 9.3667 | 0.86667 | 0 | 0 | Line tripped on R-phase to Earth fault, FD=23.36kk, FC=11.7kA from Parli end & FD=239.8km, FC=1.88kA from Pune-GIS end. Fauly is in Adani section | OMSU
[6 empty] | 2019-03-25 | 17:35 | 2019-03-25 | 18:27 |  |  |  | 9.3667 | 0.86667 | 0 |  |  | 0 |  |  |  | Line tripped on R-phase to Earth fault, FD=23.36kk, FC=11.7kA from Parli end & FD=239.8km, FC=1.88kA from Pune-GIS end. Fauly is in Adani section
|  | 400Kv PARLI-PUNE(GIS)_2 Total | [10 empty] | 9.3667 | [10 empty] | 98.74%
67 | WR1_L_067 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 9.978 | WRTS-I
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 Total | [21 empty] | 100%
68 | WR1_L_068 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 9.978 | WRTS-I
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 Total | [21 empty] | 100%
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2019-03-01 | 0:00 | 2019-03-01 | 11:52 |  |  |  | 0 | 0 | 0 | 11.8667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both ends. | LVRD |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both ends. | WRLDC
[6 empty] | 2019-03-02 | 20:18 | 2019-03-12 | 11:27 |  |  |  | 0 | 0 | 0 | 231.15 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end. | LVRD
[6 empty] | 2019-03-13 | 0:31 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 | 125.6667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end. | LVRD
[6 empty] | 2019-03-18 | 20:16 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 | 34.05 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both ends. | LVRD
[6 empty] | 2019-03-21 | 18:14 | 2019-03-22 | 12:16 |  |  |  | 0 | 0 | 0 | 18.0333 | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at both end of line. | LVRD
[6 empty] | 2019-03-02 | 20:18 | 2019-03-12 | 11:27 |  |  |  | 0 | 0 | 0 | 231.15 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end. | LVRD
[6 empty] | 2019-03-13 | 0:31 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 | 125.6667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end. | LVRD
[6 empty] | 2019-03-18 | 20:16 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 | 34.05 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both ends. | LVRD
[6 empty] | 2019-03-21 | 18:14 | 2019-03-22 | 12:16 |  |  |  | 0 | 0 | 0 | 18.0333 | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at both end of line. | LVRD
[6 empty] | 2019-03-02 | 20:18 | 2019-03-12 | 11:27 |  |  |  | 0 | 0 | 0 | 231.15 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end. | LVRD
[6 empty] | 2019-03-13 | 0:31 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 | 125.6667 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end. | LVRD
[6 empty] | 2019-03-18 | 20:16 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 | 34.05 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both ends. | LVRD
[6 empty] | 2019-03-21 | 18:14 | 2019-03-22 | 12:16 |  |  |  | 0 | 0 | 0 | 18.0333 | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at both end of line. | LVRD
[6 empty] | 2019-03-02 | 20:18 | 2019-03-12 | 11:27 |  |  |  | 0 | 0 | 0 |  |  | 231.15 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end.
[6 empty] | 2019-03-13 | 0:31 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 |  |  | 125.6667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both end.
[6 empty] | 2019-03-18 | 20:16 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 |  |  | 34.05 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at both ends.
[6 empty] | 2019-03-21 | 18:14 | 2019-03-22 | 12:16 |  |  |  | 0 | 0 | 0 |  |  | 18.0333 |  |  |  | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at both end of line.
|  | 765kV PUNE(GIS)-SOLAPUR Total | [10 empty] | 0 | [10 empty] | 100%
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I | [18 empty] | WRLDC
|  | 765kV WARDHA - AURANGABAD(PG) III Total | [21 empty] | 100%
71 | WR1_L_071 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I |  | 2019-03-21 | 15:07 | 2019-03-27 | 21:07 |  |  |  | 0 | 0 | 0 | 0 | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at Wardha end. | LVRD |  |  |  | Line H/T as per WRLDC instructions for voltage regulation and LR converted as BR at Wardha end. | WRLDC
|  | 765kV WARDHA - AURANGABAD(PG) IV Total | [10 empty] | 0 | [10 empty] | 100%
72 | WR1_L_072 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | 11.2 | WRTS-I
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 Total | [21 empty] | 100%
73 | WR1_L_073 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | 11.2 | WRTS-I
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 Total | [21 empty] | 100%
74 | WR1_L_074 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I |  | 2019-03-13 | 12:09 | 2019-03-13 | 15:05 |  |  |  | 2.9333 | 0 | 0 | 0 | Emergency outage availed for rectification of Earth wire suspension clamp at Tower No:372. | OSFT |  |  |  | Emergency outage availed for rectification of Earth wire suspension clamp at Tower No:372. | WRLDC
|  | 765kV DURG PS- CHAMPA_1 Total | [10 empty] | 2.9333 | [10 empty] | 99.61%
75 | WR1_L_075 | 765kV CHAMPA- KOTRA PS | 96.33 | WRTS-I
|  | 765kV CHAMPA- KOTRA PS Total | [21 empty] | 100%
76 | WR1_L_076 | 765kV AURANGABAD(PG)-SOLAPUR I | 279.57 | WRTS-I
|  | 765kV AURANGABAD(PG)-SOLAPUR I Total | [21 empty] | 100%
77 | WR1_L_077 | 765kV AURANGABAD(PG)-SOLAPUR II | 279.57 | WRTS-I
|  | 765kV AURANGABAD(PG)-SOLAPUR II Total | [21 empty] | 100%
78 | WR1_L_078 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I | [18 empty] | WRLDC
|  | 220kV KORBA(EAST)-BUDDHIPADAR III Total | [21 empty] | 100%
79 | WR1_L_079 | 400kV RAIPUR-RAIGARH I | 217.02 | WRTS-I |  | 2019-03-15 | 7:43 | 2019-03-15 | 19:42 |  |  |  | 11.9833 | 0 | 0 | 0 | For Line AMP & Ckt-2 A/R to be keept on Non-Auto mode | OSPT |  |  |  | For Line AMP & Ckt-2 A/R to be keept on Non-Auto mode | WRLDC
[6 empty] | 2019-03-25 | 11:38 | 2019-03-25 | 19:04 |  |  |  | 7.4333 | 0 | 0 | 0 | Emergency outage availed for attending hotspots in Jumper and at SS equipment at certain Locations | OSFT
[6 empty] | 2019-03-25 | 11:38 | 2019-03-25 | 19:04 |  |  |  | 19.4167 | 0 | 0 | 0 | Emergency outage availed for attending hotspots in Jumper and at SS equipment at certain Locations | OSFT
[6 empty] | 2019-03-25 | 11:38 | 2019-03-25 | 19:04 |  |  |  | 19.4167 | 0 | 0 | 0 | Emergency outage availed for attending hotspots in Jumper and at SS equipment at certain Locations | OSFT
[6 empty] | 2019-03-25 | 11:38 | 2019-03-25 | 19:04 |  |  |  | 19.4167 | 0 | 0 |  |  | 0 |  |  |  | Emergency outage availed for attending hotspots in Jumper and at SS equipment at certain Locations
|  | 400kV RAIPUR-RAIGARH I Total | [10 empty] | 19.4167 | [10 empty] | 97.39%
80 | WR1_L_080 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RAIGARH-ROURKELA II Total | [21 empty] | 100%
81 | WR1_L_081 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RAIGARH-IBEUL I Total | [21 empty] | 100%
82 | WR1_L_082 | 400kV IBEUL-JHARSUGUDA I | 20.03 | WRTS-I
400kV IBEUL-JHARSUGUDA I Total
83 | WR1_L_083 | 400kV JHARSUGUDA-ROURKELA I | 142.448 | WRTS-I
|  | 400kV JHARSUGUDA-ROURKELA I Total | [21 empty] | 100%
84 | WR1_L_084 | 400kV RANCHI-SIPAT I | 405.772 | WRTS-I |  | 2019-03-16 | 10:33 | 2019-03-16 | 14:45 |  |  |  | 4.2 | 0 | 0 | 0 | Emergency outage availed by ER-1 for attending hotspot and sparking on R-Ph Isolator contacts (421-89A) at Ranchi end. | OSFT |  |  |  | Emergency outage availed by ER-1 for attending hotspot and sparking on R-Ph Isolator contacts (421-89A) at Ranchi end. | LEFT
|  | 400kV RANCHI-SIPAT I Total | [10 empty] | 4.2 | [10 empty] | 99.44%
85 | WR1_L_085 | 400kV RANCHI-SIPAT II | 405.772 | WRTS-I
|  | 400kV RANCHI-SIPAT II Total | [21 empty] | 100%
86 | WR1_L_086 | 400kV RAIPUR-KSK III | 134.74 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RAIPUR-KSK III Total | [21 empty] | 100%
87 | WR1_L_087 | 400kV KSK-RKKML III | 82.248 | WRTS-I | [18 empty] | WRLDC
|  | 400kV KSK-RKKML III Total | [21 empty] | 100%
88 | WR1_L_088 | 400kV RKKML-RAIGARH III | 3.896 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RKKML-RAIGARH III Total | [21 empty] | 100%
89 | WR1_L_089 | 400kV RAIPUR-KSK IV | 161.82 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RAIPUR-KSK IV Total | [21 empty] | 100%
90 | WR1_L_090 | 400kV KSK-RAIGARH IV | 113.389 | WRTS-I | [18 empty] | WRLDC
|  | 400kV KSK-RAIGARH IV Total | [21 empty] | 100%
91 | WR1_L_091 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I |  | 2019-03-09 | 11:21 | 2019-03-09 | 23:47 |  |  |  | 0 | 0 | 0 | 12.4333 | For OPGC Line diversion (Rectification work at Railway crossing) Availed by ER-2 | LCSD |  |  |  | For OPGC Line diversion (Rectification work at Railway crossing) Availed by ER-2
|  | 400kV RAIGARH-JHARSUGUDA III Total | [10 empty] | 0 | [10 empty] | 100%
92 | WR1_L_092 | 400kV JHARSUGUDA-ROURKELA III | 143.06 | WRTS-I | [18 empty] | WRLDC
|  | 400kV JHARSUGUDA-ROURKELA III Total | [21 empty] | 100%
91 | WR1_L_093 | 400kV RAIGARH-JHARSUGUDA IV | 145.5 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RAIGARH-SUNDERGARH IV Total | [21 empty] | 100%
94 | WR1_L_094 | 400kV STERLITE-ROURKELA IV | 104.28 | WRTS-I | [18 empty] | WRLDC
|  | 400kV STERLITE-ROURKELA IV Total | [21 empty] | 100%
95 | WR1_L_095 | 765kV D'JAIGARH-BILASPUR | 90 | WRTS-I
|  | 765kV D'JAIGARH-BILASPUR Total | [21 empty] | 100%
96 | WR1_L_096 | 765kV D'JAIGARH-RANCHI I | 303 | WRTS-I
|  | 765kV D'JAIGARH-RANCHI I Total | [21 empty] | 100%
97 | WR1_L_097 | 765kV D'JAIGARH- JHARSUGUDA I | 149.789 | WRTS-I |  | 2019-03-09 | 16:10 | 2019-03-09 | 17:40 |  |  |  | 1.5 | 0 | 0 | 0 | While B-phase CT of Jharsuguda-4 failure Bus-bar protection operated & Jharsuguda-1 line tripped. | OMST |  |  |  | While B-phase CT of Jharsuguda-4 failure Bus-bar protection operated & Jharsuguda-1 line tripped. | WRLDC
|  | 765kV D'JAIGARH- JHARSUGUDA I Total | [10 empty] | 1.5 | [10 empty] | 99.8%
98 | WR1_L_098 | 765kV D'JAIGARH- JHARSUGUDA II | 149.789 | WRTS-I |  | 2019-03-22 | 14:57 | 2019-03-22 | 14:57 |  |  |  | 0 | 0 | 0 | 0 | Line A/R successful on Y-G fault through tie CB. Fault details from Dharamjaygarh: Main-I: 65km. 6.5kA, From Jharsuguda: 2.04kA, Z-I, Y-G, Fault distance not recorded in relay. | LART |  |  |  | Line A/R successful on Y-G fault through tie CB. Fault details from Dharamjaygarh: Main-I: 65km. 6.5kA, From Jharsuguda: 2.04kA, Z-I, Y-G, Fault distance not recorded in relay. | WRLDC
|  | 765kV D'JAIGARH- JHARSUGUDA II Total | [10 empty] | 0 | [10 empty] | 100%
99 | WR1_L_099 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I | 39.383 | WRTS-I
|  | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I Total | [21 empty] | 100%
100 | WR1_L_100 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II | 39.383 | WRTS-I
|  | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II Total | [21 empty] | 100%
| WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I
|  | 400kV KOLHAPUR (GIS)-MAPUSA I Total | [21 empty] | 100%
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I | [18 empty] | WRLDC
|  | 400kV KOLHAPUR (GIS)-MAPUSA II Total | [21 empty] | 100%
103 | WR1_L_103 | 400kV WARDHA-MAUDA I | 123.45 | WRTS-I
|  | 400kV WARDHA-MAUDA I Total | [21 empty] | 100%
104 | WR1_L_104 | 765kV D'JAIGARH-RANCHI II | 354 | WRTS-I | [18 empty] | WRLDC
|  | 765kV D'JAIGARH-RANCHI II Total | [21 empty] | 100%
105 | WR1_L_105 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 | 14.373 | WRTS-I | [18 empty] | WRLDC
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 Total | [21 empty] | 100%
106 | WR1_L_106 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 | 14.373 | WRTS-I
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 Total | [21 empty] | 100%
107 | WR1_L_107 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I | 14.387 | WRTS-I |  | 2019-03-02 | 9:34 | 2019-03-02 | 18:12 |  |  |  | 8.6333 | 0 | 0 | 0 | For Line AMP works, Both circuits outage required being M/c Towers. A/R of Aurangabad - Pune (GIS) - 2 to be keep on Non-auto mode during this period. | OSPT |  |  |  | For Line AMP works, Both circuits outage required being M/c Towers. A/R of Aurangabad - Pune (GIS) - 2 to be keep on Non-auto mode during this period. | WRLDC
|  | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I Total | [10 empty] | 8.6333 | [10 empty] | 98.84%
108 | WR1_L_108 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II | 14.387 | WRTS-I |  | 2019-03-01 | 12:04 | 2019-03-01 | 21:06 |  |  |  | 9.0333 | 0 | 0 | 0 | For Line AMP works, Both circuits outage required being M/c Towers. A/R of A'bad-Pune(GIS)-1 to be keep on Non-auto mode during this period. | OSPT |  |  |  | For Line AMP works, Both circuits outage required being M/c Towers. A/R of A'bad-Pune(GIS)-1 to be keep on Non-auto mode during this period. | WRLDC
[6 empty] | 2019-03-05 | 9:30 | 2019-03-05 | 12:08 |  |  |  | 0 | 2.6333 | 0 | 0 | Line tripped at Aurangabad (Waluj) only, due to Bus tripped end Aurangabad (Waluj-MSETCL). Line charged from Pune-GIS end. | SBBU
[6 empty] | 2019-03-05 | 9:30 | 2019-03-05 | 12:08 |  |  |  | 9.0333 | 2.6333 | 0 | 0 | Line tripped at Aurangabad (Waluj) only, due to Bus tripped end Aurangabad (Waluj-MSETCL). Line charged from Pune-GIS end. | SBBU
[6 empty] | 2019-03-05 | 9:30 | 2019-03-05 | 12:08 |  |  |  | 9.0333 | 2.6333 | 0 | 0 | Line tripped at Aurangabad (Waluj) only, due to Bus tripped end Aurangabad (Waluj-MSETCL). Line charged from Pune-GIS end. | SBBU
[6 empty] | 2019-03-05 | 9:30 | 2019-03-05 | 12:08 |  |  |  | 9.0333 | 2.6333 | 0 |  |  | 0 |  |  |  | Line tripped at Aurangabad (Waluj) only, due to Bus tripped end Aurangabad (Waluj-MSETCL). Line charged from Pune-GIS end.
|  | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II Total | [10 empty] | 9.0333 | [10 empty] | 98.79%
109 | WR1_L_109 | 400kV RAIPUR-RAIGARH II | 217.02 | WRTS-I |  | 2019-03-18 | 8:44 | 2019-03-18 | 20:18 |  |  |  | 0 | 11.5667 | 0 | 0 | Line outage availed for replacement of conventional insulators by polymer insulators in polluted sections / major crossing of line. Ckt-1 has been put in Non-auto mode for safety reason. | OMSU |  |  |  | Line outage availed for replacement of conventional insulators by polymer insulators in polluted sections / major crossing of line. Ckt-1 has been put in Non-auto mode for safety reason.
|  | 400kV RAIPUR-RAIGARH II Total | [10 empty] | 0 | [10 empty] | 100%
110 | WR1_L_110 | 400kV LARA(NTPC)-KOTRA PS I | 17.999 | WRTS-I | [18 empty] | WRLDC
|  | 400kV LARA(NTPC)-KOTRA PS I Total | [21 empty] | 100%
111 | WR1_L_111 | 400kV LARA(NTPC)-KOTRA PS II | 17.999 | WRTS-I | [18 empty] | WRLDC
|  | 400kV LARA(NTPC)-KOTRA PS II Total | [21 empty] | 100%
112 | WR1_L_112 | 400kV KORBA-BIRSINGHPUR_2 | 226.642 | WRTS-I |  | 2019-03-12 | 7:44 | 2019-03-12 | 18:39 |  |  |  | 10.9167 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-12 | 18:39 | 2019-03-12 | 20:38 |  |  |  | 0 | 1.9833 | 0 | 0 | Line was ready for charging at 1839 Hrs(Readiness mail attached) for line charging. But line charging delayed ny NTPC Korba and Birsinghpur. Also in Morning hours NBFC was issued after a delay of 0130 Hrs. | OMSU
[6 empty] | 2019-03-13 | 7:45 | 2019-03-13 | 19:36 |  |  |  | 11.85 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-14 | 7:48 | 2019-03-14 | 20:02 |  |  |  | 12.2333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-15 | 7:53 | 2019-03-15 | 18:10 |  |  |  | 10.2833 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-16 | 8:14 | 2019-03-16 | 12:35 |  |  |  | 4.35 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-12 | 18:39 | 2019-03-12 | 20:38 |  |  |  | 49.6333 | 1.9833 | 0 | 0 | Line was ready for charging at 1839 Hrs(Readiness mail attached) for line charging. But line charging delayed ny NTPC Korba and Birsinghpur. Also in Morning hours NBFC was issued after a delay of 0130 Hrs. | OMSU
[6 empty] | 2019-03-13 | 7:45 | 2019-03-13 | 19:36 |  |  |  | 11.85 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-14 | 7:48 | 2019-03-14 | 20:02 |  |  |  | 12.2333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-15 | 7:53 | 2019-03-15 | 18:10 |  |  |  | 10.2833 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-16 | 8:14 | 2019-03-16 | 12:35 |  |  |  | 4.35 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-12 | 18:39 | 2019-03-12 | 20:38 |  |  |  | 88.35 | 1.9833 | 0 | 0 | Line was ready for charging at 1839 Hrs(Readiness mail attached) for line charging. But line charging delayed ny NTPC Korba and Birsinghpur. Also in Morning hours NBFC was issued after a delay of 0130 Hrs. | OMSU
[6 empty] | 2019-03-13 | 7:45 | 2019-03-13 | 19:36 |  |  |  | 11.85 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-14 | 7:48 | 2019-03-14 | 20:02 |  |  |  | 12.2333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-15 | 7:53 | 2019-03-15 | 18:10 |  |  |  | 10.2833 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-16 | 8:14 | 2019-03-16 | 12:35 |  |  |  | 4.35 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-12 | 18:39 | 2019-03-12 | 20:38 |  |  |  | 127.0667 | 1.9833 | 0 |  |  | 0 |  |  |  | Line was ready for charging at 1839 Hrs(Readiness mail attached) for line charging. But line charging delayed ny NTPC Korba and Birsinghpur. Also in Morning hours NBFC was issued after a delay of 0130 Hrs.
[6 empty] | 2019-03-13 | 7:45 | 2019-03-13 | 19:36 |  |  |  | 11.85 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-14 | 7:48 | 2019-03-14 | 20:02 |  |  |  | 12.2333 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-15 | 7:53 | 2019-03-15 | 18:10 |  |  |  | 10.2833 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-16 | 8:14 | 2019-03-16 | 12:35 |  |  |  | 4.35 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
|  | 400kV KORBA-BIRSINGHPUR_2 Total | [10 empty] | 165.7833 | [10 empty] | 77.72%
113 | WR1_T_001 | ICT1_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT1_400/220kv_RAIPUR Total | [21 empty] | 100%
114 | WR1_T_002 | ICT2_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT2_400/220kv_RAIPUR Total | [21 empty] | 100%
115 | WR1_T_003 | ICT1_400/220kv_MAPUSA | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT1_400/220kv_MAPUSA Total | [21 empty] | 100%
116 | WR1_T_004 | ICT2_400/220kv_MAPUSA | 315 | WRTS-I
|  | ICT2_400/220kv_MAPUSA Total | [21 empty] | 100%
117 | WR1_T_005 | ICT1_400/220kv_BAHATAPARA | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT1_400/220kv_BAHATAPARA Total | [21 empty] | 100%
118 | WR1_T_006 | ICT1_400/220kv_RAIGARH | 315 | WRTS-I
|  | ICT1_400/220kv_RAIGARH Total | [21 empty] | 100%
119 | WR1_T_007 | ICT2_400/220kv_RAIGARH | 315 | WRTS-I
|  | ICT2_400/220kv_RAIGARH Total | [21 empty] | 100%
120 | WR1_T_008 | ICT1_765/400kv_SEONI | 1500 | WRTS-I
|  | ICT1_765/400kv_SEONI Total | [21 empty] | 100%
121 | WR1_T_009 | ICT2_765/400kv_SEONI | 1500 | WRTS-I
|  | ICT2_765/400kv_SEONI Total | [21 empty] | 100%
122 | WR1_T_010 | ICT3_765/400kv_SEONI | 1500 | WRTS-I
|  | ICT3_765/400kv_SEONI Total | [21 empty] | 100%
123 | WR1_T_011 | ICT1_400/220kv_SEONI | 315 | WRTS-I
|  | ICT1_400/220kv_SEONI Total | [21 empty] | 100%
124 | WR1_T_012 | ICT1_765/400kv_WARDHA | 1500 | WRTS-I
|  | ICT1_765/400kv_WARDHA Total | [21 empty] | 100%
125 | WR1_T_013 | ICT2_765/400kv_WARDHA | 1500 | WRTS-I
|  | ICT2_765/400kv_WARDHA Total | [21 empty] | 100%
126 | WR1_T_014 | ICT3_765/400kv_WARDHA | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT3_765/400kv_WARDHA Total | [21 empty] | 100%
127 | WR1_T_015 | ICT1_765/400kv_BILASPUR | 1500 | WRTS-I
|  | ICT1_765/400kv_BILASPUR Total | [21 empty] | 100%
128 | WR1_T_016 | ICT2_765/400kv_BILASPUR | 1500 | WRTS-I
|  | ICT2_765/400kv_BILASPUR Total | [21 empty] | 100%
129 | WR1_T_017 | ICT2_400/220kv_BAHATAPARA | 315 | WRTS-I
|  | ICT2_400/220kv_BAHATAPARA Total | [21 empty] | 100%
130 | WR1_T_018 | ICT2_400/220kv_SEONI | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT2_400/220kv_SEONI Total | [21 empty] | 100%
131 | WR1_T_019 | ICT3_400/220kv_RAIPUR | 315 | WRTS-I
|  | ICT3_400/220kv_RAIPUR Total | [21 empty] | 100%
132 | WR1_T_020 | ICT1_400/220kv_WARDHA | 315 | WRTS-I
|  | ICT1_400/220kv_WARDHA Total | [21 empty] | 100%
133 | WR1_T_021 | ICT2_400/220kv_WARDHA | 315 | WRTS-I
|  | ICT2_400/220kv_WARDHA Total | [21 empty] | 100%
134 | WR1_T_022 | ICT3_400/220kv_SOLAPUR | 500 | WRTS-I
|  | ICT3_400/220kv_SOLAPUR Total | [21 empty] | 100%
135 | WR1_T_023 | ICT1_400/220kv_SOLAPUR | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT1_400/220kv_SOLAPUR Total | [21 empty] | 100%
136 | WR1_T_024 | ICT2_400/220kv_SOLAPUR | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT2_400/220kv_SOLAPUR Total | [21 empty] | 100%
137 | WR1_T_025 | ICT1_400/220kv_PUNE | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT1_400/220kv_PUNE Total | [21 empty] | 100%
138 | WR1_T_026 | ICT2_400/220kv_PUNE | 315 | WRTS-I
|  | ICT2_400/220kv_PUNE Total | [21 empty] | 100%
139 | WR1_T_027 | ICT3_400/220kv_PUNE | 315 | WRTS-I
|  | ICT3_400/220kv_PUNE Total | [21 empty] | 100%
140 | WR1_T_028 | ICT3_765/400kv_BILASPUR | 1500 | WRTS-I
|  | ICT3_765/400kv_BILASPUR Total | [21 empty] | 100%
141 | WR1_T_029 | ICT1_765/400kv_KOTRA PS | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT1_765/400kv_KOTRA PS Total | [21 empty] | 100%
142 | WR1_T_030 | ICT2_765/400kv_KOTRA PS | 1500 | WRTS-I
|  | ICT2_765/400kv_KOTRA PS Total | [21 empty] | 100%
143 | WR1_T_031 | ICT4_765/400kv_KOTRA PS | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT4_765/400kv_KOTRA PS Total | [21 empty] | 100%
144 | WR1_T_032 | ICT3_400/220kv_MAPUSA | 315 | WRTS-I
|  | ICT3_400/220kv_MAPUSA Total | [21 empty] | 100%
145 | WR1_T_033 | ICT1_765/400kv_TAMNAR PS | 1500 | WRTS-I
|  | ICT1_765/400kv_TAMNAR PS Total | [21 empty] | 100%
146 | WR1_T_034 | ICT2_765/400kv_TAMNAR PS | 1500 | WRTS-I
|  | ICT2_765/400kv_TAMNAR PS Total | [21 empty] | 100%
147 | WR1_T_035 | ICT1_765/400kv_DURG PS | 1500 | WRTS-I
|  | ICT1_765/400kv_DURG PS Total | [21 empty] | 100%
148 | WR1_T_036 | ICT1_765/400kv_SOLAPUR | 1500 | WRTS-I
|  | ICT1_765/400kv_SOLAPUR Total | [21 empty] | 100%
149 | WR1_T_037 | ICT2_765/400kv_SOLAPUR | 1500 | WRTS-I |  | 2019-03-11 | 10:20 | 2019-03-11 | 20:42 |  |  |  | 10.3667 | 0 | 0 | 0 | For AMP Works. | OSPT |  |  |  | For AMP Works.
|  | ICT2_765/400kv_SOLAPUR Total | [10 empty] | 10.3667 | [10 empty] | 98.61%
150 | WR1_T_038 | ICT1_400/200kv_AURANGABAD | 315 | WRTS-I
|  | ICT1_400/200kv_AURANGABAD Total | [21 empty] | 100%
151 | WR1_T_039 | ICT2_400/200kv_AURANGABAD | 315 | WRTS-I
|  | ICT2_400/200kv_AURANGABAD Total | [21 empty] | 100%
152 | WR1_T_040 | ICT2_765/400kv_AURANGABAD | 1500 | WRTS-I
|  | ICT2_765/400kv_AURANGABAD Total | [21 empty] | 100%
153 | WR1_T_041 | ICT3_765/400kv_TAMNAR PS | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT3_765/400kv_TAMNAR PS Total | [21 empty] | 100%
154 | WR1_T_042 | ICT3_765/400kv_KOTRA PS | 1500 | WRTS-I
|  | ICT3_765/400kv_KOTRA PS Total | [21 empty] | 100%
155 | WR1_T_043 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I
|  | ICT1_765/400kv_AURANGABAD Total | [21 empty] | 100%
156 | WR1_T_044 | ICT2_765/400kv_D'JAIGARH | 1500 | WRTS-I
|  | ICT2_765/400kv_D'JAIGARH Total | [21 empty] | 100%
157 | WR1_T_045 | ICT1_765/400kv_D'JAIGARH | 1500 | WRTS-I
|  | ICT1_765/400kv_D'JAIGARH Total | [21 empty] | 100%
158 | WR1_T_046 | ICT1_400/200kv_BHADRAWATI | 315 | WRTS-I | [18 empty] | WRLDC
|  | ICT1_400/200kv_BHADRAWATI Total | [21 empty] | 100%
159 | WR1_T_047 | ICT1_765/400kv_PUNE(GIS) | 1500 | WRTS-I
|  | ICT1_765/400kv_PUNE(GIS) Total | [21 empty] | 100%
160 | WR1_T_048 | ICT2_765/400kv_PUNE(GIS) | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT2_765/400kv_PUNE(GIS) Total | [21 empty] | 100%
161 | WR1_T_049 | ICT1_765/400kv_CHAMPA | 1500 | WRTS-I
|  | ICT1_765/400kv_CHAMPA Total | [21 empty] | 100%
162 | WR1_T_050 | ICT2_765/400kv_CHAMPA | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT2_765/400kv_CHAMPA Total | [21 empty] | 100%
163 | WR1_R_001 | BUS REACTOR_400kV_63MVAR_RAIGARH | 63 | WRTS-I | [18 empty] | WRLDC
|  | BUS REACTOR_400kV_63MVAR_RAIGARH Total | [21 empty] | 100%
164 | WR1_R_002 | BUS REACTOR_765kV_240MVAR_SEONI | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_SEONI Total | [21 empty] | 100%
165 | WR1_R_003 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 50 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_400kV_KORBA 3_RAIPUR Total | [21 empty] | 100%
166 | WR1_R_004 | BUS REACTOR_400kV_50MVAR_WARDHA | 50 | WRTS-I
|  | BUS REACTOR_400kV_50MVAR_WARDHA Total | [21 empty] | 100%
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I
|  | BUS REACTOR_400kV_63MVAR_SOLAPUR Total | [21 empty] | 100%
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I
BUS REACTOR_400kV_63MVAR_PARLI Total
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I |  | 2019-03-11 | 11:05 | 2019-03-11 | 15:44 |  |  |  | 0 | 0 | 0 | 4.65 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-12 | 10:54 | 2019-03-12 | 16:44 |  |  |  | 0 | 0 | 0 | 5.8333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:37 | 2019-03-19 | 17:57 |  |  |  | 0 | 0 | 0 | 7.3333 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-29 | 11:11 | 2019-03-29 | 19:57 |  |  |  | 0 | 0 | 0 | 8.7667 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-12 | 10:54 | 2019-03-12 | 16:44 |  |  |  | 0 | 0 | 0 | 5.8333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:37 | 2019-03-19 | 17:57 |  |  |  | 0 | 0 | 0 | 7.3333 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-29 | 11:11 | 2019-03-29 | 19:57 |  |  |  | 0 | 0 | 0 | 8.7667 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-12 | 10:54 | 2019-03-12 | 16:44 |  |  |  | 0 | 0 | 0 | 5.8333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:37 | 2019-03-19 | 17:57 |  |  |  | 0 | 0 | 0 | 7.3333 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-29 | 11:11 | 2019-03-29 | 19:57 |  |  |  | 0 | 0 | 0 | 8.7667 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-12 | 10:54 | 2019-03-12 | 16:44 |  |  |  | 0 | 0 | 0 |  |  | 5.8333 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-19 | 10:37 | 2019-03-19 | 17:57 |  |  |  | 0 | 0 | 0 |  |  | 7.3333 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-29 | 11:11 | 2019-03-29 | 19:57 |  |  |  | 0 | 0 | 0 |  |  | 8.7667 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation.
|  | BUS REACTOR_400kV_50MVAR_PUNE Total | [10 empty] | 0 | [10 empty] | 100%
170 | WR1_R_008 | BUS REACTOR_765kV_240MVAR_WARDHA | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_WARDHA Total | [21 empty] | 100%
171 | WR1_R_009 | BUS REACTOR_765kV_240MVAR_BILASPUR | 240 | WRTS-I | [18 empty] | WRLDC
|  | BUS REACTOR_765kV_240MVAR_BILASPUR Total | [21 empty] | 100%
172 | WR1_R_010 | SWITCHABLE LR_765kV_BINA_SEONI | 240 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_765kV_BINA_SEONI Total | [21 empty] | 100%
173 | WR1_R_011 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_SEONI 1_BILASPUR Total | [21 empty] | 100%
174 | WR1_R_012 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_SEONI 2_BILASPUR Total | [21 empty] | 100%
175 | WR1_R_013 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 240 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_765kV_D'GARH_BILASPUR Total | [21 empty] | 100%
176 | WR1_R_014 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 240 | WRTS-I |  | 2019-03-01 | 6:40 | 2019-03-01 | 14:54 |  |  |  | 8.2333 | 0 | 0 | 0 | For AMP works. | OSPT |  |  |  | For AMP works.
|  | BUS REACTOR_765kV_240MVAR_KOTRA PS Total | [10 empty] | 8.2333 | [10 empty] | 98.89%
177 | WR1_R_015 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 80 | WRTS-I
|  | BUS REACTOR_400kV_80MVAR_KOTRA PS Total | [21 empty] | 100%
178 | WR1_R_016 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_DURG 1_KOTRA PS Total | [21 empty] | 100%
179 | WR1_R_017 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 50 | WRTS-I | [18 empty] | WRLDC
|  | BUS REACTOR_400kV_50MVAR_BHADRAWATI Total | [21 empty] | 100%
180 | WR1_R_018 | BUS REACTOR_400kV_80MVAR_RAIPUR | 80 | WRTS-I
|  | BUS REACTOR_400kV_80MVAR_RAIPUR Total | [21 empty] | 100%
181 | WR1_R_019 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I |  | 2019-03-28 | 11:15 | 2019-03-28 | 17:47 |  |  |  | 0 | 0 | 0 | 6.5333 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD |  |  |  | B/R H/T as per WRLDC instructions for Voltage Regulation.
|  | BUS REACTOR_400kV_50MVAR_MAPUSA Total | [10 empty] | 0 | [10 empty] | 100%
182 | WR1_R_020 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2019-03-11 | 11:06 | 2019-03-11 | 14:07 |  |  |  | 0 | 0 | 0 | 3.0167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation | WRLDC
[6 empty] | 2019-03-12 | 10:15 | 2019-03-12 | 16:39 |  |  |  | 0 | 0 | 0 | 6.4 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:42 | 2019-03-19 | 18:12 |  |  |  | 0 | 0 | 0 | 7.5 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-20 | 10:33 | 2019-03-20 | 17:40 |  |  |  | 0 | 0 | 0 | 7.1167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-27 | 9:26 | 2019-03-27 | 20:55 |  |  |  | 0 | 0 | 0 | 11.4833 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-28 | 9:11 | 2019-03-28 | 17:45 |  |  |  | 0 | 0 | 0 | 8.5667 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-29 | 10:59 | 2019-03-29 | 17:42 |  |  |  | 0 | 0 | 0 | 6.7167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-12 | 10:15 | 2019-03-12 | 16:39 |  |  |  | 0 | 0 | 0 | 6.4 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:42 | 2019-03-19 | 18:12 |  |  |  | 0 | 0 | 0 | 7.5 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-20 | 10:33 | 2019-03-20 | 17:40 |  |  |  | 0 | 0 | 0 | 7.1167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-27 | 9:26 | 2019-03-27 | 20:55 |  |  |  | 0 | 0 | 0 | 11.4833 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-28 | 9:11 | 2019-03-28 | 17:45 |  |  |  | 0 | 0 | 0 | 8.5667 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-29 | 10:59 | 2019-03-29 | 17:42 |  |  |  | 0 | 0 | 0 | 6.7167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-12 | 10:15 | 2019-03-12 | 16:39 |  |  |  | 0 | 0 | 0 | 6.4 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:42 | 2019-03-19 | 18:12 |  |  |  | 0 | 0 | 0 | 7.5 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-20 | 10:33 | 2019-03-20 | 17:40 |  |  |  | 0 | 0 | 0 | 7.1167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-27 | 9:26 | 2019-03-27 | 20:55 |  |  |  | 0 | 0 | 0 | 11.4833 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-28 | 9:11 | 2019-03-28 | 17:45 |  |  |  | 0 | 0 | 0 | 8.5667 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-29 | 10:59 | 2019-03-29 | 17:42 |  |  |  | 0 | 0 | 0 | 6.7167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-12 | 10:15 | 2019-03-12 | 16:39 |  |  |  | 0 | 0 | 0 |  |  | 6.4 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-19 | 10:42 | 2019-03-19 | 18:12 |  |  |  | 0 | 0 | 0 |  |  | 7.5 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-20 | 10:33 | 2019-03-20 | 17:40 |  |  |  | 0 | 0 | 0 |  |  | 7.1167 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-27 | 9:26 | 2019-03-27 | 20:55 |  |  |  | 0 | 0 | 0 |  |  | 11.4833 |  |  |  | H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-28 | 9:11 | 2019-03-28 | 17:45 |  |  |  | 0 | 0 | 0 |  |  | 8.5667 |  |  |  | B/R H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-29 | 10:59 | 2019-03-29 | 17:42 |  |  |  | 0 | 0 | 0 |  |  | 6.7167 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation.
|  | BUS REACTOR_400kV_80MVAR_KOLHAPUR Total | [10 empty] | 0 | [10 empty] | 100%
183 | WR1_R_021 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_DURG 2_KOTRA PS Total | [21 empty] | 100%
184 | WR1_R_022 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 240 | WRTS-I | [18 empty] | WRLDC
|  | BUS REACTOR_765kV_240MVAR_TAMNAR PS Total | [21 empty] | 100%
185 | WR1_R_023 | BUS REACTOR_765kV_240MVAR_DURG PS | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_DURG PS Total | [21 empty] | 100%
186 | WR1_R_024 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I |  | 2019-03-01 | 9:50 | 2019-03-01 | 19:21 |  |  |  | 9.5167 | 0 | 0 | 0 | For AMP works. | OSPT |  |  |  | For AMP works.
|  | BUS REACTOR_765kV_240MVAR_SOLAPUR Total | [10 empty] | 9.5167 | [10 empty] | 98.72%
187 | WR1_R_027 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 1_WARDHA Total | [21 empty] | 100%
188 | WR1_R_028 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 2_WARDHA Total | [21 empty] | 100%
190 | WR1_R_029 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 240 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR Total | [21 empty] | 100%
191 | WR1_R_030 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 2_SEONI Total | [21 empty] | 100%
192 | WR1_R_031 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I
|  | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH Total | [21 empty] | 100%
193 | WR1_R_032 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I
|  | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH Total | [21 empty] | 100%
194 | WR1_R_033 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_AURANGABAD Total | [21 empty] | 100%
195 | WR1_R_034 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_AURANGABAD Total | [21 empty] | 100%
196 | WR1_R_035 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 240 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS Total | [21 empty] | 100%
197 | WR1_R_036 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_BHATAPARA Total | [21 empty] | 100%
198 | WR1_R_037 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 1_SEONI Total | [21 empty] | 100%
199 | WR1_R_038 | BUS REACTOR_400kV_125MVAR_RAIGARH | 125 | WRTS-I | [18 empty] | WRLDC
|  | BUS REACTOR_400kV_125MVAR_RAIGARH Total | [21 empty] | 100%
200 | WR1_R_039 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD Total | [21 empty] | 100%
201 | WR1_R_040 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD Total | [21 empty] | 100%
202 | WR1_R_041 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 240 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_765kV_WARDHA 1_DURG PS Total | [21 empty] | 100%
203 | WR1_R_042 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 2_DURG PS Total | [21 empty] | 100%
204 | WR1_R_043 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 80 | WRTS-I
|  | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD Total | [21 empty] | 100%
205 | WR1_R_044 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 80 | WRTS-I
|  | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD Total | [21 empty] | 100%
206 | WR1_R_045 | BUS REACTOR_400kV_125MVAR_RAIPUR | 125 | WRTS-I | [18 empty] | WRLDC
|  | BUS REACTOR_400kV_125MVAR_RAIPUR Total | [21 empty] | 100%
207 | WR1_R_046 | BUS REACTOR_765kV_330MVAR_WARDHA | 330 | WRTS-I |  | 2019-03-30 | 11:58 | 2019-03-30 | 16:07 |  |  |  | 0 | 0 | 0 | 4.15 | For new Spare reactor commissioning | SCSD |  |  |  | For new Spare reactor commissioning | WRLDC
|  | BUS REACTOR_765kV_330MVAR_WARDHA Total | [10 empty] | 0 | [10 empty] | 100%
208 | WR1_R_047 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 80 | WRTS-I
|  | SWITCHABLE LR_400kV_KARAD_SOLAPUR Total | [21 empty] | 100%
209 | WR1_R_048 | BUS REACTOR_400kV_125MVAR_SEONI | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_SEONI Total | [21 empty] | 100%
210 | WR1_R_049 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE Total | [21 empty] | 100%
211 | WR1_R_050 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE Total | [21 empty] | 100%
212 | WR1_R_051 | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE Total | [21 empty] | 100%
213 | WR1_R_052 | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE | 50 | WRTS-I
|  | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE Total | [21 empty] | 100%
214 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I
|  | BUS REACTOR_400kV_125MVAR_PARLI Total | [21 empty] | 100%
215 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2019-03-04 | 10:39 | 2019-03-04 | 16:11 |  |  |  | 0 | 0 | 0 | 5.5333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation | WRLDC
[6 empty] | 2019-03-05 | 11:37 | 2019-03-06 | 0:52 |  |  |  | 0 | 0 | 0 | 13.25 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-06 | 11:05 | 2019-03-06 | 22:00 |  |  |  | 0 | 0 | 0 | 10.9167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-08 | 11:22 | 2019-03-08 | 18:23 |  |  |  | 0 | 0 | 0 | 7.0167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-09 | 11:12 | 2019-03-09 | 18:49 |  |  |  | 0 | 0 | 0 | 7.6167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-11 | 10:15 | 2019-03-12 | 17:49 |  |  |  | 0 | 0 | 0 | 31.5667 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-15 | 11:18 | 2019-03-15 | 20:29 |  |  |  | 0 | 0 | 0 | 9.1833 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-16 | 9:59 | 2019-03-16 | 18:39 |  |  |  | 0 | 0 | 0 | 8.6667 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:54 | 2019-03-19 | 18:19 |  |  |  | 0 | 0 | 0 | 7.4167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-22 | 8:43 | 2019-03-22 | 18:39 |  |  |  | 0 | 0 | 0 | 9.9333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-27 | 9:35 | 2019-03-27 | 21:03 |  |  |  | 0 | 0 | 0 | 11.4667 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-28 | 10:35 | 2019-03-28 | 18:11 |  |  |  | 0 | 0 | 0 | 7.6 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-05 | 11:37 | 2019-03-06 | 0:52 |  |  |  | 0 | 0 | 0 | 13.25 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-06 | 11:05 | 2019-03-06 | 22:00 |  |  |  | 0 | 0 | 0 | 10.9167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-08 | 11:22 | 2019-03-08 | 18:23 |  |  |  | 0 | 0 | 0 | 7.0167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-09 | 11:12 | 2019-03-09 | 18:49 |  |  |  | 0 | 0 | 0 | 7.6167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-11 | 10:15 | 2019-03-12 | 17:49 |  |  |  | 0 | 0 | 0 | 31.5667 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-15 | 11:18 | 2019-03-15 | 20:29 |  |  |  | 0 | 0 | 0 | 9.1833 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-16 | 9:59 | 2019-03-16 | 18:39 |  |  |  | 0 | 0 | 0 | 8.6667 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:54 | 2019-03-19 | 18:19 |  |  |  | 0 | 0 | 0 | 7.4167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-22 | 8:43 | 2019-03-22 | 18:39 |  |  |  | 0 | 0 | 0 | 9.9333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-27 | 9:35 | 2019-03-27 | 21:03 |  |  |  | 0 | 0 | 0 | 11.4667 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-28 | 10:35 | 2019-03-28 | 18:11 |  |  |  | 0 | 0 | 0 | 7.6 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-05 | 11:37 | 2019-03-06 | 0:52 |  |  |  | 0 | 0 | 0 | 13.25 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-06 | 11:05 | 2019-03-06 | 22:00 |  |  |  | 0 | 0 | 0 | 10.9167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-08 | 11:22 | 2019-03-08 | 18:23 |  |  |  | 0 | 0 | 0 | 7.0167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-09 | 11:12 | 2019-03-09 | 18:49 |  |  |  | 0 | 0 | 0 | 7.6167 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-11 | 10:15 | 2019-03-12 | 17:49 |  |  |  | 0 | 0 | 0 | 31.5667 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-15 | 11:18 | 2019-03-15 | 20:29 |  |  |  | 0 | 0 | 0 | 9.1833 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-16 | 9:59 | 2019-03-16 | 18:39 |  |  |  | 0 | 0 | 0 | 8.6667 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 10:54 | 2019-03-19 | 18:19 |  |  |  | 0 | 0 | 0 | 7.4167 | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-22 | 8:43 | 2019-03-22 | 18:39 |  |  |  | 0 | 0 | 0 | 9.9333 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-27 | 9:35 | 2019-03-27 | 21:03 |  |  |  | 0 | 0 | 0 | 11.4667 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-28 | 10:35 | 2019-03-28 | 18:11 |  |  |  | 0 | 0 | 0 | 7.6 | B/R H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-05 | 11:37 | 2019-03-06 | 0:52 |  |  |  | 0 | 0 | 0 |  |  | 13.25 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-06 | 11:05 | 2019-03-06 | 22:00 |  |  |  | 0 | 0 | 0 |  |  | 10.9167 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-08 | 11:22 | 2019-03-08 | 18:23 |  |  |  | 0 | 0 | 0 |  |  | 7.0167 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-09 | 11:12 | 2019-03-09 | 18:49 |  |  |  | 0 | 0 | 0 |  |  | 7.6167 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-11 | 10:15 | 2019-03-12 | 17:49 |  |  |  | 0 | 0 | 0 |  |  | 31.5667 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-15 | 11:18 | 2019-03-15 | 20:29 |  |  |  | 0 | 0 | 0 |  |  | 9.1833 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-16 | 9:59 | 2019-03-16 | 18:39 |  |  |  | 0 | 0 | 0 |  |  | 8.6667 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-19 | 10:54 | 2019-03-19 | 18:19 |  |  |  | 0 | 0 | 0 |  |  | 7.4167 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-22 | 8:43 | 2019-03-22 | 18:39 |  |  |  | 0 | 0 | 0 |  |  | 9.9333 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-27 | 9:35 | 2019-03-27 | 21:03 |  |  |  | 0 | 0 | 0 |  |  | 11.4667 |  |  |  | H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-28 | 10:35 | 2019-03-28 | 18:11 |  |  |  | 0 | 0 | 0 |  |  | 7.6 |  |  |  | B/R H/T as per WRLDC instructions for Voltage Regulation.
|  | BUS REACTOR_765kV_240MVAR_PUNE(GIS) Total | [10 empty] | 0 | [10 empty] | 100%
216 | WR1_R_055 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 240 | WRTS-I |  | 2019-03-01 | 7:24 | 2019-03-01 | 11:52 |  |  |  | 0 | 0 | 0 | 4.4667 | H/T as per WRLDC instructions for voltage regulation | SVRD |  |  |  | H/T as per WRLDC instructions for voltage regulation
[6 empty] | 2019-03-03 | 9:45 | 2019-03-03 | 18:08 |  |  |  | 0 | 0 | 0 | 8.3833 | H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-04 | 8:48 | 2019-03-04 | 20:56 |  |  |  | 0 | 0 | 0 | 12.1333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-05 | 7:45 | 2019-03-05 | 20:11 |  |  |  | 0 | 0 | 0 | 12.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-06 | 6:15 | 2019-03-06 | 20:56 |  |  |  | 0 | 0 | 0 | 14.6833 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-07 | 5:55 | 2019-03-11 | 15:21 |  |  |  | 0 | 0 | 0 | 105.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-13 | 8:25 | 2019-03-14 | 0:14 |  |  |  | 0 | 0 | 0 | 15.8167 | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-14 | 6:40 | 2019-03-14 | 21:55 |  |  |  | 0 | 0 | 0 | 15.25 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-15 | 10:15 | 2019-03-16 | 22:14 |  |  |  | 0 | 0 | 0 | 35.9833 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-17 | 6:45 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 | 23.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 9:55 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 | 20.4 | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-27 | 11:48 | 2019-03-27 | 20:49 |  |  |  | 0 | 0 | 0 | 9.0167 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-03 | 9:45 | 2019-03-03 | 18:08 |  |  |  | 0 | 0 | 0 | 8.3833 | H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-04 | 8:48 | 2019-03-04 | 20:56 |  |  |  | 0 | 0 | 0 | 12.1333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-05 | 7:45 | 2019-03-05 | 20:11 |  |  |  | 0 | 0 | 0 | 12.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-06 | 6:15 | 2019-03-06 | 20:56 |  |  |  | 0 | 0 | 0 | 14.6833 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-07 | 5:55 | 2019-03-11 | 15:21 |  |  |  | 0 | 0 | 0 | 105.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-13 | 8:25 | 2019-03-14 | 0:14 |  |  |  | 0 | 0 | 0 | 15.8167 | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-14 | 6:40 | 2019-03-14 | 21:55 |  |  |  | 0 | 0 | 0 | 15.25 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-15 | 10:15 | 2019-03-16 | 22:14 |  |  |  | 0 | 0 | 0 | 35.9833 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-17 | 6:45 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 | 23.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 9:55 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 | 20.4 | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-27 | 11:48 | 2019-03-27 | 20:49 |  |  |  | 0 | 0 | 0 | 9.0167 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-03 | 9:45 | 2019-03-03 | 18:08 |  |  |  | 0 | 0 | 0 | 8.3833 | H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-04 | 8:48 | 2019-03-04 | 20:56 |  |  |  | 0 | 0 | 0 | 12.1333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-05 | 7:45 | 2019-03-05 | 20:11 |  |  |  | 0 | 0 | 0 | 12.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-06 | 6:15 | 2019-03-06 | 20:56 |  |  |  | 0 | 0 | 0 | 14.6833 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-07 | 5:55 | 2019-03-11 | 15:21 |  |  |  | 0 | 0 | 0 | 105.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-13 | 8:25 | 2019-03-14 | 0:14 |  |  |  | 0 | 0 | 0 | 15.8167 | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-14 | 6:40 | 2019-03-14 | 21:55 |  |  |  | 0 | 0 | 0 | 15.25 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-15 | 10:15 | 2019-03-16 | 22:14 |  |  |  | 0 | 0 | 0 | 35.9833 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-17 | 6:45 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 | 23.4333 | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD
[6 empty] | 2019-03-19 | 9:55 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 | 20.4 | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-27 | 11:48 | 2019-03-27 | 20:49 |  |  |  | 0 | 0 | 0 | 9.0167 | H/T as per WRLDC instructions for Voltage Regulation. | SVRD
[6 empty] | 2019-03-03 | 9:45 | 2019-03-03 | 18:08 |  |  |  | 0 | 0 | 0 |  |  | 8.3833 |  |  |  | H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-04 | 8:48 | 2019-03-04 | 20:56 |  |  |  | 0 | 0 | 0 |  |  | 12.1333 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-05 | 7:45 | 2019-03-05 | 20:11 |  |  |  | 0 | 0 | 0 |  |  | 12.4333 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-06 | 6:15 | 2019-03-06 | 20:56 |  |  |  | 0 | 0 | 0 |  |  | 14.6833 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-07 | 5:55 | 2019-03-11 | 15:21 |  |  |  | 0 | 0 | 0 |  |  | 105.4333 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-13 | 8:25 | 2019-03-14 | 0:14 |  |  |  | 0 | 0 | 0 |  |  | 15.8167 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-14 | 6:40 | 2019-03-14 | 21:55 |  |  |  | 0 | 0 | 0 |  |  | 15.25 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-15 | 10:15 | 2019-03-16 | 22:14 |  |  |  | 0 | 0 | 0 |  |  | 35.9833 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-17 | 6:45 | 2019-03-18 | 6:11 |  |  |  | 0 | 0 | 0 |  |  | 23.4333 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation
[6 empty] | 2019-03-19 | 9:55 | 2019-03-20 | 6:19 |  |  |  | 0 | 0 | 0 |  |  | 20.4 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation.
[6 empty] | 2019-03-27 | 11:48 | 2019-03-27 | 20:49 |  |  |  | 0 | 0 | 0 |  |  | 9.0167 |  |  |  | H/T as per WRLDC instructions for Voltage Regulation.
|  | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) Total | [10 empty] | 0 | [10 empty] | 100%
217 | WR1_R_056 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I
|  | BUS REACTOR_400kV_80MVAR_DHULE Total | [21 empty] | 100%
218 | WR1_R_057 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 3_WARDHA Total | [21 empty] | 100%
219 | WR1_R_058 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_A'BAD 4_WARDHA Total | [21 empty] | 100%
220 | WR1_R_059 | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH Total | [21 empty] | 100%
221 | WR1_R_060 | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH Total | [21 empty] | 100%
222 | WR1_R_061 | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR | 240 | WRTS-I | [18 empty] | WRLDC
|  | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR Total | [21 empty] | 100%
223 | WR1_R_062 | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR Total | [21 empty] | 100%
224 | WR1_R_063 | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH Total | [21 empty] | 100%
225 | WR1_R_064 | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH Total | [21 empty] | 100%
226 | WR1_R_065 | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) | 125 | WRTS-I |  | 2019-03-12 | 11:00 | 2019-03-12 | 16:51 |  |  |  | 0 | 0 | 0 | 5.85 | BR H/T as per WRLDC instructions for Voltage Regulation | SVRD |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation
|  | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) Total | [10 empty] | 0 | [10 empty] | 100%
227 | WR1_R_066 | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD | 80 | WRTS-I
|  | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD Total | [21 empty] | 100%
228 | WR1_R_067 | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD | 80 | WRTS-I
|  | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD Total | [21 empty] | 100%
229 | WR1_R_068 | BUS REACTOR_765kV_240MVAR_CHAMPA | 240 | WRTS-I
|  | BUS REACTOR_765kV_240MVAR_CHAMPA Total | [21 empty] | 100%
230 | WR1_R_069 | BUS REACTOR_400kV_80MVAR_CHAMPA | 80 | WRTS-I
|  | BUS REACTOR_400kV_80MVAR_CHAMPA Total | [21 empty] | 100%
231 | WR1_R_070 | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH Total | [21 empty] | 100%
232 | WR1_R_071 | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH Total | [21 empty] | 100%
233 | WR1_P_001 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I
|  | HVDC_POLE1_BHADRAWATI Total | [21 empty] | 100%
234 | WR1_P_002 | HVDC_POLE2_BHADRAWATI | 500 | WRTS-I
|  | HVDC_POLE2_BHADRAWATI Total | [21 empty] | 100%
235 | WR1_T_051 | ICT4_765/400kv_CHAMPA | 1500 | WRTS-I
|  | ICT4_765/400kv_CHAMPA Total | [21 empty] | 100%
236 | WR1_T_052 | ICT5_765/400kv_CHAMPA | 1500 | WRTS-I
|  | ICT5_765/400kv_CHAMPA Total | [21 empty] | 100%
237 | WR1_L_113 | 400kV RAIGARH-JHARSUGUDA I | 110.98 | WRTS-I |  | 2019-03-09 | 11:19 | 2019-03-09 | 23:45 |  |  |  | 0 | 0 | 0 | 12.4333 | For OPGC Line diversion (Rectification work at Railway crossing) Availed by ER-2 | LCSD |  |  |  | For OPGC Line diversion (Rectification work at Railway crossing) Availed by ER-2
|  | 400kV RAIGARH-JHARSUGUDA I Total | [10 empty] | 0 | [10 empty] | 100%
238 | WR1_L_114 | 400kV RAIPUR-RAIGARH III | 217.02 | WRTS-I |  | 2019-03-17 | 8:31 | 2019-03-17 | 20:10 |  |  |  | 0 | 11.65 | 0 | 0 | Line outage availed for replacement of conventional insulators by polymer insulators in polluted sections / major crossing of line. Ckt-4 has been put in Non-auto mode for safety reason. | OMSU |  |  |  | Line outage availed for replacement of conventional insulators by polymer insulators in polluted sections / major crossing of line. Ckt-4 has been put in Non-auto mode for safety reason.
|  | 400kV RAIPUR-RAIGARH III Total | [10 empty] | 0 | [10 empty] | 100%
239 | WR1_L_115 | 765kV DURG PS- CHAMPA_2 | 149.15 | WRTS-I
|  | 765kV DURG PS- CHAMPA_2 Total | [21 empty] | 100%
240 | WR1_L_116 | 765kV DURG PS -WARDHA_3 | 357.27 | WRTS-I |  | 2019-03-28 | 20:41 | 2019-03-31 | 24:00 |  |  |  | 0 | 0 | 0 | 75.3167 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg PS end | LVRD |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg PS end | WRLDC
|  | 765kV DURG PS -WARDHA_3 Total | [10 empty] | 0 | [10 empty] | 100%
241 | WR1_L_117 | 765kV DURG PS -WARDHA_4 | 357.27 | WRTS-I |  | 2019-03-14 | 21:53 | 2019-03-22 | 5:53 |  |  |  | 0 | 0 | 0 | 176 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg end . | LVRD |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Durg end . | WRLDC
|  | 765kV DURG PS -WARDHA_4 Total | [10 empty] | 0 | [10 empty] | 100%
242 | WR1_T_052 | ICT6_765/400kv_CHAMPA | 1500 | WRTS-I
|  | ICT6_765/400kv_CHAMPA Total | [21 empty] | 100%
243 | WR1_T_118 | 765KV D'JAIGARH- CHAMPA | 56.48 | WRTS-I
765KV D'JAIGARH- CHAMPA TOTAL
244 | WR1_T_053 | ICT3_765/400kv_CHAMPA | 1500 | WRTS-I
|  | ICT3_765/400kv_CHAMPA Total | [21 empty] | 100%
245 | WR1_L_118 | 400kV KORBA-BIRSINGHPUR_1 | 226.642 | WRTS-I |  | 2019-03-07 | 8:48 | 2019-03-07 | 19:30 |  |  |  | 10.7 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT |  |  |  | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-08 | 9:05 | 2019-03-08 | 19:29 |  |  |  | 10.4 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-09 | 8:57 | 2019-03-09 | 19:12 |  |  |  | 10.25 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-10 | 12:40 | 2019-03-10 | 19:43 |  |  |  | 7.05 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-11 | 8:35 | 2019-03-11 | 19:37 |  |  |  | 11.0333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-16 | 13:26 | 2019-03-16 | 19:28 |  |  |  | 6.0333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-08 | 9:05 | 2019-03-08 | 19:29 |  |  |  | 55.4667 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-09 | 8:57 | 2019-03-09 | 19:12 |  |  |  | 10.25 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-10 | 12:40 | 2019-03-10 | 19:43 |  |  |  | 7.05 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-11 | 8:35 | 2019-03-11 | 19:37 |  |  |  | 11.0333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-16 | 13:26 | 2019-03-16 | 19:28 |  |  |  | 6.0333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-08 | 9:05 | 2019-03-08 | 19:29 |  |  |  | 89.8333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-09 | 8:57 | 2019-03-09 | 19:12 |  |  |  | 10.25 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-10 | 12:40 | 2019-03-10 | 19:43 |  |  |  | 7.05 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-11 | 8:35 | 2019-03-11 | 19:37 |  |  |  | 11.0333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-16 | 13:26 | 2019-03-16 | 19:28 |  |  |  | 6.0333 | 0 | 0 | 0 | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator. | OSPT
[6 empty] | 2019-03-08 | 9:05 | 2019-03-08 | 19:29 |  |  |  | 124.2 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-09 | 8:57 | 2019-03-09 | 19:12 |  |  |  | 10.25 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN S/S string due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-10 | 12:40 | 2019-03-10 | 19:43 |  |  |  | 7.05 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-11 | 8:35 | 2019-03-11 | 19:37 |  |  |  | 11.0333 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
[6 empty] | 2019-03-16 | 13:26 | 2019-03-16 | 19:28 |  |  |  | 6.0333 | 0 | 0 |  |  | 0 |  |  |  | For installation of CLR Polymer insulators of 120 KN strings, due to failure of BHEL make Batch 2008 insulator.
|  | 400kV KORBA-BIRSINGHPUR_2 Total | [10 empty] | 158.5667 | [10 empty] | 78.69%
246 | WR1_T_053 | ICT2_765/400kv_DURG PS | 1500 | WRTS-I
|  | ICT2_765/400kv_DURG PS Total | [21 empty] | 100%
247 | WR1_T_054 | ICT4_765/400kv_TAMNAR PS | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT4_765/400kv_TAMNAR PS Total | [21 empty] | 100%
248 | WR1_R_072 | SWITCHABLE LR_765kV_WARDHA 4_DURG PS | 240 | WRTS-I
|  | SWITCHABLE LR_765kV_WARDHA 4_DURG PS Total | [21 empty] | 100%
249 | WR1_L_118 | 400kV LARA(NTPC)-CHAMPA I | 113.527 | WRTS-I | [18 empty] | WRLDC
|  | 400kV LARA(NTPC)-CHAMPA I Total | [21 empty] | 100%
250 | WR1_L_119 | 400kV LARA(NTPC)-CHAMPA II | 113.527 | WRTS-I | [18 empty] | WRLDC
|  | 400kV LARA(NTPC)-CHAMPA II Total | [21 empty] | 100%
251 | WR1_L_120 | 400kV RAIPUR-RAIGARH IV | 217.02 | WRTS-I |  | 2019-03-16 | 9:06 | 2019-03-16 | 20:49 |  |  |  | 0 | 11.7167 | 0 | 0 | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. | OMSU |  |  |  | For Replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line.
[6 empty] | 2019-03-26 | 9:29 | 2019-03-26 | 18:42 |  |  |  | 0 | 9.2167 | 0 | 0 | For replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. | OMSU
[6 empty] | 2019-03-26 | 9:29 | 2019-03-26 | 18:42 |  |  |  | 0 | 9.2167 | 0 | 0 | For replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. | OMSU
[6 empty] | 2019-03-26 | 9:29 | 2019-03-26 | 18:42 |  |  |  | 0 | 9.2167 | 0 | 0 | For replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line. | OMSU
[6 empty] | 2019-03-26 | 9:29 | 2019-03-26 | 18:42 |  |  |  | 0 | 9.2167 | 0 |  |  | 0 |  |  |  | For replacement of Conventional Insulators by Polymer Insulators in Polluted Sections / Major Crossing of Line.
|  | 400kV RAIPUR-RAIGARH IV Total | [10 empty] | 0 | [10 empty] | 100%
252 | WR1_L_121 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_3 | 11.2 | WRTS-I |  | 2019-03-09 | 9:21 | 2019-03-09 | 20:40 |  |  |  | 0 | 11.3167 | 0 | 0 | For alignment checking of line side isolators (406R-89L & 407R-89L) of 50 MVA line reactors (Availed by NTPC). Bay belongs to NTPC | OMSU |  |  |  | For alignment checking of line side isolators (406R-89L & 407R-89L) of 50 MVA line reactors (Availed by NTPC). Bay belongs to NTPC
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_3 Total | [10 empty] | 0 | [10 empty] | 100%
253 | WR1_L_122 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_4 | 11.2 | WRTS-I
|  | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_4 Total | [21 empty] | 100%
254 | WR1_L_0123 | 400kV RAIGARH-JHARSUGUDA II | 110.98 | WRTS-I | [18 empty] | WRLDC
|  | 400kV RAIGARH-SUNDERGARH II Total | [21 empty] | 100%
255 | WR1_T_124 | 765kV AURANGABAD(PG)-PADGHE(GIS) I | 284.816 | WRTS-I |  | 2019-03-01 | 0:00 | 2019-03-01 | 11:22 |  |  |  | 0 | 0 | 0 | 11.3667 | WRLDC instructed to keep out the line due to voltage regulation after attending SF6 gas leakage problem at padghe SS end. | LVRD |  |  |  | WRLDC instructed to keep out the line due to voltage regulation after attending SF6 gas leakage problem at padghe SS end. | WRLDC
[6 empty] | 2019-03-21 | 21:28 | 2019-03-30 | 9:55 |  |  |  | 0 | 0 | 0 | 204.45 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Aurangabad end. | LVRD
[6 empty] | 2019-03-21 | 21:28 | 2019-03-30 | 9:55 |  |  |  | 0 | 0 | 0 | 204.45 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Aurangabad end. | LVRD
[6 empty] | 2019-03-21 | 21:28 | 2019-03-30 | 9:55 |  |  |  | 0 | 0 | 0 | 204.45 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Aurangabad end. | LVRD
[6 empty] | 2019-03-21 | 21:28 | 2019-03-30 | 9:55 |  |  |  | 0 | 0 | 0 |  |  | 204.45 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Aurangabad end.
|  | 765kV AURANGABAD(PG)-PADGHE(GIS) I Total | [10 empty] | 0 | [10 empty] | 100%
256 | WR1_T_125 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | 284.816 | WRTS-I |  | 2019-03-01 | 16:39 | 2019-03-11 | 15:47 |  |  |  | 0 | 0 | 0 | 239.1333 | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Aurangabad end. | LVRD |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. LR converted as BR at Aurangabad end. | WRLDC
|  | 765kV AURANGABAD(PG)-PADGHE(GIS) II Total | [10 empty] | 0 | [10 empty] | 100%
257 | WR1_T_055 | ICT2_765/400kv_PADGHE(GIS) | 1500 | WRTS-I | [18 empty] | WRLDC
|  | ICT2_765/400kv_PADGHE(GIS) Total | [21 empty] | 100%
258 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PADGHE(GIS) | 240 | WRTS-I
BUS REACTOR_765kV_240MVAR_PADGHE(GIS) TOTAL
259 | WR1_R_055 | SWITCHABLE LR_400kV_B'WATI 2_RAIPUR | 50 | WRTS-I | [19 empty] | 100%
SWITCHABLE LR_400kV_B'WATI 2_RAIPUR Total
260 | WR1_T_125 | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) I | 16.74 | WRTS-I
|  | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) I TOTAL | [21 empty] | 100%
261 | WR1_T_125 | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) II | 16.74 | WRTS-I | [18 empty] | WRLDC
|  | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) II TOTAL | [21 empty] | 100%
262 | WR1_T_056 | ICT1_765/400kv_PADGHE(GIS) | 1500 | WRTS-I
|  | ICT1_765/400kv_PADGHE(GIS) Total | [21 empty] | 100%
263 |  | 400kV WARDHA-WARORA-I_LILOPOINT_PG | 3.708 | WRTS-I
|  | 400kV WARDHA-WARORA-I_LILOPOINT_PG Total | [21 empty] | 100%
264 |  | 400kV WARDHA-WARORA-2_LILOPOINT_PG | 3.708 | WRTS-I
|  | 400kV WARDHA-WARORA-2_LILOPOINT_PG Total | [21 empty] | 100%
265 |  | 400kV WARORA-PARLI-I_LILOPOINT_PG | 333.231 | WRTS-I
|  | 400kV WARORA-PARLI-I_LILOPOINT_PG Total | [21 empty] | 100%
266 |  | 400kV WARORA-PARLI-2_LILOPOINT_PG | 333.231 | WRTS-I
|  | 400kV WARORA-PARLI-2_LILOPOINT_PG Total | [21 empty] | 100%
267 |  | SWITCHABLE LR_JHARSUGUDA3_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_JHARSUGUDA3_D'JAIGARH Total | [21 empty] | 100%
268 |  | SWITCHABLE LR_JHARSUGUDA4_D'JAIGARH | 330 | WRTS-I
|  | SWITCHABLE LR_JHARSUGUDA4_D'JAIGARH Total | [21 empty] | 100%
269 |  | 765kV D'JAIGARH- JHARSUGUDA III | 149.4 | WRTS-I
|  | 765kV D'JAIGARH- JHARSUGUDA III Total | [21 empty] | 100%
270 |  | 765kV D'JAIGARH- JHARSUGUDA IV | 149.4 | WRTS-I |  | 2019-03-09 | 16:10 | 2019-03-10 | 2:42 |  |  |  | 10.5333 | 0 | 0 | 0 | Due to failure of B-ph CT of Jharsuguda-4 Main bay (718) leads to Bus-2 tripped at Dharamjaygarh & Line tripped on operation of LBB protection. | SEFT |  |  |  | Due to failure of B-ph CT of Jharsuguda-4 Main bay (718) leads to Bus-2 tripped at Dharamjaygarh & Line tripped on operation of LBB protection.
[6 empty] | 2019-03-26 | 9:24 | 2019-03-26 | 20:28 |  |  |  | 11.0667 | 0 | 0 | 0 | For erection of failure B-ph CT and isolator of Main Bay (718) at Dharamjaygarh end. | OSPT
[6 empty] | 2019-03-26 | 9:24 | 2019-03-26 | 20:28 |  |  |  | 21.6 | 0 | 0 | 0 | For erection of failure B-ph CT and isolator of Main Bay (718) at Dharamjaygarh end. | OSPT
[6 empty] | 2019-03-26 | 9:24 | 2019-03-26 | 20:28 |  |  |  | 21.6 | 0 | 0 | 0 | For erection of failure B-ph CT and isolator of Main Bay (718) at Dharamjaygarh end. | OSPT
[6 empty] | 2019-03-26 | 9:24 | 2019-03-26 | 20:28 |  |  |  | 21.6 | 0 | 0 |  |  | 0 |  |  |  | For erection of failure B-ph CT and isolator of Main Bay (718) at Dharamjaygarh end.
|  | 765kV D'JAIGARH- JHARSUGUDA IV Total | [10 empty] | 21.6 | [10 empty] | 97.1%
271 |  | SWITCHABLE LR_D'JAIGARH1_RANCHI | 240 | WRTS-I
|  | SWITCHABLE LR_D'JAIGARH1_RANCHI Total | [21 empty] | 100%
272 |  | SWITCHABLE LR_D'JAIGARH2_RANCHI | 240 | WRTS-I
|  | SWITCHABLE LR_D'JAIGARH2_RANCHI Total | [21 empty] | 100%