## TRIPPINGS (hidden)
ELEMENT WISE TRIPPING DETAILS FOR POWERGRID WRTS FOR THE MONTH OF AUG-19
|  | POWERGRID WRTS |  | 2019-08-31 |  |  |  |  | ATTRIBUTED TO ( IN HRS:MIN)
SN | EVENT NO. | NAME OF LINE/ICT | OWENRSHIP | Tripping No. | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | LICENCEE | OTHERS | SYSTEM CONSTR. | DEEMED AVAILABLE | OUTAGE CATEGORY | UNIT OUT DUE TO TRIPPING OF LINE | REASON | OUTAGE CATEGORY | Tripping Code | Restoration Code | WRLDC Comments | POWERGRID Comments
1 | 707054 | 765kV DURG PS -WARDHA_3 | WR-I | 0 | 2019-08-01 | 0:00 | 2019-08-03 | 9:17 | 0 | 0 | 0 | 1900-01-01 09:17 | D | N | Line kept uncharged due to system constraint as per WRLDC instruction. | LVRD | 07/1436,NL-07/668 | 08/170, NL-08/58
2 | 707068 | 765kV PUNE(GIS)-SOLAPUR | WR-I | 0 | 2019-08-01 | 0:00 | 2019-08-05 | 9:05 | 0 | 0 | 0 | 1900-01-03 09:05 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR's converted as BR's at 12:22 hrs at Pune-GIS & at 12:42 hrs at Solapur end. | LVRD | 07/1629, NL-07/748 | 08/284, NL-08/102
3 | 707071 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | WR-I | 0 | 2019-08-01 | 0:00 | 2019-08-01 | 6:15 | 0 | 0 | 0 | 0.26042 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 11:42 hrs. | LVRD | 07/1726, NL-07/782 | 08/06, NL-08/03
4 | 707077 | 765kV DURG PS -WARDHA_2 | WR-I | 0 | 2019-08-01 | 0:00 | 2019-08-09 | 8:18 | 0 | 0 | 0 | 1900-01-07 08:18 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 18:32 hrs. | LVRD | 07/1831, NL-07/824 | 08/598, NL-07/206
5 | 707095 | 765kV WARDHA - AURANGABAD(PG) I | WR-I | 0 | 2019-08-01 | 0:00 | 2019-08-08 | 10:21 | 0 | 0 | 0 | 1900-01-06 10:21 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Wardha at 03:18 hrs. | LVRD | 07/2153, NL-07/994 | 08/521, NL-08/194
6 | 707100 | 765kV WARDHA - AURANGABAD(PG) III | WR-I | 0 | 2019-08-01 | 0:00 | 2019-08-18 | 6:34 | 0 | 0 | 0 | 1900-01-16 06:34 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Wardha at 16:11 hrs. | LVRD | 07/2183, NL-07/1009 | 08/1147, 418
7 | 708001 | 765kV AURANGABAD(PG)-PADGHE(GIS) I | WR-I | 0 | 2019-08-01 | 1:15 | 2019-08-12 | 9:47 | 0 | 0 | 0 | 1900-01-10 08:32 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 01:34 hrs. | LVRD | 08/01, NL-08/01 | 08/782, NL-08/263
8 | 708002 | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-01 | 9:57 | 2019-08-01 | 19:32 | 0 | 0.39931 | 0 | 0 | O | N | For Shunt reactor erection work. Bay belongs to NTPC | OMSU | 08/20 | 08/49
9 | 708003 | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-02 | 8:54 | 2019-08-02 | 22:15 | 0 | 0 | 0 | 0.55625 | D | N | Outage availed by NTPC for Shunt reactor erection work at Korba end. | OMSU | 08/96 | 08/163
10 | 708004 | 765kV SEONI-WARDHA I | WR-I | 0 | 2019-08-02 | 11:40 | 2019-08-02 | 18:39 | 0.29097 | 0 | 0 | 0 | L | N | Emergency outage availed for attending oil leakage from radiator fin on spare Line Reactor at Wardha end ( Spare unit is in service in place of R phase). | OSFT | 08/113, NL-08/37 | 08/141, NL-08/45
11 | 708007 | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-03 | 8:42 | 2019-08-03 | 18:55 | 0 | 0 | 0 | 0.42569 | D | N | Outage availed by NTPC for Shunt reactor erection work at Korba end. | OMSU | 08/172 | 08/217
12 | 708008 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WR-I | 0 | 2019-08-03 | 10:53 | 2019-08-04 | 10:14 | 0 | 0 | 0 | 0.97292 | D | N | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD | 08/191, NL-08/63 | 08/237, NL-08/90
13 | 708009 | 765kV DURG PS -WARDHA_4 | WR-I | 0 | 2019-08-03 | 13:36 | 2019-08-05 | 17:59 | 0 | 0 | 0 | 1900-01-01 04:23 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 13:41 hrs. | LVRD | 08/197, NL-08/69 | 08/335, NL-08/120
14 | 708010 | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-03 | 18:55 | 2019-08-03 | 20:17 | 0 | 0 | 0 | 0.056944 | D | N | Line Kept open as per WRLDC instructions for Voltage Regulation. | LVRD | 08/217 | 08/223
15 | 708012 | 400kV KOLHAPUR (GIS)-MAPUSA I | WR-I | 0 | 2019-08-05 | 2:51 | 2019-08-05 | 6:37 | 0 | 0 | 0 | 0.15694 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation | LVRD | 08/269 | 08/275
16 | 708014 | 765kV DURG PS -WARDHA_3 | WR-I | 0 | 2019-08-05 | 16:51 | 2019-08-05 | 21:16 | 0.18403 | 0 | 0 | 0 | L | N | Line is tripped due to failure of "R-ph line reactor LA" at Wardha end. Line reactor at Durg end is converted as Bus reactor at 17:34 hrs with WRLDC code 334/119. Readiness mail is sent at 21:16hrs. | SEFT | --- | ---
17 | 708015 | SWITCHABLE LR_765kV_WARDHA 3_DURG PS | WR-I | 0 | 2019-08-05 | 16:51 | 2019-08-05 | 17:34 | 0 | 0 | 0 | 0.029861 | D | N | SLR is opened after tripping of line due to failure of "R-ph line reactor LA" at Wardha end, and converted as Bus Reactor at 17:34 hrs. as per WRLDC instruction for V/R. | SVRD | --- | 08/334, NL-08/119
18 | 708016 | 765kV PUNE(GIS)-SOLAPUR | WR-I | 0 | 2019-08-05 | 20:58 | 2019-08-13 | 9:32 | 0 | 0 | 0 | 1900-01-06 12:34 | D | N | Line is H/T as per WRLDC instructions for Voltage Regulation and SLRs converted as BR's at 21:10 hrs at Pune-GIS & at 21:31 hrs at Solapur end for V/R. | LVRD | 08/346, NL-08/128 | 08/831, NL-08/283
19 | 708017 | 765kV DURG PS -WARDHA_3 | WR-I | 0 | 2019-08-05 | 21:16 | 2019-08-17 | 6:19 | 0 | 0 | 0 | 1900-01-10 09:03 | D | N | Line is kept out under voltage regulation after sending readiness mail to WRLDC at 21:16 hrs. | LVRD | --- | 08/1075, NL-08/387
20 | 708018 | 400kV KOLHAPUR (GIS)-MAPUSA II | WR-I | 0 | 2019-08-06 | 4:09 | 2019-08-06 | 6:24 | 0 | 0 | 0 | 0.09375 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation. | LVRD | 08/356 | 08/364
21 | 708019 | 765kV TAMNAR PS-KOTRA PS I | WR-I | 0 | 2019-08-06 | 9:14 | 2019-08-06 | 19:25 | 0.42431 | 0 | 0 | 0 | L | N | For Replacement of Broken Insulator & 765KV-RAIGARH-PS-TAMNAR-2 AR in Non auto mode required | OSPT | 08/376, NL-08/139 | 08/420, NL-08/153
22 | 708020 | STATCOM AURANGABAD | WR-I | 0 | 2019-08-06 | 10:33 | 2019-08-06 | 18:30 | 0.33125 | 0 | 0 | 0 | L | N | Emergency outage of coupling transformer at Aurangabad SS for attend sparking on LV isolator B-phase. | OSFT | 08/383 | 08/414
23 | 708022 | 765kV TAMNAR PS-KOTRA PS II | WR-I | 0 | 2019-08-07 | 9:05 | 2019-08-07 | 16:53 | 0.325 | 0 | 0 | 0 | L | N | 'For Replacement of Broken Insulator & 765KV-RAIGARH-PS-TAMNAR-2 AR in Non auto mode required | OSPT | 08/449, NL-08/164 | 08/481, NL-08/179
24 | 708023 | STATCOM AURANGABAD | WR-I | 0 | 2019-08-08 | 4:48 | 2019-08-08 | 10:58 | 0.25694 | 0 | 0 | 0 | L | N | STATCOM tripped on R phase ground over current protection due to burning of R phase isolator contacts of secondary side of Coupling transformer. | OMST | --- | 08/530
25 | 708024 | 765kV WARDHA - AURANGABAD(PG) II | WR-I | 0 | 2019-08-08 | 15:40 | 2019-08-13 | 9:39 | 0 | 0 | 0 | 1900-01-03 17:59 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at 16:03 hrs. | LVRD | 08/550, NL-08/198 | 08/832, NL-08/284
26 | 708025 | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-09 | 9:00 | 2019-08-09 | 19:23 | 0 | 0.43264 | 0 | 0 | O | N | Outage availed by NTPC for Shunt reactor erection work.Bay Belongs to NTPC | OMSU | 08/602 | 08/638
27 | 708027 | 765kV DURG PS -WARDHA_1 | WR-I | 0 | 2019-08-09 | 16:09 | 2019-08-20 | 12:07 | 0 | 0 | 0 | 1900-01-09 19:58 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 16:21 hrs. | LVRD | 08/623, NL-08/217 | 08/1267 NL-08/466
28 | 708028 | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-10 | 8:55 | 2019-08-11 | 10:31 | 0 | 1899-12-31 01:36 | 0 | 0 | O | N | Outage availed by NTPC for Shunt reactor erection work. Opportunity working code availed from WRLDC for TLM works. Line charging attempted at 19:32 hrs. but tripped on O/V. | OMSU | 08/669 | 08/733
29 | 708029 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WR-I | 0 | 2019-08-10 | 9:49 | 2019-08-12 | 23:14 | 0 | 0 | 0 | 1900-01-01 13:25 | D | N | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/674, NL-08/230 | 08/816, NL-08/278
30 | 708030 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | WR-I | 0 | 2019-08-12 | 13:38 | 2019-08-16 | 6:58 | 0 | 0 | 0 | 1900-01-02 17:20 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 14:07 hrs. | LVRD | 08/796, NL-08/269 | 08/991, NL-08/356
31 | 708031 | ICT1_400/220kv_WARDHA | WR-I | 0 | 2019-08-13 | 10:26 | 2019-08-13 | 17:55 | 0.31181 | 0 | 0 | 0 | L | N | For AMP works. | OSPT | 08/842 | 08/865
32 | 708032 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 | WR-I | 0 | 2019-08-13 | 12:48 | 2019-08-13 | 17:55 | 0.21319 | 0 | 0 | 0 | L | N | For line AMP works & Relay Testing, 400KV-PUNE-GIS-PUNE-PG-1, 2 & 4 AR kept in non auto mode. | OSPT | 08/852 | 08/864
33 | 708033 | 765kV PUNE(GIS)-SOLAPUR | WR-I | 0 | 2019-08-13 | 18:36 | 2019-08-16 | 13:03 | 0 | 0 | 0 | 1900-01-01 18:27 | D | N | Line is H/T as per WRLDC instructions for Voltage Regulation and SLRs converted as BR's at 20:26 hrs at Pune-GIS & for V/R. BR's HT at 08:48hrs@Pune & at 08:50hrs@Solapur end. | LVRD | 08/868, NL-08/306 | 08/1016, NL-08/368
34 | 708034 | 765kV AURANGABAD(PG)-SOLAPUR II | WR-I | 0 | 2019-08-13 | 18:52 | 2019-08-13 | 19:24 | 0.022222 | 0 | 0 | 0 | L | N | Line is tripped due to failure of 71152 Tie CB at Solapur end. Readiness for charging of line is conveyed to WRLDC by email at 19:24hrs. | SEFT | --- | ---
35 | 708035 | 765kV AURANGABAD(PG)-SOLAPUR II | WR-I | 0 | 2019-08-13 | 19:24 | 2019-08-13 | 22:39 | 0 | 0 | 0 | 0.13542 | D | N | Line is kept out under voltage regulation after sending readiness mail to WRLDC at 19:24 hrs. | LVRD | --- | 08/879, NL-08/311 |  | Readiness mail attached
36 | 708036 | 765kV WARDHA - AURANGABAD(PG) I | WR-I | 0 | 2019-08-13 | 21:16 | 2019-08-16 | 9:56 | 0 | 0 | 0 | 1900-01-01 12:40 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at hrs. | LVRD | 08/875, NL-08/307 | 08/1007, NL-08/363
37 | 708037 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WR-I | 0 | 2019-08-14 | 10:12 | 2019-08-14 | 20:13 | 0 | 0 | 0 | 0.41736 | D | N | SLR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/891, NL-08/320 | 08/915, NL-08/333
38 | 708038 | 400kV WARORA-PARLI-2_LILOPOINT_PG | WR-I | 0 | 2019-08-14 | 14:51 | 2019-08-14 | 18:07 | 0 | 0.13611 | 0 | 0 | O | N | Emergency outage availed for rectification of hot spot Y-phase wave trap at Warora end. | OMSU | 08/900 | 08/909
39 | 708039 | 765kV SEONI-WARDHA I | WR-I | 0 | 2019-08-15 | 9:49 | 2019-08-17 | 7:16 | 0 | 0 | 0 | 1899-12-31 21:27 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at seoni end . | LVRD | 08/942, NL08/343 | 08/1078, NL-08/388
40 | 708040 | 400kV BHATAPARA-KORBA | WR-I | 0 | 2019-08-15 | 10:07 | 2019-08-15 | 10:17 | 0 | 0 | 0.0069444 | 0 | S | N | Line tripped on over voltage | GOVC | --- | --- |  | Mail from NTPC regrading tripping of line on overvolatage and DR not trigerred as the overvolatge function is threough electromechanical relay is atatched.
41 | 708041 | 400kV BHATAPARA-KORBA | WR-I | 0 | 2019-08-15 | 10:17 | 2019-08-18 | 5:46 | 0 | 0 | 0 | 1900-01-01 19:29 | D | N | Line kept uncharged for Voltage Regulation by WRLDC | LVRD | 08/957 | 08/1144
42 | 708042 | 765kV AURANGABAD(PG)-PADGHE(GIS) I | WR-I | 0 | 2019-08-15 | 16:52 | 2019-08-16 | 7:13 | 0 | 0 | 0 | 0.59792 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 17:09 hrs. | LVRD | 08/973, NL-08/346 | 08/997, NL-08/357
43 | 708043 | 765kV AURANGABAD(PG)-PADGHE(GIS) I | WR-I | 0 | 2019-08-16 | 7:13 | 2019-08-23 | 17:57 | 0 | 0 | 0 | 1900-01-06 10:44 | D | N | 'Outage availed for LILO works at Pune (GIS) by M/s. CWRTL. LILO Aurangabad - PuneGIS charged at 13:36hrs on 22.08.2019 and Padghe - Pune GIS charged at 17:57 hrs on 23.08.2019 | LCSD | 08/997, NL-08/357 | ---
44 | 708044 | 400KV RANCHI-SIPAT I | WR-I | 0 | 2019-08-16 | 9:27 | 2019-08-16 | 21:21 | 0 | 0 | 0.49583 | 0 | S | N | Outage availed by ER for attending Low clearance issue of 400kV New Ranchi - Patratu (D/C) crossing over the 400kV Ranchi - Sipat D/C between location no. 5/0 and 6/0 due to theft of conductor hardware by miscreants. | LMAC | 08/1004, NL-08/360, ER-08/534 | 08/1050, NL-08/380, ER-08/571 |  | Honorable Chief Minister of Jharkhand had set target of 15.08.2019 to charge 400 KV New Ranchi -Patratu line, however conductor hardware theft has resulted in lower clearance between earth wire of 400 KV Ranchi-Sipat TL and bottom conductor of 400 KV New Ranchi -Patratu TL .correspondence with WRPC attached
45 | 708045 | 400KV RANCHI-SIPAT II | WR-I | 0 | 2019-08-16 | 9:37 | 2019-08-16 | 20:50 | 0 | 0 | 0.46736 | 0 | S | N | Outage availed by ER for attending Low clearance issue of 400kV New Ranchi - Patratu (D/C) crossing over the 400kV Ranchi - Sipat D/C between location no. 5/0 and 6/0 due to theft of conductor hardware by miscreants. | LMAC | 08/1005, NL-08/361, ER-08/535 | 08/1051, NL-08/381, ER-08/572 |  | Honorable Chief Minister of Jharkhand had set target of 15.08.2019 to charge 400 KV New Ranchi -Patratu line, however conductor hardware theft has resulted in lower clearance between earth wire of 400 KV Ranchi-Sipat TL and bottom conductor of 400 KV New Ranchi -Patratu TL .correspondence with WRPC attached
46 | 708046 | 765kV WARDHA - AURANGABAD(PG) I | WR-I | 0 | 2019-08-16 | 23:25 | 2019-08-21 | 11:42 | 0 | 0 | 0 | 1900-01-03 12:17 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at hrs. | LVRD | 08/1062, NL-08/384 | 08/1336, NL-08/497
47 | 708048 | 765kV DURG PS -WARDHA_4 | WR-I | 0 | 2019-08-17 | 22:22 | 2019-08-28 | 8:48 | 0 | 0 | 0 | 1900-01-09 10:26 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 22:37 Hrs. | LVRD | 08/1130, NL-08/412 | 08/1768, NL-08/689
48 | 708050 | 400kV RAIGARH-JHARSUGUDA I | WR-I | 0 | 2019-08-18 | 2:21 | 2019-08-18 | 2:39 | 0.0125 | 0 | 0 | 0 | L | N | Line tripped on B-G fault at 02:21 Hrs at Raigarh end due to rain, lightning and thunderstorm. Fault details from Raigarh: B-G 7.396KA,47.88KM from Sundergarh . 5.054KA, 56.52KM from Raigarh end. News paper cutting attached. Line was charged in 0:18 hours withouta nay maintainnece works | LEFT | 08/1140, NL-08/415, ER-08/608 | ---
49 |  | 400kV RAIGARH-JHARSUGUDA II | WR-I | 0 | 2019-08-18 | 2:52 | 2019-08-18 | 8:00 | 0 | 0 | 0.21389 | 0 | S | N | Line tripped on B-G fault at 02:52 Hrs dure to LA Conductionat Jharsuguda , considering safety of working staff the restoration work could not be commenced in view of Heavy lighning and rains. 'Newspaper cutting attached | LNCC
50 | 708051 | 400kV RAIGARH-JHARSUGUDA II | WR-I | 0 | 2019-08-18 | 8:00 | 2019-08-18 | 14:25 | 0.26736 | 0 | 0 | 0 | L | N | Line tripped on B-G fault at 02:52 Hrs during persistent B-G fault due to rain and thunderstorm. Fault details from Raigarh: 49.902(M1),46.64KM(M2) from Raigarh end 5.2KA, 60KM(M1), 60.7KM(M2) | SEFT | --- | ---
51 | 708052 | 400kV RAIGARH-JHARSUGUDA I | WR-I | 0 | 2019-08-18 | 6:18 | 2019-08-18 | 6:18 | 0 | 0 | 0 | 0 | L | N | Line AR successful, B-E, F.C-9.873, 13.473KM(M1), 10.553kM(M2) | LART | --- | ---
52 |  | 400kV LARA(NTPC)-CHAMPA II | WR-I | 0 | 2019-08-18 | 5:52 | 2019-08-18 | 7:13 | 0 | 0 | 0.05625 | 0 | S | N | Line tripped on B-G fault due to rains, lightning and thunderstorm. Fault details at Champ: B-G, 113km, 4.7kA. At Lara(NTPC): B-G, 6.9km, 13.55kA. Fault is in Raigarh TLM. Newspaper cutting atatched | LNCC | 08/1151 | --- | As per the submitted details considered under LNCC category. MS WRPC may kindly review
53 | 708053 | 765kV WARDHA - AURANGABAD(PG) III | WR-I | 0 | 2019-08-18 | 14:59 | 2019-08-23 | 12:25 | 0 | 0 | 0 | 1900-01-03 21:26 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Wardha at 15:19 hrs. | LVRD | 08/1172 NL-08/427 | 08/1491 NL-08/564
54 | 708054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WR-I | 0 | 2019-08-20 | 10:55 | 2019-08-22 | 13:09 | 0 | 0 | 0 | 1900-01-01 02:14 | D | N | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/1266 NL-08/465 | 08/1422 NL-08/541
55 | 708055 | 765kV D'JAIGARH-RANCHI I | WR-I | 0 | 2019-08-20 | 13:28 | 2019-08-20 | 18:50 | 0.22361 | 0 | 0 | 0 | L | N | Outage availed for rectification of damage conductor by Tamnar-TLM. | OSPT | 08/1272 NL-08/476, & Er-703 | 08/1292 NL-08/481, & Er-718
56 | 708056 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | WR-I | 0 | 2019-08-20 | 16:34 | 2019-08-20 | 19:57 | 0.14097 | 0 | 0 | 0 | L | N | Emergrncy outage is availed for rectifing OPGW suspension clamps at Tower NO: 16. | OSFT | 08/1279 | ---
57 | 708057 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | WR-I | 0 | 2019-08-20 | 16:47 | 2019-08-20 | 19:59 | 0.13333 | 0 | 0 | 0 | L | N | Emergrncy outage is availed for rectifing OPGW suspension clamps at Tower NO: 16. | OSFT | 08/1282 | ---
58 | 708058 | 765kV PUNE(GIS)-SOLAPUR | WR-I | 0 | 2019-08-20 | 17:01 | 2019-08-20 | 20:07 | 0 | 0 | 0 | 0.12917 | D | N | To facilitate emergency outage of 400KV Pune-Pune-1&2 and control loading on 400KV Pune-Pune-3&4. Ki ndly change the reason as mentioned above category changed to LPRD | LPRD | 08/1283, NL-08/476 | 08/1307, NL-08/484
59 | 708059 | 765kV PUNE(GIS)-SOLAPUR | WR-I | 0 | 2019-08-20 | 20:07 | 2019-08-26 | 10:09 | 0 | 0 | 0 | 1900-01-04 14:02 | D | N | Line kept open as per WRLDC instructions for Voltage Regulation and . SLRs converted as BRs at both ends for V/R. SLR at Pune GIS is converted as B/R at 20:26hrs. SLR at Solapur is converted as B/R at 20:55hrs. | LVRD | 08/1307, NL-08/484 | 08/1625, NL-08/630
60 | 708060 | 400kV LARA(NTPC)-KOTRA PS I | WR-I | 0 | 2019-08-21 | 9:34 | 2019-08-21 | 22:10 | 0 | 0.525 | 0 | 0 | O | N | Outage availed by Lara NTPC for Isolator stem replacement. Bay Belongs to NTPC | OMSU | 08/1327 | 08/1386
61 | 708061 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WR-I | 0 | 2019-08-21 | 10:04 | 2019-08-21 | 18:52 | 0 | 0 | 0 | 0.36667 | D | N | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/1334 NL-08/496 | 08/1375 NL-08/516
62 | 708062 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WR-I | 0 | 2019-08-21 | 11:22 | 2019-08-21 | 18:12 | 0 | 0 | 0 | 0.28472 | D | N | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/1338 | 08/1372
63 | 708063 | 765kV DURG PS -WARDHA_2 | WR-I | 0 | 2019-08-21 | 16:36 | 2019-08-31 | 24:00 | 0 | 0 | 0 | 1900-01-09 07:24 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 16:40 Hrs. | LVRD | 08/1360, NL-08/512 | ---
64 | 708065 | 765kV WARDHA - AURANGABAD(PG) I | WR-I | 0 | 2019-08-21 | 20:19 | 2019-08-29 | 10:30 | 0 | 0 | 0 | 1900-01-06 14:11 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at 21:22 hrs. | LVRD | 08/1383 NL-08/520 | 08/1842 NL-08/715
65 | Missing | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | WR-I |  | 2019-08-21 | 12:50 | 2019-08-22 | 13:36 | 0 | 0 | 0 | 1899-12-31 00:46 | D | N | For Construction works of 765kV Aurangabad-Pune | SCSD
66 | 708066 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WR-I | 0 | 2019-08-22 | 11:10 | 2019-08-22 | 17:23 | 0 | 0 | 0 | 0.25903 | D | N | LR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/1413 NL-08/537 | 08/1439 NL-08/545
67 | 708067 | 765kV AURANGABAD (PG) - PUNE (GIS) LINE | WR-I | 0 | --- | --- | 2019-08-22 | 13:36 | 0 | 0 | 0 | 0 |  | N | FIRST TIME CHARGING of 765kV Aurangabad - Pune (GIS) Line alongwith both end line reactors are in service. [LILO of 765kV Aurangabad - Padghe ckt - 1 at Pune (GIS)] | --- | --- | 08/1420 NL-08/539
68 | 708070 | 400kV RAIPUR-SIPAT I | WR-I | 0 | 2019-08-23 | 11:23 | 2019-08-23 | 21:08 | 0 | 0.40625 | 0 | 0 | O | N | For PMU Installation at Sipat (NTPC) end | OMSU | 08/1484 | 08/1525
69 | 708071 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | WR-I | 0 | 2019-08-23 | 11:35 | 2019-08-23 | 11:58 | 0 | 0.015972 | 0 | 0 | O | N | Emergency outage availed by MSETCL for shifting of bus at Waluj end as their TBC was engaged. | OMSU | 08/1487 | 08/1490
70 | 708072 | 765kV WARDHA - AURANGABAD(PG) II | WR-I | 0 | 2019-08-23 | 13:29 | 2019-08-23 | 17:15 | 0.15694 | 0 | 0 | 0 | L | N | Emergency outage availed for attending 03 nos.opened jumpers at Loc.No. 335. Readyness mail sent to WRLDC at 17:15 hrs | OSFT | 08/1495 NL-08/565 | ---
71 | 708073 | 765kV D'JAIGARH- JHARSUGUDA III | WR-I | 0 | 2019-08-23 | 14:18 | 2019-08-23 | 15:36 | 0 | 0 | 0.054167 | 0 | S | N | Line tripped on Y ph - B ph fault. FC Y ph 17.2 KA, FC B ph 12.8 KA and FD 55.59 km from Dharamjayagarh end du to heavy rains, lightning , line was restored in 1.18 hours without any maintainence works.Newspaper cutting attached | LNCC | --- | 08/1501 NL-08/569, ER 08/826
72 | 708074 | 765kV WARDHA - AURANGABAD(PG) II | WR-I | 0 | 2019-08-23 | 17:15 | 2019-08-23 | 19:24 | 0 | 0 | 0 | 0.089583 | D | N | Line charged as per WRLDC instructions | LVRD | --- | 08/1512 NL-08/574 |  | Readiness mail attached
73 | 708075 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | WR-I | 0 | 2019-08-23 | 19:06 | 2019-08-24 | 12:28 | 0 | 0 | 0 | 0.72361 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Aurangabad end at 19:50 hrs. | LVRD | 08/1518 NL-08/576 | ---
74 | 708076 | 765kV PUNE-GIS-PADGHE(GIS) | WR-I | 0 | --- | --- | 2019-08-23 | 17:57 | 0 | 0 | 0 | 0 |  | N | First Time Charged, charged from Pune-GIS end | --- | --- | 08/106 NL-08/571
75 | 708077 | 400kV RAIGARH-JHARSUGUDA III | WR-I | 0 | 2019-08-24 | 10:47 | 2019-08-24 | 15:36 | 0.20069 | 0 | 0 | 0 | L | N | Emergency outage availed by ER-II/Odisha/ Sundargarh for attending 03 nos of Porcelain insulators broken at bottom phase (Y Phase) at location 781. | OSFT | 08/1538 NL-08/592 ER-08/847 | 08/1553 NL-08/603 ER-08/857
76 | 708078 | 765kV AURANGABAD_PUNE(GIS) | WR-I | 0 | 2019-08-24 | 21:30 | 2019-08-31 | 10:17 | 0 | 0 | 0 | 1900-01-05 12:47 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Pune GIS end at 21:47 and Aurangabad end at 22:04 | LVRD | 08/1576 NL-08/619 | 08/1969 NL-08/770
77 | 708079 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | WR-I | 0 | 2019-08-25 | 9:46 | 2019-08-25 | 13:37 | 0.16042 | 0 | 0 | 0 | L | N | Outage availed for line AMP works & Relay Testing. | OSPT | 08/1594 | 08/1598
78 | 708080 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WR-I | 0 | 2019-08-25 | 11:28 | 2019-08-25 | 20:00 | 0 | 0 | 0 | 0.35556 | D | N | BR H/T as per WRLDC instructions for Voltage Regulation. | SVRD | 08/1596, NL-08/623 | 08/1610, NL-08/628
79 | 708081 | 400kV KOLHAPUR (GIS)-MAPUSA I | WR-I | 0 | 2019-08-25 | 13:23 | 2019-08-25 | 13:23 | 0 | 0 | 0 | 0 | L | N | A/R Successful at both ends on B ph to E fault. At Kolapur FD=94.7km, FC=1.126kA and at Mapusa end FD=29.32km, FC=2.42kA | LART | --- | ---
80 | 708082 | 400kV KOLHAPUR (GIS)-MAPUSA II | WR-I | 0 | 2019-08-25 | 13:23 | 2019-08-26 | 13:09 | 0 | 0 | 0.99028 | 0 | S | N | Line tripped due to vegetaive deposition in chowkal region(Photographs attached). It may please be noted that Chowkal village in Amboli, Maharashtra is situated at an elelvation of 870mtrs above grouund level. The tower is located at hilltop which is covered in cloud dense fog. The area suffers from vegetative pollution moss deposition. | LNCC | --- | 08/1652 | As per the submitted details considered under LNCC category. MS WRPC may kindly review
81 | 708083 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | WR-I | 0 | 2019-08-26 | 9:46 | 2019-08-26 | 18:09 | 0 | 0 | 0 | 0.34931 | D | N | Bus Reactor hand tripped as per WRLDC instructions for voltage regulation. | SVRD | 08/1646 | 08/1663
82 | 708084 | 400KV RANCHI-SIPAT I | WR-I | 0 | 2019-08-26 | 12:21 | 2019-08-26 | 18:44 | 0 | 0.26597 | 0 | 0 | O | N | For installation of PMU at Sipat(NTPC) end | OMSU | 08/1650, NL-08/635, ER-08/919 | 08/1661, NL-08/646, ER-08/943
83 | 708085 | 765kV PUNE(GIS)-SOLAPUR | WR-I | 0 | 2019-08-27 | 1:20 | 2019-08-31 | 24:00 | 0 | 0 | 0 | 1900-01-03 22:40 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Pune GIS end at 02:28 hrs and Solapur end at 01:36 hrs. | LVRD | 08/1681, NL-08/654 | ---
84 | 708086 | 400kV KORBA-RAIPUR III | WR-I | 0 | 2019-08-27 | 8:57 | 2019-08-27 | 19:44 | 0 | 0.44931 | 0 | 0 | O | N | For Bay PM . Bay Belongs to NTPC | OMSU | 08/1689 | 08/1737
85 | 708087 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | WR-I | 0 | 2019-08-27 | 9:56 | 2019-08-27 | 20:25 | 0 | 0 | 0 | 0.43681 | D | N | SLR is H/T as per WRLDC instruction for V/R | SVRD | 08/1699, NL-08/666 | 08/1739, NL-08/679
86 | 708088 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | WR-I | 0 | 2019-08-27 | 11:41 | 2019-08-28 | 21:44 | 0 | 0 | 0 | 1899-12-31 10:03 | D | N | Bus Reactor is hand tripped as per WRLDC instructions for voltage regulation. | SVRD | 08/1710, NL-08/671 | 08/1820
87 | 708089 | 400kV BHADRAVATI-CHANDRAPUR III | WR-I | 0 | 2019-08-27 | 13:37 | 2019-08-28 | 19:02 | 1899-12-31 05:25 | 0 | 0 | 0 | L | N | Emergency outage of line is availed by Chandrapur(MSTCL) for Bay Isolators rectification works. | OMST | 08/1714 | 08/1807
88 | 708090 | 765kV DURG PS -WARDHA_3 | WR-I | 0 | 2019-08-28 | 14:17 | 2019-08-31 | 24:00 | 0 | 0 | 0 | 1900-01-02 09:43 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at Hrs. | LVRD | 08/1791, NL-08/699 | ---
89 | 708091 | 765kV WARDHA - AURANGABAD(PG) III | WR-I | 0 | 2019-08-28 | 17:17 | 2019-08-28 | 20:01 | 0 | 0 | 0.11389 | 0 | S | N | Line tripped on B Phase Buccolz at Aurangabad due to ingress of moisture due to heavy rains . As buccolz is exposed directly to rains inspite of POWERGRID best efforts due to heavy rains moisture ingressed in Buccolz leading to maloperation of buccolz.Charging clerance given to WRLDC at 2001 hours. Newspaper cutting attached | LNCC |  |  | As per the submitted details considered under LNCC category. MS WRPC may kindly review
90 | 708092 | 765kV WARDHA - AURANGABAD(PG) III | WR-I | 0 | 2019-08-28 | 20:01 | 2019-08-31 | 24:00 | 0 | 0 | 0 | 1900-01-02 03:59 | D | N | Line kept open by WRLDC on high voltage and to convert LR as BR at Wardha end. | LVRD | 08/1821, NL 08/712
91 | 708093 | 400kV BHADRAVATI-CHANDRAPUR III | WR-I | 0 | 2019-08-28 | 19:23 | 2019-08-28 | 20:03 | 0.027778 | 0 | 0 | 0 | L | N | Line tripped on DT received from MSETCL | OMST | 08/1814
92 | 708094 | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR | WR-I | 0 | 2019-08-29 | 9:39 | 2019-08-29 | 17:39 | 0.33333 | 0 | 0 | 0 | L | N | For Reactor AMP works. | OSPT | 08/1838, NL-08/713 | 08/1866, NL-08/736
93 | 708095 | 400KV RAIPUR-SIPAT II | WR-I | 0 | 2019-08-29 | 10:40 | 2019-08-29 | 19:25 | 0 | 0.36458 | 0 | 0 | O | N | For installation of PMU at Sipat (NTPC) end. Line charged from Raipur but tripped by receipt of DT from Sipat end due to over voltage protection operated at Sipat end. | OMSU | 08/1846 | 08/1868
94 | 708096 | SWITCHABLE LR_765kV_AURANGABAD_PUNE GIS | WR-I | 0 | 2019-08-29 | 10:48 | 2019-08-29 | 18:34 | 0 | 0 | 0 | 0.32361 | D | N | SLR H/T as per WRLDC instructions for Voltage Regulation | SVRD | 08/1849, NL-08/719 | 08/1930, NL-08/750
95 | 708097 | 400kV BHADRAVATI-CHANDRAPUR II | WR-I | 0 | 2019-08-29 | 11:39 | 2019-08-29 | 12:11 | 0 | 0.022222 | 0 | 0 | O | N | Outage availed by MSETCL for shifting of line from Main Bus-2 to Main Bus-1 at Chandrapur (MSETCL) end as that TBC is engaged | OMSU | 08/1852 | 08/1852
96 | 708098 | 400kV KORBA-RAIPUR IV | WR-I | 0 | 2019-08-29 | 17:07 | 2019-08-29 | 19:03 | 0 | 0 | 0.080556 | 0 | S | N | Line tripped on R-B Phase fault due to heavy rain and thunderstorm. Fault details from Raipur end - FD-171 km, FC-R-3.2 kA, B-2.84 kA. Fault details from Korba end - FD- 42.4 km, FC-R-9.97 kA. | LNCC | --- | 08/1869 | As per the submitted details considered under LNCC category. MS WRPC may kindly review
97 | 708100 | 400KV RAIPUR-SIPAT II | WR-I | 0 | 2019-08-29 | 19:25 | 2019-08-29 | 21:33 | 0 | 0 | 0.088889 | 0 | S | N | For installation of PMU at Sipat (NTPC) end. Line charged from Raipur but tripped by receipt of DT from Sipat end due to over voltage protection operated at Sipat end AT 19:25 Hrs. Again charging attempt taken from Sipat and synchronised at raipur at 21:33 Hrs. | GOVC | 08/1868 | 08/1879
98 | 708101 | 400KV RAIPUR-WARDHA I | WR-I | 0 | 2019-08-30 | 8:53 | 2019-08-30 | 19:53 | 0.45833 | 0 | 0 | 0 | L | N | Line AMP works & 400KV Raipur Wardha ckt # 2 A/R in non auto mode required | OSPT | 08/1899 | 08/1937
99 | 708102 | 400kV RAIPUR-BHADRAVATI III | WR-I | 0 | 2019-08-30 | 12:36 | 2019-08-30 | 12:36 | 0 | 0 | 0 | 0 | L | N | Line A/R Successful at both ends on B phase to E fault.,FD=202km, FC=1.87kA from Raipur and FD=151.km,FC=2.42kA from Bhadrawati end | LART | --- | ---
100 | 708103 | 400KV RAIPUR-WARDHA II | WR-I | 0 | 2019-08-31 | 8:54 | 2019-08-31 | 20:12 | 0.47083 | 0 | 0 | 0 | L | N | For Line AMP works & 400KV Raipur Wardha ckt # 1 A/R in non auto mode required | OSPT | 08/1964 | 08/1999
101 | 708104 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | WR-I | 0 | 2019-08-31 | 17:44 | 2019-08-31 | 24:00 | 0 | 0 | 0 | 0.26111 | D | N | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Aurangabad end at 17:47 hrs. | LVRD | 08/1990, NL-08/780 | ---
102 | Missing | 765KV/400KV CHAMPA-ICT-4 | WR-I | 0 | 2019-08-31 | 16:06 | 2019-08-31 | 16:17 | 0.0076389 | 0 | 0 | 0 | L | N | ICT tripped due to malfunctioning of BCU | OMST
103 | Missing | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-23 | 18:50 | 2019-08-23 | 20:13 | 0 | 0 | 0.057639 | 0 | S | N | Due to heavy rains and lightning ,tripped on R-Y fault. KSTPS end indications: R ph current-4.03 kA, Y ph current-3.849kA, distance-161.2 km. Essar Mahan end indication: R ph current - 5.98 kA, Y ph current - 5.08 kA, distance - 74.79 km. Newspaper cutting atatched. | LNCC |  |  | As per the submnitted details considered under LNCC category. MS WRPC may kindly review
104 | Missing | 400kV KORBA-MAHAN | WR-I | 0 | 2019-08-30 | 3:54 | 2019-08-30 | 4:59 | 0 | 0 | 0.045139 | 0 | S | N | Line tripped due to heavy rains and lightning on Line tripped on Y ph -to E fault. FC-7.211KA,FD-35.37km from Mahan end .'Patrollin report atatched | LNCC |  |  | As per the submnitted details considered under LNCC category. MS WRPC may kindly review
TOTAL | (A)+(B)= | GRAND TOTAL IN HRS:MIN | [6 empty] | 1900-01-05 04:18 | 1900-01-03 02:01 | 1900-01-01 16:06 | 1900-07-02 18:21
[7 empty] | TOTAL HRS |  | 148.3 | 98.02 | 64.1 | 4434.35
[7 empty] | (B) Total Outage Hrs due to more than two tripping |  |  |  |  | 0
[7 empty] | (A) Total Outage Hrs in Western Region |  |  |  |  | 148.3
[7 empty] | (A+B) Grand Total Outage Hrs (including more than two tripping) |  |  |  |  | 148.3
Formulas:
LICENCEE = SUM(J6:[LICENCEE, row above])
OTHERS = SUM(K6:[OTHERS, row above])
SYSTEM CONSTR. = SUM(L6:[SYSTEM CONSTR., row above])
DEEMED AVAILABLE = SUM(M6:[DEEMED AVAILABLE, row above])

## SOP
Standard of Performance data for the month of August - 2019
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., Western Region-I | [21 empty] | 744
ANNEXURE-A
SN | Unique ID of transmission Element | NAME OF LINE/ICT | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  | Total outage in days (1) | DURATION OF OUTAGE ATTRIBUTABLE TO (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by WRLDC | Category
[6 empty] | Date | Time | Date | Time | No. of towers damaged | no. of insulator failed |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | WR1_L_001 | 400kV KORBA-KORBA(WEST) | 14 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-KORBA(WEST) Total
2 | WR1_L_002 | 400kV KORBA-BHILAI I | 197 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-BHILAI I Total
3 | WR1_L_003 | 400kV KORBA-BHILAI II | 192 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-BHILAI II Total
4 | WR1_L_004 | 400kV BHILAI-KORADI | 272 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHILAI-KORADI Total
5 | WR1_L_005 | 400kV KORADI-SATPURA | 149 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORADI-SATPURA Total
6 | WR1_L_006 | 400kV RAIPUR-BHILAI I | 13 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-BHILAI I Total
7 | WR1_L_007 | 400kV BHILAI-BHADRAVATI I | 322 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHILAI-BHADRAVATI I Total
8 | WR1_L_008 | 400kV RAIPUR-BHADRAVATI I | 333 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-BHADRAVATI I Total
9 | WR1_L_009 | 400kV RAIPUR-BHADRAVATI II | 345.55 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-BHADRAVATI II Total
10 | WR1_L_010 | 400kV RAIPUR-BHADRAVATI III | 345.55 | WRTS-I |  | 2019-08-30 | 12:36 | 2019-08-30 | 12:36 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line A/R Successful at both ends on B phase to E fault.,FD=202km, FC=1.87kA from Raipur and FD=151.km,FC=2.42kA from Bhadrawati end | WRPC | 100% | LART
|  | 400kV RAIPUR-BHADRAVATI III Total | [10 empty] | 0
11 | WR1_L_011 | 400kV BHADRAVATI-CHANDRAPUR I | 20 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHADRAVATI-CHANDRAPUR I Total
12 | WR1_L_012 | 400kV BHADRAVATI-CHANDRAPUR II | 20 | WRTS-I |  | 2019-08-29 | 11:39 | 2019-08-29 | 12:11 |  |  |  | 0 | 0.53333 | 0 | 0 |  |  |  | Outage availed by MSETCL for shifting of line from Main Bus-2 to Main Bus-1 at Chandrapur (MSETCL) end as that TBC is engaged | WRPC | 100% | OMSU
|  | 400kV BHADRAVATI-CHANDRAPUR II Total | [10 empty] | 0
13 | WR1_L_013 | 400kV BHADRAVATI-CHANDRAPUR III | 22.42 | WRTS-I |  | 2019-08-27 | 13:37 | 2019-08-28 | 19:02 |  |  |  | 29.4167 | 0 | 0 | 0 |  |  |  | Emergency outage of line is availed by Chandrapur(MSTCL) for Bay Isolators rectification works. | WRPC | 95.96% | OMST
[6 empty] | 2019-08-28 | 19:23 | 2019-08-28 | 20:03 |  |  |  | 0.66667 | 0 | 0 | 0 |  |  |  | Line tripped on DT received from MSETCL |  |  | OMST
|  | 400kV BHADRAVATI-CHANDRAPUR III Total | [10 empty] | 30.0833
14 | WR1_L_014 | 400kV BHADRAVATI-CHANDRAPUR IV | 22.42 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHADRAVATI-CHANDRAPUR IV Total
15 | WR1_L_015 | 400kV MAHAN-VINDHYACHAL | 19 | WRTS-I | [16 empty] | WRPC | 100%
400kV MAHAN-VINDHYACHAL Total
16 | WR1_L_016 | 400kV KORBA-MAHAN | 196 | WRTS-I |  | 2019-08-01 | 9:57 | 2019-08-01 | 19:32 |  |  |  | 0 | 9.5833 | 0 | 0 |  |  |  | For Shunt reactor erection work. Bay belongs to NTPC | WRPC | 100% | OMSU
[6 empty] | 2019-08-02 | 8:54 | 2019-08-02 | 22:15 |  |  |  | 0 | 0 | 0 | 13.35 |  |  |  | Outage availed by NTPC for Shunt reactor erection work at Korba end. |  |  | OMSU
[6 empty] | 2019-08-03 | 8:42 | 2019-08-03 | 18:55 |  |  |  | 0 | 0 | 0 | 10.2167 |  |  |  | Outage availed by NTPC for Shunt reactor erection work at Korba end. |  |  | OMSU
[6 empty] | 2019-08-03 | 18:55 | 2019-08-03 | 20:17 |  |  |  | 0 | 0 | 0 | 1.3667 |  |  |  | Line Kept open as per WRLDC instructions for Voltage Regulation. |  |  | LVRD
[6 empty] | 2019-08-09 | 9:00 | 2019-08-09 | 19:23 |  |  |  | 0 | 10.3833 | 0 | 0 |  |  |  | Outage availed by NTPC for Shunt reactor erection work.Bay Belongs to NTPC |  |  | OMSU
[6 empty] | 2019-08-10 | 8:55 | 2019-08-11 | 10:31 |  |  |  | 0 | 25.6 | 0 | 0 |  |  |  | Outage availed by NTPC for Shunt reactor erection work. Opportunity working code availed from WRLDC for TLM works. Line charging attempted at 19:32 hrs. but tripped on O/V. |  |  | OMSU
[6 empty] | 2019-08-23 | 18:50 | 2019-08-23 | 20:13 |  |  |  | 0 | 0 | 1.3833 | 0 |  |  |  | Due to heavy rains and lightning ,tripped on R-Y fault. KSTPS end indications: R ph current-4.03 kA, Y ph current-3.849kA, distance-161.2 km. Essar Mahan end indication: R ph current - 5.98 kA, Y ph current - 5.08 kA, distance - 74.79 km. Newspaper cutting atatched. |  |  | LNCC
[6 empty] | 2019-08-30 | 3:54 | 2019-08-30 | 4:59 |  |  |  | 0 | 0 | 1.0833 | 0 |  |  |  | Line tripped due to heavy rains and lightning on Line tripped on Y ph -to E fault. FC-7.211KA,FD-35.37km from Mahan end .'Patrollin report atatched |  |  | LNCC
|  | 400kV KORBA-MAHAN Total | [10 empty] | 0
17 | WR1_L_017 | 400kV VINDHYACHAL-KORBA II | 288.994 | WRTS-I | [16 empty] | WRPC | 100%
400kV VINDHYACHAL-KORBA II Total
18 | WR1_L_018 | 400kV SATPURA-SEONI | 1.507 | WRTS-I | [16 empty] | WRPC | 100%
400kV SATPURA-SEONI Total
19 | WR1_L_019 | 400kV BHILAI-SEONI | 1.498 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHILAI-SEONI Total
20 | WR1_L_020 | 400kV BHILAI-BHATAPARA | 90.453 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHILAI-BHATAPARA Total
21 | WR1_L_021 | 400kV BHATAPARA-KORBA | 123.73 | WRTS-I |  | 2019-08-15 | 10:07 | 2019-08-15 | 10:17 |  |  |  | 0 | 0 | 0.16667 | 0 |  |  |  | Line tripped on over voltage | WRPC | 100% | GOVC
[6 empty] | 2019-08-15 | 10:17 | 2019-08-18 | 5:46 |  |  |  | 0 | 0 | 0 | 67.4833 |  |  |  | Line kept uncharged for Voltage Regulation by WRLDC |  |  | LVRD
|  | 400kV BHATAPARA-KORBA Total | [10 empty] | 0
22 | WR1_L_022 | 400kV KORBA-SIPAT | 68.653 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-SIPAT Total
23 | WR1_L_023 | 400kV RAIPUR-SIPAT I | 149.12 | WRTS-I |  | 2019-08-23 | 11:23 | 2019-08-23 | 21:08 |  |  |  | 0 | 9.75 | 0 | 0 |  |  |  | For PMU Installation at Sipat (NTPC) end | WRPC | 100% | OMSU
|  | 400kV RAIPUR-SIPAT I Total | [10 empty] | 0
24 | WR1_L_024 | 400KV RAIPUR-SIPAT II | 149.12 | WRTS-I |  | 2019-08-29 | 10:40 | 2019-08-29 | 19:25 |  |  |  | 0 | 8.75 | 0 | 0 |  |  |  | For installation of PMU at Sipat (NTPC) end. Line charged from Raipur but tripped by receipt of DT from Sipat end due to over voltage protection operated at Sipat end. | WRPC | 100% | OMSU
[6 empty] | 2019-08-29 | 19:25 | 2019-08-29 | 21:33 |  |  |  | 0 | 0 | 2.1333 | 0 |  |  |  | For installation of PMU at Sipat (NTPC) end. Line charged from Raipur but tripped by receipt of DT from Sipat end due to over voltage protection operated at Sipat end AT 19:25 Hrs. Again charging attempt taken from Sipat and synchronised at raipur at 21:33 Hrs. |  |  | GOVC
|  | 400KV RAIPUR-SIPAT II Total | [10 empty] | 0
25 | WR1_L_025 | 400kV RAIPUR-SIPAT III | 162.04 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-SIPAT III Total
26 | WR1_L_026 | 765kV BILASPUR-SIPAT I | 21.507 | WRTS-I | [16 empty] | WRPC | 100%
765kV BILASPUR-SIPAT I Total
27 | WR1_L_027 | 765kV SEONI-BILASPUR I | 337.046 | WRTS-I | [16 empty] | WRPC | 100%
765kV SEONI-BILASPUR I Total
28 | WR1_L_028 | 765kV BILASPUR-SIPAT II | 22.216 | WRTS-I | [16 empty] | WRPC | 100%
765kV BILASPUR-SIPAT II Total
29 | WR1_L_029 | 765kV SEONI-BILASPUR II | 338.33 | WRTS-I | [16 empty] | WRPC | 100%
765kV SEONI-BILASPUR II Total
30 | WR1_L_030 | 765kV SEONI-WARDHA I | 267.894 | WRTS-I |  | 2019-08-02 | 11:40 | 2019-08-02 | 18:39 |  |  |  | 6.9833 | 0 | 0 | 0 |  |  |  | Emergency outage availed for attending oil leakage from radiator fin on spare Line Reactor at Wardha end ( Spare unit is in service in place of R phase). | WRPC | 99.06% | OSFT
[6 empty] | 2019-08-15 | 9:49 | 2019-08-17 | 7:16 |  |  |  | 0 | 0 | 0 | 45.45 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at seoni end . |  |  | LVRD
|  | 765kV SEONI-WARDHA I Total | [10 empty] | 6.9833
31 | WR1_L_031 | 765kV SEONI-WARDHA II | 260.763 | WRTS-I | [16 empty] | WRPC | 100%
765kV SEONI-WARDHA II Total
32 | WR1_L_032 | 400kV WARDHA-AKOLA I | 161.865 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-AKOLA I Total
33 | WR1_L_033 | 400kV WARDHA-AKOLA II | 161.865 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-AKOLA II Total
34 | WR1_L_034 | 400kV AURANGABAD (PG) -AKOLA I | 289.966 | WRTS-I | [16 empty] | WRPC | 100%
400kV AURANGABAD (PG) -AKOLA I Total
35 | WR1_L_035 | 400kV AURANGABAD (PG) -AKOLA II | 289.966 | WRTS-I | [16 empty] | WRPC | 100%
400kV AURANGABAD (PG) -AKOLA II Total
36 | WR1_L_036 | 400kV BHADRAVATI-PARLI I | 378.667 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHADRAVATI-PARLI I Total
37 | WR1_L_037 | 400kV PARLI(PG)-PARLI(MSETCL) I | 4.958 | WRTS-I | [16 empty] | WRPC | 100%
400kV PARLI(PG)-PARLI(MSETCL) I Total
38 | WR1_L_038 | 400kV PARLI(PG)-PARLI(MSETCL) II | 4.958 | WRTS-I | [16 empty] | WRPC | 100%
400kV PARLI(PG)-PARLI(MSETCL) II Total
39 | WR1_L_039 | 400kV KORBA-RAIPUR III | 212.83 | WRTS-I |  | 2019-08-27 | 8:57 | 2019-08-27 | 19:44 |  |  |  | 0 | 10.7833 | 0 | 0 |  |  |  | For Bay PM . Bay Belongs to NTPC | WRPC | 100% | OMSU
|  | 400kV KORBA-RAIPUR III Total | [10 empty] | 0
40 | WR1_L_040 | 400kV KORBA-RAIPUR IV | 212.83 | WRTS-I |  | 2019-08-29 | 17:07 | 2019-08-29 | 19:03 |  |  |  | 0 | 0 | 1.9333 | 0 |  |  |  | Line tripped on R-B Phase fault due to heavy rain and thunderstorm. Fault details from Raipur end - FD-171 km, FC-R-3.2 kA, B-2.84 kA. Fault details from Korba end - FD- 42.4 km, FC-R-9.97 kA. | WRPC | 100% | LNCC
|  | 400kV KORBA-RAIPUR IV Total | [10 empty] | 0
41 | WR1_L_041 | 400kV WARDHA-PARLI I | 336.939 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-PARLI I Total
42 | WR1_L_042 | 400kV WARDHA-PARLI II | 336.939 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-PARLI II Total
43 | WR1_L_043 | 400kV WARDHA-MAUDA II | 123.45 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-MAUDA II Total
44 | WR1_L_044 | 400kV KORBA-VANDANA | 14.768 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-VANDANA Total
45 | WR1_L_045 | 400kV VANDANA-BIRSINGHPUR | 211.874 | WRTS-I | [16 empty] | WRPC | 100%
400kV VANDANA-BIRSINGHPUR Total
46 | WR1_L_046 | 400kV RAIPUR-WARDHA I | 370.565 | WRTS-I |  | 2019-08-30 | 8:53 | 2019-08-30 | 19:53 |  |  |  | 11 | 0 | 0 | 0 |  |  |  | Line AMP works & 400KV Raipur Wardha ckt # 2 A/R in non auto mode required | WRPC | 98.52% | OSPT
|  | 400kV RAIPUR-WARDHA I Total | [10 empty] | 11
47 | WR1_L_047 | 400kV RAIPUR-WARDHA II | 370.565 | WRTS-I |  | 2019-08-31 | 8:54 | 2019-08-31 | 20:12 |  |  |  | 11.3 | 0 | 0 | 0 |  |  |  | For Line AMP works & 400KV Raipur Wardha ckt # 1 A/R in non auto mode required | WRPC | 98.48% | OSPT
|  | 400kV RAIPUR-WARDHA II Total | [10 empty] | 11.3
48 | WR1_L_048 | 400kV RAIPUR-DURG I | 21.43 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-DURG I Total
49 | WR1_L_049 | 400kV RAIPUR-DURG II | 21.43 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-DURG II Total
50 | WR1_L_050 | 400kV RAIGARH-KOTRA PS I | 6.288 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIGARH-KOTRA PS I Total
51 | WR1_L_051 | 400kV RAIGARH-KOTRA PS II | 6.288 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIGARH-KOTRA PS II Total
52 | WR1_L_052 | 765kV TAMNAR PS-KOTRA PS I | 47.986 | WRTS-I |  | 2019-08-06 | 9:14 | 2019-08-06 | 19:25 |  |  |  | 10.1833 | 0 | 0 | 0 |  |  |  | For Replacement of Broken Insulator & 765KV-RAIGARH-PS-TAMNAR-2 AR in Non auto mode required | WRPC | 98.63% | OSPT
|  | 765kV TAMNAR PS-KOTRA PS I Total | [10 empty] | 10.1833
53 | WR1_L_053 | 765kV TAMNAR PS-KOTRA PS II | 47.986 | WRTS-I |  | 2019-08-07 | 9:05 | 2019-08-07 | 16:53 |  |  |  | 7.8 | 0 | 0 | 0 |  |  |  | 'For Replacement of Broken Insulator & 765KV-RAIGARH-PS-TAMNAR-2 AR in Non auto mode required | WRPC | 98.95% | OSPT
|  | 765kV TAMNAR PS-KOTRA PS II Total | [10 empty] | 7.8
54 | WR1_L_054 | 765kV KOTRA PS-DURG PS I | 239.843 | WRTS-I | [16 empty] | WRPC | 100%
765kV KOTRA PS-DURG PS I Total
55 | WR1_L_055 | 765kV KOTRA PS-DURG PS II | 239.843 | WRTS-I | [16 empty] | WRPC | 100%
765kV KOTRA PS-DURG PS II Total
56 | WR1_L_056 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | 52.563 | WRTS-I | [16 empty] | WRPC | 100%
400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II Total
57 | WR1_L_057 | 400kV BHADRAVATI-DHARIWAL TPP II | 2.923 | WRTS-I | [16 empty] | WRPC | 100%
400kV BHADRAVATI-DHARIWAL TPP II Total
58 | WR1_L_058 | 400kV DHARIWAL TPP-PARLI II | 375.785 | WRTS-I | [16 empty] | WRPC | 100%
400kV DHARIWAL TPP-PARLI II Total
59 | WR1_L_059 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | 52.563 | WRTS-I |  | 2019-08-23 | 11:35 | 2019-08-23 | 11:58 |  |  |  | 0 | 0.38333 | 0 | 0 |  |  |  | Emergency outage availed by MSETCL for shifting of bus at Waluj end as their TBC was engaged. | WRPC | 100% | OMSU
|  | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I Total | [10 empty] | 0
60 | WR1_L_060 | 765KV DURG PS - D'JAIGARH | 357.62 | WRTS-I | [16 empty] | WRPC | 100%
765KV DURG PS - D'JAIGARH Total
61 | WR1_L_061 | 765kV WARDHA - AURANGABAD(PG) I | 347.577 | WRTS-I |  | 2019-08-01 | 0:00 | 2019-08-08 | 10:21 |  |  |  | 0 | 0 | 0 | 178.35 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Wardha at 03:18 hrs. | WRPC | 100% | LVRD
[6 empty] | 2019-08-13 | 21:16 | 2019-08-16 | 9:56 |  |  |  | 0 | 0 | 0 | 60.6667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at hrs. |  |  | LVRD
[6 empty] | 2019-08-16 | 23:25 | 2019-08-21 | 11:42 |  |  |  | 0 | 0 | 0 | 108.2833 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at hrs. |  |  | LVRD
[6 empty] | 2019-08-21 | 20:19 | 2019-08-29 | 10:30 |  |  |  | 0 | 0 | 0 | 182.1833 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at 21:22 hrs. |  |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) I Total | [10 empty] | 0
62 | WR1_L_062 | 765kV WARDHA - AURANGABAD(PG) II | 347.577 | WRTS-I |  | 2019-08-08 | 15:40 | 2019-08-13 | 9:39 |  |  |  | 0 | 0 | 0 | 113.9833 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Wardha at 16:03 hrs. | WRPC | 99.49% | LVRD
[6 empty] | 2019-08-23 | 13:29 | 2019-08-23 | 17:15 |  |  |  | 3.7667 | 0 | 0 | 0 |  |  |  | Emergency outage availed for attending 03 nos.opened jumpers at Loc.No. 335. Readyness mail sent to WRLDC at 17:15 hrs |  |  | OSFT
[6 empty] | 2019-08-23 | 17:15 | 2019-08-23 | 19:24 |  |  |  | 0 | 0 | 0 | 2.15 |  |  |  | Line charged as per WRLDC instructions |  |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) II Total | [10 empty] | 3.7667
63 | WR1_L_063 | 765kV DURG PS -WARDHA_1 | 369.107 | WRTS-I |  | 2019-08-09 | 16:09 | 2019-08-20 | 12:07 |  |  |  | 0 | 0 | 0 | 259.9667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 16:21 hrs. | WRPC | 100% | LVRD
|  | 765kV DURG PS -WARDHA_1 Total | [10 empty] | 0
64 | WR1_L_064 | 765kV DURG PS -WARDHA_2 | 369.107 | WRTS-I |  | 2019-08-01 | 0:00 | 2019-08-09 | 8:18 |  |  |  | 0 | 0 | 0 | 200.3 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 18:32 hrs. | WRPC | 100% | LVRD
[6 empty] | 2019-08-21 | 16:36 | 2019-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 247.4 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 16:40 Hrs. |  |  | LVRD
|  | 765kV DURG PS -WARDHA_2 Total | [10 empty] | 0
65 | WR1_L_065 | 400Kv PARLI-PUNE(GIS)_1 | 9.57 | WRTS-I | [16 empty] | WRPC | 100%
400Kv PARLI-PUNE(GIS)_1 Total
66 | WR1_L_066 | 400Kv PARLI-PUNE(GIS)_2 | 9.57 | WRTS-I | [16 empty] | WRPC | 100%
400Kv PARLI-PUNE(GIS)_2 Total
67 | WR1_L_067 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | 9.978 | WRTS-I |  | 2019-08-20 | 16:34 | 2019-08-20 | 19:57 |  |  |  | 3.3833 | 0 | 0 | 0 |  |  |  | Emergrncy outage is availed for rectifing OPGW suspension clamps at Tower NO: 16. | WRPC | 99.03% | OSFT
[6 empty] | 2019-08-25 | 9:46 | 2019-08-25 | 13:37 |  |  |  | 3.85 | 0 | 0 | 0 |  |  |  | Outage availed for line AMP works & Relay Testing. |  |  | OSPT
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 Total | [10 empty] | 7.2333
68 | WR1_L_068 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | 9.978 | WRTS-I |  | 2019-08-20 | 16:47 | 2019-08-20 | 19:59 |  |  |  | 3.2 | 0 | 0 | 0 |  |  |  | Emergrncy outage is availed for rectifing OPGW suspension clamps at Tower NO: 16. | WRPC | 99.57% | OSFT
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 Total | [10 empty] | 3.2
69 | WR1_L_069 | 765kV PUNE(GIS)-SOLAPUR | 269.842 | WRTS-I |  | 2019-08-01 | 0:00 | 2019-08-05 | 9:05 |  |  |  | 0 | 0 | 0 | 105.0833 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR's converted as BR's at 12:22 hrs at Pune-GIS & at 12:42 hrs at Solapur end. | WRPC | 100% | LVRD
[6 empty] | 2019-08-05 | 20:58 | 2019-08-13 | 9:32 |  |  |  | 0 | 0 | 0 | 180.5667 |  |  |  | Line is H/T as per WRLDC instructions for Voltage Regulation and SLRs converted as BR's at 21:10 hrs at Pune-GIS & at 21:31 hrs at Solapur end for V/R. |  |  | LVRD
[6 empty] | 2019-08-13 | 18:36 | 2019-08-16 | 13:03 |  |  |  | 0 | 0 | 0 | 66.45 |  |  |  | Line is H/T as per WRLDC instructions for Voltage Regulation and SLRs converted as BR's at 20:26 hrs at Pune-GIS & for V/R. BR's HT at 08:48hrs@Pune & at 08:50hrs@Solapur end. |  |  | LVRD
[6 empty] | 2019-08-20 | 17:01 | 2019-08-20 | 20:07 |  |  |  | 0 | 0 | 0 | 3.1 |  |  |  | To facilitate emergency outage of 400KV Pune-Pune-1&2 and control loading on 400KV Pune-Pune-3&4. Ki ndly change the reason as mentioned above category changed to LPRD |  |  | LPRD
[6 empty] | 2019-08-20 | 20:07 | 2019-08-26 | 10:09 |  |  |  | 0 | 0 | 0 | 134.0333 |  |  |  | Line kept open as per WRLDC instructions for Voltage Regulation and . SLRs converted as BRs at both ends for V/R. SLR at Pune GIS is converted as B/R at 20:26hrs. SLR at Solapur is converted as B/R at 20:55hrs. |  |  | LVRD
[6 empty] | 2019-08-27 | 1:20 | 2019-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 118.6667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Pune GIS end at 02:28 hrs and Solapur end at 01:36 hrs. |  |  | LVRD
|  | 765kV PUNE(GIS)-SOLAPUR Total | [10 empty] | 0
70 | WR1_L_070 | 765kV WARDHA - AURANGABAD(PG) III | 355 | WRTS-I |  | 2019-08-01 | 0:00 | 2019-08-18 | 6:34 |  |  |  | 0 | 0 | 0 | 414.5667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Wardha at 16:11 hrs. | WRPC | 100% | LVRD
[6 empty] | 2019-08-18 | 14:59 | 2019-08-23 | 12:25 |  |  |  | 0 | 0 | 0 | 117.4333 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Wardha at 15:19 hrs. |  |  | LVRD
[6 empty] | 2019-08-28 | 17:17 | 2019-08-28 | 20:01 |  |  |  | 0 | 0 | 2.7333 | 0 |  |  |  | Line tripped on B Phase Buccolz at Aurangabad due to ingress of moisture due to heavy rains . As buccolz is exposed directly to rains inspite of POWERGRID best efforts due to heavy rains moisture ingressed in Buccolz leading to maloperation of buccolz.Charging clerance given to WRLDC at 2001 hours. Newspaper cutting attached |  |  | LNCC
[6 empty] | 2019-08-28 | 20:01 | 2019-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 75.9833 |  |  |  | Line kept open by WRLDC on high voltage and to convert LR as BR at Wardha end. |  |  | LVRD
|  | 765kV WARDHA - AURANGABAD(PG) III Total | [10 empty] | 0
71 | WR1_L_071 | 765kV WARDHA - AURANGABAD(PG) IV | 355 | WRTS-I | [16 empty] | WRPC | 100%
765kV WARDHA - AURANGABAD(PG) IV Total
72 | WR1_L_072 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | 11.2 | WRTS-I | [16 empty] | WRPC | 100%
400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 Total
73 | WR1_L_073 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | 11.2 | WRTS-I | [16 empty] | WRPC | 100%
400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 Total
74 | WR1_L_074 | 765kV DURG PS- CHAMPA_1 | 149.15 | WRTS-I | [16 empty] | WRPC | 100%
765kV DURG PS- CHAMPA_1 Total
75 | WR1_L_075 | 765kV CHAMPA- KOTRA PS | 96.33 | WRTS-I | [16 empty] | WRPC | 100%
765kV CHAMPA- KOTRA PS Total
76 | WR1_L_076 | 765kV AURANGABAD(PG)-SOLAPUR I | 279.57 | WRTS-I | [16 empty] | WRPC | 100%
765kV AURANGABAD(PG)-SOLAPUR I Total
77 | WR1_L_077 | 765kV AURANGABAD(PG)-SOLAPUR II | 279.57 | WRTS-I |  | 2019-08-13 | 18:52 | 2019-08-13 | 19:24 |  |  |  | 0.53333 | 0 | 0 | 0 |  |  |  | Line is tripped due to failure of 71152 Tie CB at Solapur end. Readiness for charging of line is conveyed to WRLDC by email at 19:24hrs. | WRPC | 99.93% | SEFT
[6 empty] | 2019-08-13 | 19:24 | 2019-08-13 | 22:39 |  |  |  | 0 | 0 | 0 | 3.25 |  |  |  | Line is kept out under voltage regulation after sending readiness mail to WRLDC at 19:24 hrs. |  |  | LVRD
|  | 765kV AURANGABAD(PG)-SOLAPUR II Total | [10 empty] | 0.53333
78 | WR1_L_078 | 220kV KORBA(EAST)-BUDDHIPADAR III | 184 | WRTS-I | [16 empty] | WRPC | 100%
220kV KORBA(EAST)-BUDDHIPADAR III Total
79 | WR1_L_079 | 400kV RAIPUR-RAIGARH I | 217.02 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-RAIGARH I Total
80 | WR1_L_080 | 400kV RAIGARH-ROURKELA II | 212.46 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIGARH-ROURKELA II Total
81 | WR1_L_081 | 400kV RAIGARH-IBEUL I | 94.43 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIGARH-IBEUL I Total
82 | WR1_L_082 | 400kV IBEUL-JHARSUGUDA I | 20.03 | WRTS-I | [16 empty] | WRPC | 100%
400kV IBEUL-JHARSUGUDA I Total
83 | WR1_L_083 | 400kV JHARSUGUDA-ROURKELA I | 142.448 | WRTS-I | [16 empty] | WRPC | 100%
400kV JHARSUGUDA-ROURKELA I Total
84 | WR1_L_084 | 400kV RANCHI-SIPAT I | 405.772 | WRTS-I |  | 2019-08-16 | 9:27 | 2019-08-16 | 21:21 |  |  |  | 0 | 0 | 11.9 | 0 |  |  |  | Outage availed by ER for attending Low clearance issue of 400kV New Ranchi - Patratu (D/C) crossing over the 400kV Ranchi - Sipat D/C between location no. 5/0 and 6/0 due to theft of conductor hardware by miscreants. | WRPC | 100% | LMAC
[6 empty] | 2019-08-26 | 12:21 | 2019-08-26 | 18:44 |  |  |  | 0 | 6.3833 | 0 | 0 |  |  |  | For installation of PMU at Sipat(NTPC) end |  |  | OMSU
|  | 400kV RANCHI-SIPAT I Total | [10 empty] | 0
85 | WR1_L_085 | 400kV RANCHI-SIPAT II | 405.772 | WRTS-I |  | 2019-08-16 | 9:37 | 2019-08-16 | 20:50 |  |  |  | 0 | 0 | 11.2167 | 0 |  |  |  | Outage availed by ER for attending Low clearance issue of 400kV New Ranchi - Patratu (D/C) crossing over the 400kV Ranchi - Sipat D/C between location no. 5/0 and 6/0 due to theft of conductor hardware by miscreants. | WRPC | 100% | LMAC
|  | 400kV RANCHI-SIPAT II Total | [10 empty] | 0
86 | WR1_L_086 | 400kV RAIPUR-KSK III | 134.74 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-KSK III Total
87 | WR1_L_087 | 400kV KSK-RKKML III | 82.248 | WRTS-I | [16 empty] | WRPC | 100%
400kV KSK-RKKML III Total
88 | WR1_L_088 | 400kV RKKML-RAIGARH III | 3.896 | WRTS-I | [16 empty] | WRPC | 100%
400kV RKKML-RAIGARH III Total
89 | WR1_L_089 | 400kV RAIPUR-KSK IV | 161.82 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-KSK IV Total
90 | WR1_L_090 | 400kV KSK-RAIGARH IV | 113.389 | WRTS-I | [16 empty] | WRPC | 100%
400kV KSK-RAIGARH IV Total
91 | WR1_L_091 | 400kV RAIGARH-JHARSUGUDA III | 110.98 | WRTS-I |  | 2019-08-24 | 10:47 | 2019-08-24 | 15:36 |  |  |  | 4.8167 | 0 | 0 | 0 |  |  |  | Emergency outage availed by ER-II/Odisha/ Sundargarh for attending 03 nos of Porcelain insulators broken at bottom phase (Y Phase) at location 781. | WRPC | 99.35% | OSFT
|  | 400kV RAIGARH-JHARSUGUDA III Total | [10 empty] | 4.8167
92 | WR1_L_092 | 400kV JHARSUGUDA-ROURKELA III | 143.06 | WRTS-I | [16 empty] | WRPC | 100%
400kV JHARSUGUDA-ROURKELA III Total
91 | WR1_L_093 | 400kV RAIGARH-JHARSUGUDA IV | 145.5 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIGARH-SUNDERGARH IV Total
94 | WR1_L_094 | 400kV STERLITE-ROURKELA IV | 104.28 | WRTS-I | [16 empty] | WRPC | 100%
400kV STERLITE-ROURKELA IV Total
95 | WR1_L_095 | 765kV D'JAIGARH-BILASPUR | 90 | WRTS-I | [16 empty] | WRPC | 100%
765kV D'JAIGARH-BILASPUR Total
96 | WR1_L_096 | 765kV D'JAIGARH-RANCHI I | 303 | WRTS-I |  | 2019-08-20 | 13:28 | 2019-08-20 | 18:50 |  |  |  | 5.3667 | 0 | 0 | 0 |  |  |  | Outage availed for rectification of damage conductor by Tamnar-TLM. | WRPC | 99.28% | OSPT
|  | 765kV D'JAIGARH-RANCHI I Total | [10 empty] | 5.3667
97 | WR1_L_097 | 765kV D'JAIGARH- JHARSUGUDA I | 149.789 | WRTS-I | [16 empty] | WRPC | 100%
765kV D'JAIGARH- JHARSUGUDA I Total
98 | WR1_L_098 | 765kV D'JAIGARH- JHARSUGUDA II | 149.789 | WRTS-I | [16 empty] | WRPC | 100%
765kV D'JAIGARH- JHARSUGUDA II Total
99 | WR1_L_099 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I | 39.383 | WRTS-I | [16 empty] | WRPC | 100%
400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I Total
100 | WR1_L_100 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II | 39.383 | WRTS-I | [16 empty] | WRPC | 100%
400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II Total
| WR1_L_101 | 400kV KOLHAPUR (GIS)-MAPUSA I |  |  |  | 2019-08-05 | 2:51 | 2019-08-05 | 6:37 |  |  |  | 0 | 0 | 0 | 3.7667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation | WRPC | 100% | LVRD
[6 empty] | 2019-08-25 | 13:23 | 2019-08-25 | 13:23 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | A/R Successful at both ends on B ph to E fault. At Kolapur FD=94.7km, FC=1.126kA and at Mapusa end FD=29.32km, FC=2.42kA |  |  | LART
|  | 400kV KOLHAPUR (GIS)-MAPUSA I Total | [10 empty] | 0
102 | WR1_L_102 | 400kV KOLHAPUR (GIS)-MAPUSA II | 156.039 | WRTS-I |  | 2019-08-06 | 4:09 | 2019-08-06 | 6:24 |  |  |  | 0 | 0 | 0 | 2.25 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation. | WRPC | 100% | LVRD
[6 empty] | 2019-08-25 | 13:23 | 2019-08-26 | 13:09 |  |  |  | 0 | 0 | 23.7667 | 0 |  |  |  | Line tripped due to vegetaive deposition in chowkal region(Photographs attached). It may please be noted that Chowkal village in Amboli, Maharashtra is situated at an elelvation of 870mtrs above grouund level. The tower is located at hilltop which is covered in cloud dense fog. The area suffers from vegetative pollution moss deposition. |  |  | LNCC
|  | 400kV KOLHAPUR (GIS)-MAPUSA II Total | [10 empty] | 0
103 | WR1_L_103 | 400kV WARDHA-MAUDA I | 123.45 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-MAUDA I Total
104 | WR1_L_104 | 765kV D'JAIGARH-RANCHI II | 354 | WRTS-I | [16 empty] | WRPC | 100%
765kV D'JAIGARH-RANCHI II Total
105 | WR1_L_105 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 | 14.373 | WRTS-I |  | 2019-08-13 | 12:48 | 2019-08-13 | 17:55 |  |  |  | 5.1167 | 0 | 0 | 0 |  |  |  | For line AMP works & Relay Testing, 400KV-PUNE-GIS-PUNE-PG-1, 2 & 4 AR kept in non auto mode. | WRPC | 99.31% | OSPT
|  | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 Total | [10 empty] | 5.1167
106 | WR1_L_106 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 | 14.373 | WRTS-I | [16 empty] | WRPC | 100%
400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 Total
107 | WR1_L_107 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I | 14.387 | WRTS-I | [16 empty] | WRPC | 100%
400Kv AURANGABAD(MSETCL)-PUNE(GIS) I Total
108 | WR1_L_108 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II | 14.387 | WRTS-I | [16 empty] | WRPC | 100%
400Kv AURANGABAD(MSETCL)-PUNE(GIS) II Total
109 | WR1_L_109 | 400kV RAIPUR-RAIGARH II | 217.02 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-RAIGARH II Total
110 | WR1_L_110 | 400kV LARA(NTPC)-KOTRA PS I | 17.999 | WRTS-I |  | 2019-08-21 | 9:34 | 2019-08-21 | 22:10 |  |  |  | 0 | 12.6 | 0 | 0 |  |  |  | Outage availed by Lara NTPC for Isolator stem replacement. Bay Belongs to NTPC | WRPC | 100% | OMSU
|  | 400kV LARA(NTPC)-KOTRA PS I Total | [10 empty] | 0
111 | WR1_L_111 | 400kV LARA(NTPC)-KOTRA PS II | 17.999 | WRTS-I | [16 empty] | WRPC | 100%
400kV LARA(NTPC)-KOTRA PS II Total
112 | WR1_L_112 | 400kV KORBA-BIRSINGHPUR_2 | 226.642 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-BIRSINGHPUR_2 Total
113 | WR1_T_001 | ICT1_400/220kv_RAIPUR | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_RAIPUR Total
114 | WR1_T_002 | ICT2_400/220kv_RAIPUR | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_RAIPUR Total
115 | WR1_T_003 | ICT1_400/220kv_MAPUSA | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_MAPUSA Total
116 | WR1_T_004 | ICT2_400/220kv_MAPUSA | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_MAPUSA Total
117 | WR1_T_005 | ICT1_400/220kv_BAHATAPARA | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_BAHATAPARA Total
118 | WR1_T_006 | ICT1_400/220kv_RAIGARH | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_RAIGARH Total
119 | WR1_T_007 | ICT2_400/220kv_RAIGARH | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_RAIGARH Total
120 | WR1_T_008 | ICT1_765/400kv_SEONI | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_SEONI Total
121 | WR1_T_009 | ICT2_765/400kv_SEONI | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_SEONI Total
122 | WR1_T_010 | ICT3_765/400kv_SEONI | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_765/400kv_SEONI Total
123 | WR1_T_011 | ICT1_400/220kv_SEONI | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_SEONI Total
124 | WR1_T_012 | ICT1_765/400kv_WARDHA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_WARDHA Total
125 | WR1_T_013 | ICT2_765/400kv_WARDHA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_WARDHA Total
126 | WR1_T_014 | ICT3_765/400kv_WARDHA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_765/400kv_WARDHA Total
127 | WR1_T_015 | ICT1_765/400kv_BILASPUR | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_BILASPUR Total
128 | WR1_T_016 | ICT2_765/400kv_BILASPUR | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_BILASPUR Total
129 | WR1_T_017 | ICT2_400/220kv_BAHATAPARA | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_BAHATAPARA Total
130 | WR1_T_018 | ICT2_400/220kv_SEONI | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_SEONI Total
131 | WR1_T_019 | ICT3_400/220kv_RAIPUR | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_400/220kv_RAIPUR Total
132 | WR1_T_020 | ICT1_400/220kv_WARDHA | 315 | WRTS-I |  | 2019-08-13 | 10:26 | 2019-08-13 | 17:55 |  |  |  | 7.4833 | 0 | 0 | 0 |  |  |  | For AMP works. | WRPC | 98.99% | OSPT
|  | ICT1_400/220kv_WARDHA Total | [10 empty] | 7.4833
133 | WR1_T_021 | ICT2_400/220kv_WARDHA | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_WARDHA Total
134 | WR1_T_022 | ICT3_400/220kv_SOLAPUR | 500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_400/220kv_SOLAPUR Total
135 | WR1_T_023 | ICT1_400/220kv_SOLAPUR | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_SOLAPUR Total
136 | WR1_T_024 | ICT2_400/220kv_SOLAPUR | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_SOLAPUR Total
137 | WR1_T_025 | ICT1_400/220kv_PUNE | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/220kv_PUNE Total
138 | WR1_T_026 | ICT2_400/220kv_PUNE | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/220kv_PUNE Total
139 | WR1_T_027 | ICT3_400/220kv_PUNE | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_400/220kv_PUNE Total
140 | WR1_T_028 | ICT3_765/400kv_BILASPUR | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_765/400kv_BILASPUR Total
141 | WR1_T_029 | ICT1_765/400kv_KOTRA PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_KOTRA PS Total
142 | WR1_T_030 | ICT2_765/400kv_KOTRA PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_KOTRA PS Total
143 | WR1_T_031 | ICT4_765/400kv_KOTRA PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT4_765/400kv_KOTRA PS Total
144 | WR1_T_032 | ICT3_400/220kv_MAPUSA | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_400/220kv_MAPUSA Total
145 | WR1_T_033 | ICT1_765/400kv_TAMNAR PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_TAMNAR PS Total
146 | WR1_T_034 | ICT2_765/400kv_TAMNAR PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_TAMNAR PS Total
147 | WR1_T_035 | ICT1_765/400kv_DURG PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_DURG PS Total
148 | WR1_T_036 | ICT1_765/400kv_SOLAPUR | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_SOLAPUR Total
149 | WR1_T_037 | ICT2_765/400kv_SOLAPUR | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_SOLAPUR Total
150 | WR1_T_038 | ICT1_400/200kv_AURANGABAD | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/200kv_AURANGABAD Total
151 | WR1_T_039 | ICT2_400/200kv_AURANGABAD | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_400/200kv_AURANGABAD Total
152 | WR1_T_040 | ICT2_765/400kv_AURANGABAD | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_AURANGABAD Total
153 | WR1_T_041 | ICT3_765/400kv_TAMNAR PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_765/400kv_TAMNAR PS Total
154 | WR1_T_042 | ICT3_765/400kv_KOTRA PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_765/400kv_KOTRA PS Total
155 | WR1_T_043 | ICT1_765/400kv_AURANGABAD | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_AURANGABAD Total
156 | WR1_T_044 | ICT2_765/400kv_D'JAIGARH | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_D'JAIGARH Total
157 | WR1_T_045 | ICT1_765/400kv_D'JAIGARH | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_D'JAIGARH Total
158 | WR1_T_046 | ICT1_400/200kv_BHADRAWATI | 315 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_400/200kv_BHADRAWATI Total
159 | WR1_T_047 | ICT1_765/400kv_PUNE(GIS) | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_PUNE(GIS) Total
160 | WR1_T_048 | ICT2_765/400kv_PUNE(GIS) | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_PUNE(GIS) Total
161 | WR1_T_049 | ICT1_765/400kv_CHAMPA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_CHAMPA Total
162 | WR1_T_050 | ICT2_765/400kv_CHAMPA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_CHAMPA Total
163 | WR1_R_001 | BUS REACTOR_400kV_63MVAR_RAIGARH | 63 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_63MVAR_RAIGARH Total
164 | WR1_R_002 | BUS REACTOR_765kV_240MVAR_SEONI | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_SEONI Total
165 | WR1_R_003 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | 50 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_KORBA 3_RAIPUR Total
166 | WR1_R_004 | BUS REACTOR_400kV_50MVAR_WARDHA | 50 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_50MVAR_WARDHA Total
167 | WR1_R_005 | BUS REACTOR_400kV_63MVAR_SOLAPUR | 63 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_63MVAR_SOLAPUR Total
168 | WR1_R_006 | BUS REACTOR_400kV_63MVAR_PARLI | 63 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_63MVAR_PARLI Total
169 | WR1_R_007 | BUS REACTOR_400kV_50MVAR_PUNE | 50 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_50MVAR_PUNE Total
170 | WR1_R_008 | BUS REACTOR_765kV_240MVAR_WARDHA | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_WARDHA Total
171 | WR1_R_009 | BUS REACTOR_765kV_240MVAR_BILASPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_BILASPUR Total
172 | WR1_R_010 | SWITCHABLE LR_765kV_BINA_SEONI | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_BINA_SEONI Total
173 | WR1_R_011 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_SEONI 1_BILASPUR Total
174 | WR1_R_012 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_SEONI 2_BILASPUR Total
175 | WR1_R_013 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_D'GARH_BILASPUR Total
176 | WR1_R_014 | BUS REACTOR_765kV_240MVAR_KOTRA PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_KOTRA PS Total
177 | WR1_R_015 | BUS REACTOR_400kV_80MVAR_KOTRA PS | 80 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_80MVAR_KOTRA PS Total
178 | WR1_R_016 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_DURG 1_KOTRA PS Total
179 | WR1_R_017 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | 50 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_50MVAR_BHADRAWATI Total
180 | WR1_R_018 | BUS REACTOR_400kV_80MVAR_RAIPUR | 80 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_80MVAR_RAIPUR Total
181 | WR1_R_019 | BUS REACTOR_400kV_50MVAR_MAPUSA | 50 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_50MVAR_MAPUSA Total
182 | WR1_R_020 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | 80 | WRTS-I |  | 2019-08-21 | 11:22 | 2019-08-21 | 18:12 |  |  |  | 0 | 0 | 0 | 6.8333 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation. | WRPC | 100% | SVRD
[6 empty] | 2019-08-26 | 9:46 | 2019-08-26 | 18:09 |  |  |  | 0 | 0 | 0 | 8.3833 |  |  |  | Bus Reactor hand tripped as per WRLDC instructions for voltage regulation. |  |  | SVRD
|  | BUS REACTOR_400kV_80MVAR_KOLHAPUR Total | [10 empty] | 0
183 | WR1_R_021 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_DURG 2_KOTRA PS Total
184 | WR1_R_022 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_TAMNAR PS Total
185 | WR1_R_023 | BUS REACTOR_765kV_240MVAR_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_DURG PS Total
186 | WR1_R_024 | BUS REACTOR_765kV_240MVAR_SOLAPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_SOLAPUR Total
187 | WR1_R_027 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_A'BAD 1_WARDHA Total
188 | WR1_R_028 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_A'BAD 2_WARDHA Total
190 | WR1_R_029 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR Total
191 | WR1_R_030 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_WARDHA 2_SEONI Total
192 | WR1_R_031 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR 1_765kV_330MVAR_D'JAIGARH Total
193 | WR1_R_032 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR 2_765kV_330MVAR_D'JAIGARH Total
194 | WR1_R_033 | BUS REACTOR_765kV_240MVAR_AURANGABAD | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_AURANGABAD Total
195 | WR1_R_034 | BUS REACTOR_400kV_125MVAR_AURANGABAD | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_AURANGABAD Total
196 | WR1_R_035 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_CHAMPA 1_DURG PS Total
197 | WR1_R_036 | BUS REACTOR_400kV_125MVAR_BHATAPARA | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_BHATAPARA Total
198 | WR1_R_037 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_WARDHA 1_SEONI Total
199 | WR1_R_038 | BUS REACTOR_400kV_125MVAR_RAIGARH | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_RAIGARH Total
200 | WR1_R_039 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | 240 | WRTS-I |  | 2019-08-21 | 12:50 | 2019-08-22 | 13:36 |  |  |  | 0 | 0 | 0 | 24.7667 |  |  |  | For Construction works of 765kV Aurangabad-Pune | WRPC | 100% | SCSD
|  | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD Total | [10 empty] | 0
201 | WR1_R_040 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_PADGHE2_AURANGABAD Total
202 | WR1_R_041 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_WARDHA 1_DURG PS Total
203 | WR1_R_042 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_WARDHA 2_DURG PS Total
204 | WR1_R_043 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | 80 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_BOISAR2_AURANGABAD Total
205 | WR1_R_044 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | 80 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_BOISAR1_AURANGABAD Total
206 | WR1_R_045 | BUS REACTOR_400kV_125MVAR_RAIPUR | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_RAIPUR Total
207 | WR1_R_046 | BUS REACTOR_765kV_330MVAR_WARDHA | 330 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_330MVAR_WARDHA Total
208 | WR1_R_047 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | 80 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_KARAD_SOLAPUR Total
209 | WR1_R_048 | BUS REACTOR_400kV_125MVAR_SEONI | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_SEONI Total
210 | WR1_R_049 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | 50 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE Total
211 | WR1_R_050 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | 50 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE Total
212 | WR1_R_051 | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE | 50 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE Total
213 | WR1_R_052 | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE | 50 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE Total
214 | WR1_R_053 | BUS REACTOR_400kV_125MVAR_PARLI | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_PARLI Total
215 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | 240 | WRTS-I |  | 2019-08-20 | 10:55 | 2019-08-22 | 13:09 |  |  |  | 0 | 0 | 0 | 50.2333 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation. | WRPC | 100% | SVRD
[6 empty] | 2019-08-25 | 11:28 | 2019-08-25 | 20:00 |  |  |  | 0 | 0 | 0 | 8.5333 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation. |  |  | SVRD
[6 empty] | 2019-08-27 | 11:41 | 2019-08-28 | 21:44 |  |  |  | 0 | 0 | 0 | 34.05 |  |  |  | Bus Reactor is hand tripped as per WRLDC instructions for voltage regulation. |  |  | SVRD
|  | BUS REACTOR_765kV_240MVAR_PUNE(GIS) Total | [10 empty] | 0
216 | WR1_R_055 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | 240 | WRTS-I |  | 2019-08-03 | 10:53 | 2019-08-04 | 10:14 |  |  |  | 0 | 0 | 0 | 23.35 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation | WRPC | 100% | SVRD
[6 empty] | 2019-08-10 | 9:49 | 2019-08-12 | 23:14 |  |  |  | 0 | 0 | 0 | 61.4167 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation. |  |  | SVRD
[6 empty] | 2019-08-14 | 10:12 | 2019-08-14 | 20:13 |  |  |  | 0 | 0 | 0 | 10.0167 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation. |  |  | SVRD
[6 empty] | 2019-08-21 | 10:04 | 2019-08-21 | 18:52 |  |  |  | 0 | 0 | 0 | 8.8 |  |  |  | BR H/T as per WRLDC instructions for Voltage Regulation. |  |  | SVRD
[6 empty] | 2019-08-22 | 11:10 | 2019-08-22 | 17:23 |  |  |  | 0 | 0 | 0 | 6.2167 |  |  |  | LR H/T as per WRLDC instructions for Voltage Regulation. |  |  | SVRD
[6 empty] | 2019-08-27 | 9:56 | 2019-08-27 | 20:25 |  |  |  | 0 | 0 | 0 | 10.4833 |  |  |  | SLR is H/T as per WRLDC instruction for V/R |  |  | SVRD
|  | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) Total | [10 empty] | 0
217 | WR1_R_056 | BUS REACTOR_400kV_80MVAR_DHULE | 80 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_80MVAR_DHULE Total
218 | WR1_R_057 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_A'BAD 3_WARDHA Total
219 | WR1_R_058 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_A'BAD 4_WARDHA Total
220 | WR1_R_059 | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH Total
221 | WR1_R_060 | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH Total
222 | WR1_R_061 | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR | 240 | WRTS-I |  | 2019-08-29 | 9:39 | 2019-08-29 | 17:39 |  |  |  | 8 | 0 | 0 | 0 |  |  |  | For Reactor AMP works. | WRPC | 98.92% | OSPT
|  | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR Total | [10 empty] | 8
223 | WR1_R_062 | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR Total
224 | WR1_R_063 | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH Total
225 | WR1_R_064 | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH Total
226 | WR1_R_065 | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) Total
227 | WR1_R_066 | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD | 80 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_WARDHA1_AURANGABAD Total
228 | WR1_R_067 | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD | 80 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_WARDHA2_AURANGABAD Total
229 | WR1_R_068 | BUS REACTOR_765kV_240MVAR_CHAMPA | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_CHAMPA Total
230 | WR1_R_069 | BUS REACTOR_400kV_80MVAR_CHAMPA | 80 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_80MVAR_CHAMPA Total
231 | WR1_R_070 | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH Total
232 | WR1_R_071 | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH Total
233 | WR1_P_001 | HVDC_POLE1_BHADRAWATI | 500 | WRTS-I | [16 empty] | WRPC | 100%
HVDC_POLE1_BHADRAWATI Total
234 | WR1_P_002 | HVDC_POLE2_BHADRAWATI | 500 | WRTS-I | [16 empty] | WRPC | 100%
HVDC_POLE2_BHADRAWATI Total
235 | WR1_T_051 | ICT4_765/400kv_CHAMPA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT4_765/400kv_CHAMPA Total
236 | WR1_T_052 | ICT5_765/400kv_CHAMPA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT5_765/400kv_CHAMPA Total
237 | WR1_L_113 | 400kV RAIGARH-JHARSUGUDA I | 110.98 | WRTS-I |  | 2019-08-18 | 2:21 | 2019-08-18 | 2:39 |  |  |  | 0.3 | 0 | 0 | 0 |  |  |  | Line tripped on B-G fault at 02:21 Hrs at Raigarh end due to rain, lightning and thunderstorm. Fault details from Raigarh: B-G 7.396KA,47.88KM from Sundergarh . 5.054KA, 56.52KM from Raigarh end. News paper cutting attached. Line was charged in 0:18 hours withouta nay maintainnece works | WRPC | 99.96% | LEFT
[6 empty] | 2019-08-18 | 6:18 | 2019-08-18 | 6:18 |  |  |  | 0 | 0 | 0 | 0 |  |  |  | Line AR successful, B-E, F.C-9.873, 13.473KM(M1), 10.553kM(M2) |  |  | LART
|  | 400kV RAIGARH-JHARSUGUDA I Total | [10 empty] | 0.3
238 | WR1_L_114 | 400kV RAIPUR-RAIGARH III | 217.02 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-RAIGARH III Total
239 | WR1_L_115 | 765kV DURG PS- CHAMPA_2 | 149.15 | WRTS-I | [16 empty] | WRPC | 100%
765kV DURG PS- CHAMPA_2 Total
240 | WR1_L_116 | 765kV DURG PS -WARDHA_3 | 357.27 | WRTS-I |  | 2019-08-01 | 0:00 | 2019-08-03 | 9:17 |  |  |  | 0 | 0 | 0 | 57.2833 |  |  |  | Line kept uncharged due to system constraint as per WRLDC instruction. | WRPC | 99.41% | LVRD
[6 empty] | 2019-08-05 | 16:51 | 2019-08-05 | 21:16 |  |  |  | 4.4167 | 0 | 0 | 0 |  |  |  | Line is tripped due to failure of "R-ph line reactor LA" at Wardha end. Line reactor at Durg end is converted as Bus reactor at 17:34 hrs with WRLDC code 334/119. Readiness mail is sent at 21:16hrs. |  |  | SEFT
[6 empty] | 2019-08-05 | 21:16 | 2019-08-17 | 6:19 |  |  |  | 0 | 0 | 0 | 273.05 |  |  |  | Line is kept out under voltage regulation after sending readiness mail to WRLDC at 21:16 hrs. |  |  | LVRD
[6 empty] | 2019-08-28 | 14:17 | 2019-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 81.7167 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at Hrs. |  |  | LVRD
|  | 765kV DURG PS -WARDHA_3 Total | [10 empty] | 4.4167
241 | WR1_L_117 | 765kV DURG PS -WARDHA_4 | 357.27 | WRTS-I |  | 2019-08-03 | 13:36 | 2019-08-05 | 17:59 |  |  |  | 0 | 0 | 0 | 52.3833 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 13:41 hrs. | WRPC | 100% | LVRD
[6 empty] | 2019-08-17 | 22:22 | 2019-08-28 | 8:48 |  |  |  | 0 | 0 | 0 | 250.4333 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Durg end at 22:37 Hrs. |  |  | LVRD
|  | 765kV DURG PS -WARDHA_4 Total | [10 empty] | 0
242 | WR1_T_052 | ICT6_765/400kv_CHAMPA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT6_765/400kv_CHAMPA Total
243 | WR1_T_118 | 765KV D'JAIGARH- CHAMPA | 56.48 | WRTS-I | [16 empty] | WRPC | 100%
765KV D'JAIGARH- CHAMPA TOTAL
244 | WR1_T_053 | ICT3_765/400kv_CHAMPA | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT3_765/400kv_CHAMPA Total
245 | WR1_L_118 | 400kV KORBA-BIRSINGHPUR_1 | 226.642 | WRTS-I | [16 empty] | WRPC | 100%
400kV KORBA-BIRSINGHPUR_2 Total
246 | WR1_T_053 | ICT2_765/400kv_DURG PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_DURG PS Total
247 | WR1_T_054 | ICT4_765/400kv_TAMNAR PS | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT4_765/400kv_TAMNAR PS Total
248 | WR1_R_072 | SWITCHABLE LR_765kV_WARDHA 4_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_WARDHA 4_DURG PS Total
249 | WR1_L_118 | 400kV LARA(NTPC)-CHAMPA I | 113.527 | WRTS-I | [16 empty] | WRPC | 100%
400kV LARA(NTPC)-CHAMPA I Total
250 | WR1_L_119 | 400kV LARA(NTPC)-CHAMPA II | 113.527 | WRTS-I |  | 2019-08-18 | 5:52 | 2019-08-18 | 7:13 |  |  |  | 0 | 0 | 1.35 | 0 |  |  |  | Line tripped on B-G fault due to rains, lightning and thunderstorm. Fault details at Champ: B-G, 113km, 4.7kA. At Lara(NTPC): B-G, 6.9km, 13.55kA. Fault is in Raigarh TLM. Newspaper cutting atatched | WRPC | 100% | LNCC
|  | 400kV LARA(NTPC)-CHAMPA II Total | [10 empty] | 0
251 | WR1_L_120 | 400kV RAIPUR-RAIGARH IV | 217.02 | WRTS-I | [16 empty] | WRPC | 100%
400kV RAIPUR-RAIGARH IV Total
252 | WR1_L_121 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_3 | 11.2 | WRTS-I | [16 empty] | WRPC | 100%
400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_3 Total
253 | WR1_L_122 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_4 | 11.2 | WRTS-I | [16 empty] | WRPC | 100%
400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_4 Total
254 | WR1_L_0123 | 400kV RAIGARH-JHARSUGUDA II | 110.98 | WRTS-I |  | 2019-08-18 | 2:52 | 2019-08-18 | 8:00 |  |  |  | 0 | 0 | 5.1333 | 0 |  |  |  | Line tripped on B-G fault at 02:52 Hrs dure to LA Conductionat Jharsuguda , considering safety of working staff the restoration work could not be commenced in view of Heavy lighning and rains. 'Newspaper cutting attached | WRPC | 99.14% | LNCC
[6 empty] | 2019-08-18 | 8:00 | 2019-08-18 | 14:25 |  |  |  | 6.4167 | 0 | 0 | 0 |  |  |  | Line tripped on B-G fault at 02:52 Hrs during persistent B-G fault due to rain and thunderstorm. Fault details from Raigarh: 49.902(M1),46.64KM(M2) from Raigarh end 5.2KA, 60KM(M1), 60.7KM(M2) |  |  | SEFT
|  | 400kV RAIGARH-SUNDERGARH II Total | [10 empty] | 6.4167
255 | WR1_T_124 | 765kV AURANGABAD(PG)-PADGHE(GIS) I | 284.816 | WRTS-I |  | 2019-08-01 | 1:15 | 2019-08-12 | 9:47 |  |  |  | 0 | 0 | 0 | 272.5333 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 01:34 hrs. | WRPC | 100% | LVRD
[6 empty] | 2019-08-15 | 16:52 | 2019-08-16 | 7:13 |  |  |  | 0 | 0 | 0 | 14.35 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 17:09 hrs. |  |  | LVRD
[6 empty] | 2019-08-16 | 7:13 | 2019-08-23 | 17:57 |  |  |  | 0 | 0 | 0 | 178.7333 |  |  |  | 'Outage availed for LILO works at Pune (GIS) by M/s. CWRTL. LILO Aurangabad - PuneGIS charged at 13:36hrs on 22.08.2019 and Padghe - Pune GIS charged at 17:57 hrs on 23.08.2019 |  |  | LCSD
|  | 765kV AURANGABAD(PG)-PADGHE(GIS) I Total | [10 empty] | 0
256 | WR1_T_125 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | 284.816 | WRTS-I |  | 2019-08-01 | 0:00 | 2019-08-01 | 6:15 |  |  |  | 0 | 0 | 0 | 6.25 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 11:42 hrs. | WRPC | 100% | LVRD
[6 empty] | 2019-08-12 | 13:38 | 2019-08-16 | 6:58 |  |  |  | 0 | 0 | 0 | 89.3333 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and . SLR converted as BR at Aurangabad end at 14:07 hrs. |  |  | LVRD
[6 empty] | 2019-08-23 | 19:06 | 2019-08-24 | 12:28 |  |  |  | 0 | 0 | 0 | 17.3667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Aurangabad end at 19:50 hrs. |  |  | LVRD
[6 empty] | 2019-08-31 | 17:44 | 2019-08-31 | 24:00 |  |  |  | 0 | 0 | 0 | 6.2667 |  |  |  | Line H/T as per WRLDC instructions for Voltage Regulation and SLR converted as BR at Aurangabad end at 17:47 hrs. |  |  | LVRD
|  | 765kV AURANGABAD(PG)-PADGHE(GIS) II Total | [10 empty] | 0
257 | WR1_T_055 | ICT2_765/400kv_PADGHE(GIS) | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT2_765/400kv_PADGHE(GIS) Total
258 | WR1_R_054 | BUS REACTOR_765kV_240MVAR_PADGHE(GIS) | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_765kV_240MVAR_PADGHE(GIS) TOTAL
259 | WR1_R_055 | SWITCHABLE LR_400kV_B'WATI 2_RAIPUR | 50 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_400kV_B'WATI 2_RAIPUR Total
260 | WR1_T_125 | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) I | 16.74 | WRTS-I | [16 empty] | WRPC | 100%
400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) I TOTAL
261 | WR1_T_125 | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) II | 16.74 | WRTS-I | [16 empty] | WRPC | 100%
400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) II TOTAL
262 | WR1_T_056 | ICT1_765/400kv_PADGHE(GIS) | 1500 | WRTS-I | [16 empty] | WRPC | 100%
ICT1_765/400kv_PADGHE(GIS) Total
263 |  | 400kV WARDHA-WARORA-I_LILOPOINT_PG | 3.708 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-WARORA-I_LILOPOINT_PG Total
264 |  | 400kV WARDHA-WARORA-2_LILOPOINT_PG | 3.708 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARDHA-WARORA-2_LILOPOINT_PG Total
265 |  | 400kV WARORA-PARLI-I_LILOPOINT_PG | 333.231 | WRTS-I | [16 empty] | WRPC | 100%
400kV WARORA-PARLI-I_LILOPOINT_PG Total
266 |  | 400kV WARORA-PARLI-2_LILOPOINT_PG | 333.231 | WRTS-I |  | 2019-08-14 | 14:51 | 2019-08-14 | 18:07 |  |  |  | 0 | 3.2667 | 0 | 0 |  |  |  | Emergency outage availed for rectification of hot spot Y-phase wave trap at Warora end. | WRPC | 100% | OMSU
|  | 400kV WARORA-PARLI-2_LILOPOINT_PG Total | [10 empty] | 0
267 |  | SWITCHABLE LR_JHARSUGUDA3_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_JHARSUGUDA3_D'JAIGARH Total
268 |  | SWITCHABLE LR_JHARSUGUDA4_D'JAIGARH | 330 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_JHARSUGUDA4_D'JAIGARH Total
269 |  | 765kV D'JAIGARH- JHARSUGUDA III | 149.4 | WRTS-I |  | 2019-08-23 | 14:18 | 2019-08-23 | 15:36 |  |  |  | 0 | 0 | 1.3 | 0 |  |  |  | Line tripped on Y ph - B ph fault. FC Y ph 17.2 KA, FC B ph 12.8 KA and FD 55.59 km from Dharamjayagarh end du to heavy rains, lightning , line was restored in 1.18 hours without any maintainence works.Newspaper cutting attached | WRPC | 100% | LNCC
|  | 765kV D'JAIGARH- JHARSUGUDA III Total | [10 empty] | 0
270 |  | 765kV D'JAIGARH- JHARSUGUDA IV | 149.4 | WRTS-I | [16 empty] | WRPC | 100%
765kV D'JAIGARH- JHARSUGUDA IV Total
271 |  | SWITCHABLE LR_D'JAIGARH1_RANCHI | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_D'JAIGARH1_RANCHI Total
272 |  | SWITCHABLE LR_D'JAIGARH2_RANCHI | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_D'JAIGARH2_RANCHI Total
273 |  | STATCOM AURANGABAD | 975 | WRTS-I |  | 2019-08-06 | 10:33 | 2019-08-06 | 18:30 |  |  |  | 7.95 | 0 | 0 | 0 |  |  |  | Emergency outage of coupling transformer at Aurangabad SS for attend sparking on LV isolator B-phase. | WRPC | 98.1% | OSFT
[6 empty] | 2019-08-08 | 4:48 | 2019-08-08 | 10:58 |  |  |  | 6.1667 | 0 | 0 | 0 |  |  |  | STATCOM tripped on R phase ground over current protection due to burning of R phase isolator contacts of secondary side of Coupling transformer. |  |  | OMST
|  | STATCOM AURANGABAD Total | [10 empty] | 14.1167
274 |  | STATCOM SOLAPUR | 975 | WRTS-I | [16 empty] | WRPC | 100%
STATCOM SOLAPUR Total
275 |  | SWITCHABLE LR_765kV_RAJNANDGAON 1_BILASPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_RAJNANDGAON 1_BILASPUR Total
276 |  | SWITCHABLE LR_765kV_RAJNANDGAON 2_BILASPUR | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_RAJNANDGAON 2_BILASPUR Total
277 |  | SWITCHABLE LR_765kV_JHARSUGUDA1_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_JHARSUGUDA1_DURG PS Total
278 |  | SWITCHABLE LR_765kV_JHARSUGUDA2_DURG PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
SWITCHABLE LR_765kV_JHARSUGUDA2_DURG PS Total
279 |  | BUS REACTOR_400kV_125MVAR_DHARAMJAYGARH SS | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_DHARAMJAYGARH SS Total
280 |  | BUS REACTOR-2_765kV_240MVAR_CHAMPA PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR-2_765kV_240MVAR_CHAMPA PS Total
281 |  | BUS REACTOR 3_765kV_330MVAR_DHARAMJAIAGARH SS | 330 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR 3_765kV_330MVAR_DHARAMJAIAGARH SS Total
282 |  | LR_400kV_80MVAR A'BAD 1_at WARDHA Ss | 80 | WRTS-I | [16 empty] | WRPC | 100%
LR_400kV_80MVAR A'BAD 1_at WARDHA Ss Total
283 |  | LR_400kV_80MVAR A'BAD 2_ at WARDHA Ss | 80 | WRTS-I | [16 empty] | WRPC | 100%
LR_400kV_80MVAR A'BAD 2_ at WARDHA Ss Total
284 |  | BUS REACTOR_400kV_125MVAR_KOTRA SS | 125 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR_400kV_125MVAR_KOTRA SS Total
285 |  | BUS REACTOR-2_765kV_240MVAR_Kotra PS | 240 | WRTS-I | [16 empty] | WRPC | 100%
BUS REACTOR-2_765kV_240MVAR_Kotra PS Total
286 |  | SWITCHABLE LR_765kV_AURANGABAD_PUNE GIS | 240 | WRTS-I |  | 2019-08-29 | 10:48 | 2019-08-29 | 18:34 |  |  |  | 0 | 0 | 0 | 7.7667 |  |  |  | SLR H/T as per WRLDC instructions for Voltage Regulation | WRPC | 100% | SVRD
|  | SWITCHABLE LR_765kV_AURANGABAD_PUNE GIS Total | [10 empty] | 0

## Element list (hidden)
SN | Element Name | TYPE | LENGTH | Jurisidiction | DOCO | Type of conductor | Configuration | PGCIL Code | SN
1 | 400kV KORBA-KORBA(WEST) | LINE | 14 | CG(O&M) | 1983-01-25 | Twin | ACSR Moose | WR1_L_001 | 1
2 | 400kV KORBA-BHILAI I | LINE | 197 | CG(O&M) | 1984-01-01 | Twin | ACSR Moose | WR1_L_002 | 2
3 | 400kV KORBA-BHILAI II | LINE | 192 | CG(O&M) | 1984-01-01 | Twin | ACSR Moose | WR1_L_003 | 3
4 | 400kV BHILAI-KORADI | LINE | 272 | MH(O&M) | 1984-05-01 | Twin | ACSR Moose | WR1_L_004 | 4
5 | 400kV KORADI-SATPURA | LINE | 149 | MH(O&M) | 1987-04-18 | Twin | ACSR Moose | WR1_L_005 | 5
6 | 400kV RAIPUR-BHILAI I | LINE | 13 | CG(O&M) | 1989-03-28 | Twin | ACSR Moose | WR1_L_006 | 6
7 | 400kV BHILAI-BHADRAVATI I | LINE | 322 | WR1-LINE | 1990-01-22 | Twin | ACSR Moose | WR1_L_007 | 7
8 | 400kV RAIPUR-BHADRAVATI I | LINE | 333 | WR1-LINE | 1989-03-28 | Twin | ACSR Moose | WR1_L_008 | 8
9 | 400kV RAIPUR-BHADRAVATI II | LINE | 345.55 | WR1-LINE | 2005-06-01 | Twin | ACSR Moose | WR1_L_009 | 9
10 | 400kV RAIPUR-BHADRAVATI III | LINE | 345.55 | WR1-LINE | 2005-06-01 | Twin | ACSR Moose | WR1_L_010 | 10
11 | 400kV BHADRAVATI-CHANDRAPUR I | LINE | 20 | MH(O&M) | 1989-03-28 | Twin | ACSR Moose | WR1_L_011 | 11
12 | 400kV BHADRAVATI-CHANDRAPUR II | LINE | 20 | MH(O&M) | 1989-03-28 | Twin | ACSR Moose | WR1_L_012 | 12
13 | 400kV BHADRAVATI-CHANDRAPUR III | LINE | 22.42 | MH(O&M) | 2006-05-01 | Twin | ACSR Moose | WR1_L_013 | 13
14 | 400kV BHADRAVATI-CHANDRAPUR IV | LINE | 22.42 | MH(O&M) | 2006-05-01 | Twin | ACSR Moose | WR1_L_014 | 14
15 | 400kV MAHAN-VINDHYACHAL | LINE | 19 | CG(O&M) | 1988-07-24 | Twin | ACSR Moose | WR1_L_015 | 15
16 | 400kV KORBA-MAHAN | LINE | 196 | CG(O&M) | 1988-07-24 | Twin | ACSR Moose | WR1_L_016 | 16
17 | 400kV VINDHYACHAL-KORBA II | LINE | 288.994 | CG(O&M) | 2007-06-01 | Twin | ACSR Moose | WR1_L_017 | 17
18 | 400kV SATPURA-SEONI | LINE | 1.507 | MH(O&M) | 2007-11-01 | Twin | ACSR Moose | WR1_L_018 | 18
19 | 400kV BHILAI-SEONI | LINE | 1.498 | MH(O&M) | 2007-11-01 | Twin | ACSR Moose | WR1_L_019 | 19
20 | 400kV BHILAI-BHATAPARA | LINE | 90.453 | CG(O&M) | 2000-01-01 | Twin | ACSR Moose | WR1_L_020 | 20
21 | 400kV BHATAPARA-KORBA | LINE | 123.73 | CG(O&M) | 2000-01-01 | Twin | ACSR Moose | WR1_L_021 | 21
22 | 400kV KORBA-SIPAT | LINE | 68.653 | CG(O&M) | 2014-09-03 | Twin | ACSR Moose | WR1_L_022 | 22
23 | 400kV RAIPUR-SIPAT I | LINE | 149.12 | CG(O&M) | 2008-08-01 | Twin | ACSR Moose | WR1_L_023 | 23
24 | 400KV RAIPUR-SIPAT II | LINE | 149.12 | CG(O&M) | 2008-08-01 | Twin | ACSR Moose | WR1_L_024 | 24
25 | 400kV RAIPUR-SIPAT III | LINE | 162.04 | CG(O&M) | 1990-02-08 | Twin | ACSR Moose | WR1_L_025 | 25
26 | 765kV BILASPUR-SIPAT I | LINE | 21.507 | CG(O&M) | 2013-04-01 | Quad | Bersimis | WR1_L_026 | 26
27 | 765kV SEONI-BILASPUR I | LINE | 337.046 | WR1-LINE | 2013-04-01 | Quad | Bersimis | WR1_L_027 | 27
28 | 765kV BILASPUR-SIPAT II | LINE | 22.216 | CG(O&M) | 2013-04-01 | Quad | Bersimis | WR1_L_028 | 28
29 | 765kV SEONI-BILASPUR II | LINE | 338.33 | WR1-LINE | 2013-04-01 | Quad | Bersimis | WR1_L_029 | 29
30 | 765kV SEONI-WARDHA I | LINE | 267.894 | MH(O&M) | 2009-04-01 | Quad | Bersimis | WR1_L_030 | 30
31 | 765kV SEONI-WARDHA II | LINE | 260.763 | MH(O&M) | 2012-03-01 | Quad | Bersimis | WR1_L_031 | 31
32 | 400kV WARDHA-AKOLA I | LINE | 161.865 | MH(O&M) | 2009-04-01 | Twin | ACSR Moose | WR1_L_032 | 32
33 | 400kV WARDHA-AKOLA II | LINE | 161.865 | MH(O&M) | 2009-04-01 | Twin | ACSR Moose | WR1_L_033 | 33
34 | 400kV AURANGABAD (PG) -AKOLA I | LINE | 289.966 | MH(O&M) | 2009-12-01 | Twin | ACSR Moose | WR1_L_034 | 34
35 | 400kV AURANGABAD (PG) -AKOLA II | LINE | 289.966 | MH(O&M) | 2009-12-01 | Twin | ACSR Moose | WR1_L_035 | 35
36 | 400kV BHADRAVATI-PARLI I | LINE | 378.667 | MH(O&M) | 2011-06-01 | Twin | ACSR Moose | WR1_L_036 | 36
37 | 400kV PARLI(PG)-PARLI(MSETCL) I | LINE | 4.958 | MH(O&M) | 2011-06-01 | Twin | ACSR Moose | WR1_L_037 | 37
38 | 400kV PARLI(PG)-PARLI(MSETCL) II | LINE | 4.958 | MH(O&M) | 2011-06-01 | Twin | ACSR Moose | WR1_L_038 | 38
39 | 400kV KORBA-RAIPUR III | LINE | 212.83 | CG(O&M) | 2011-07-01 | Twin | ACSR Moose | WR1_L_039 | 39
40 | 400kV KORBA-RAIPUR IV | LINE | 212.83 | CG(O&M) | 2011-07-01 | Twin | ACSR Moose | WR1_L_040 | 40
41 | 400kV WARDHA-PARLI I | LINE | 336.939 | MH(O&M) | 2011-08-01 | Quad | ACSR Moose | WR1_L_041 | 41
42 | 400kV WARDHA-PARLI II | LINE | 336.939 | MH(O&M) | 2011-08-01 | Quad | ACSR Moose | WR1_L_042 | 42
43 | 400kV WARDHA-MAUDA II | LINE | 123.45 | MH(O&M) | 2012-06-01 | Quad | ACSR Moose | WR1_L_043 | 43
44 | 400kV KORBA-VANDANA | LINE | 14.768 | CG(O&M) | 2012-04-01 | Twin | ACSR Moose | WR1_L_044 | 44
45 | 400kV VANDANA-BIRSINGHPUR | LINE | 211.874 | CG(O&M) | 2012-04-01 | Twin | ACSR Moose | WR1_L_045 | 45
46 | 400kV RAIPUR-WARDHA I | LINE | 370.565 | WR1-LINE | 2013-01-01 | Quad | ACSR Moose | WR1_L_046 | 46
47 | 400kV RAIPUR-WARDHA II | LINE | 370.565 | WR1-LINE | 2013-01-01 | Quad | ACSR Moose | WR1_L_047 | 47
48 | 400kV RAIPUR-DURG I | LINE | 21.43 | CG(O&M) | 2013-04-01 | Twin | ACSR Moose | WR1_L_048 | 48
49 | 400kV RAIPUR-DURG II | LINE | 21.43 | CG(O&M) | 2013-04-01 | Twin | ACSR Moose | WR1_L_049 | 49
50 | 400kV RAIGARH-KOTRA PS I | LINE | 6.288 | CG(O&M) | 2013-05-01 | Twin | ACSR Moose | WR1_L_050 | 50
51 | 400kV RAIGARH-KOTRA PS II | LINE | 6.288 | CG(O&M) | 2013-05-01 | Twin | ACSR Moose | WR1_L_051 | 51
52 | 765kV TAMNAR PS-KOTRA PS I | LINE | 47.986 | CG(O&M) | 2013-11-01 | Hexa | Zebra | WR1_L_052 | 52
53 | 765kV TAMNAR PS-KOTRA PS II | LINE | 47.986 | CG(O&M) | 2013-11-01 | Hexa | Zebra | WR1_L_053 | 53
54 | 765kV KOTRA PS-DURG PS I | LINE | 239.843 | CG(O&M) | 2014-02-01 | Hexa | Zebra | WR1_L_054 | 54
55 | 765kV KOTRA PS-DURG PS II | LINE | 239.843 | CG(O&M) | 2014-02-01 | Hexa | Zebra | WR1_L_055 | 55
56 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) II | LINE | 52.563 | MH(O&M) | 2014-04-29 | Quad | ACSR Moose | WR1_L_056 | 56
57 | 400kV BHADRAVATI-DHARIWAL TPP II | LINE | 2.923 | MH(O&M) | 2014-04-21 | Twin | ACSR Moose | WR1_L_057 | 57
58 | 400kV DHARIWAL TPP-PARLI II | LINE | 375.785 | MH(O&M) | 2014-04-21 | Twin | ACSR Moose | WR1_L_058 | 58
59 | 400kV AURANGABAD(PG)-AURANGABAD(MSETCL) I | LINE | 52.563 | MH(O&M) | 2014-04-30 | Quad | ACSR Moose | WR1_L_059 | 59
60 | 765KV DURG PS - D'JAIGARH | LINE | 357.62 | CG(O&M) | 2014-05-24 | Quad | Bersimis | WR1_L_060 | 60
61 | 765kV WARDHA - AURANGABAD(PG) I | LINE | 347.577 | MH(O&M) | 2014-07-08 | Quad | Bersimis | WR1_L_061 | 61
62 | 765kV WARDHA - AURANGABAD(PG) II | LINE | 347.577 | MH(O&M) | 2014-07-08 | Quad | Bersimis | WR1_L_062 | 62
63 | 765kV DURG PS -WARDHA_1 | LINE | 369.107 | WR1-LINE | 2014-11-17 | Hexa | zebra | WR1_L_063 | 63
64 | 765kV DURG PS -WARDHA_2 | LINE | 369.107 | WR1-LINE | 2014-11-17 | Hexa | Zebra | WR1_L_064 | 64
65 | 400Kv PARLI-PUNE(GIS)_1 | LINE | 9.57 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_065 | 65
66 | 400Kv PARLI-PUNE(GIS)_2 | LINE | 9.57 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_066 | 66
67 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_1 | LINE | 9.978 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_067 | 67
68 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_2 | LINE | 9.978 | MH(O&M) | 2015-03-02 | Twin | ACSR Moose | WR1_L_068 | 68
69 | 765kV PUNE(GIS)-SOLAPUR | LINE | 269.842 | MH(O&M) | 2015-03-02 | Quad | Bersimis | WR1_L_069 | 69
70 | 765kV WARDHA - AURANGABAD(PG) III | LINE | 355 | MH(O&M) | 2015-04-01 | Hexa | zebra | WR1_L_070 | 70
71 | 765kV WARDHA - AURANGABAD(PG) IV | LINE | 355 | MH(O&M) | 2015-04-01 | Hexa | zebra | WR1_L_071 | 71
72 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_1 | LINE | 11.2 | MH(O&M) | 2015-04-03 | Twin | ACSR Moose | WR1_L_072 | 72
73 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_2 | LINE | 11.2 | MH(O&M) | 2015-04-03 | Twin | ACSR Moose | WR1_L_073 | 73
74 | 765kV DURG PS- CHAMPA_1 | LINE | 149.15 | CG(O&M) | 2015-05-30 | Hexa | zebra | WR1_L_074 | 74
75 | 765kV CHAMPA- KOTRA PS | LINE | 96.33 | CG(O&M) | 2015-05-31 | Quad | Bersimis | WR1_L_075 | 75
76 | 765kV AURANGABAD(PG)-SOLAPUR I | LINE | 279.57 | MH(O&M) | 2015-10-07 | Hexa | zebra | WR1_L_076 | 76
77 | 765kV AURANGABAD(PG)-SOLAPUR II | LINE | 279.57 | MH(O&M) | 2015-10-07 | Hexa | zebra | WR1_L_077 | 77
78 | 220kV KORBA(EAST)-BUDDHIPADAR III | LINE | 184 | WR1-IR1 | 1999-09-01 | Single | AAAC Zebra | WR1_L_078 | 78
79 | 400kV RAIPUR-RAIGARH I | LINE | 217.02 | WR1-IR2 | 2003-04-01 | Twin | ACSR Moose | WR1_L_079 | 79
80 | 400kV RAIGARH-ROURKELA II | LINE | 212.46 | WR1-IR2 | 2014-07-03 | Twin | ACSR Moose | WR1_L_080 | 80
81 | 400kV RAIGARH-IBEUL I | LINE | 94.43 | WR1-IR2 | 2014-11-13 | Twin | ACSR Moose | WR1_L_081 | 81
82 | 400kV IBEUL-JHARSUGUDA I | LINE | 20.03 | WR1-IR2 | 2014-11-13 | Twin | ACSR Moose | WR1_L_082 | 82
83 | 400kV JHARSUGUDA-ROURKELA I | LINE | 142.448 | WR1-IR2 | 2003-04-01 | Twin | ACSR Moose | WR1_L_083 | 83
84 | 400kV RANCHI-SIPAT I | LINE | 405.772 | WR1-IR3 | 2009-01-01 | Twin | ACSR Moose | WR1_L_084 | 84
85 | 400kV RANCHI-SIPAT II | LINE | 405.772 | WR1-IR3 | 2009-01-01 | Twin | ACSR Moose | WR1_L_085 | 85
86 | 400kV RAIPUR-KSK III | LINE | 134.74 | WR1-IR4 | 2014-07-01 | Twin | ACSR Moose | WR1_L_086 | 86
87 | 400kV KSK-RKKML III | LINE | 82.248 | WR1-IR4 | 2014-10-11 | Twin | ACSR Moose | WR1_L_087 | 87
88 | 400kV RKKML-RAIGARH III | LINE | 3.896 | WR1-IR4 | 2014-10-11 | Twin | ACSR Moose | WR1_L_088 | 88
89 | 400kV RAIPUR-KSK IV | LINE | 161.82 | WR1-IR4 | 2014-07-25 | Twin | ACSR Moose | WR1_L_089 | 89
90 | 400kV KSK-RAIGARH IV | LINE | 113.389 | WR1-IR4 | 2014-07-25 | Twin | ACSR Moose | WR1_L_090 | 90
91 | 400kV RAIGARH-JHARSUGUDA III | LINE | 110.98 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_091 | 91
92 | 400kV JHARSUGUDA-ROURKELA III | LINE | 143.06 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_092 | 92
93 | 400kV RAIGARH-STERLITE IV | LINE | 105 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_093 | 93
94 | 400kV STERLITE-ROURKELA IV | LINE | 104.28 | WR1-IR4 | 2003-04-01 | Twin | ACSR Moose | WR1_L_094 | 94
95 | 765kV D'JAIGARH-BILASPUR | LINE | 90 | WR1-IR5 | 2014-04-01 | Quad | Bersimis | WR1_L_095 | 95
96 | 765kV D'JAIGARH-RANCHI I | LINE | 303 | WR1-IR5 | 2014-04-01 | Quad | Bersimis | WR1_L_096 | 96
97 | 765kV D'JAIGARH- JHARSUGUDA I | LINE | 149.789 | WR1-IR6 | 2014-07-31 | Quad | Bersimis | WR1_L_097 | 97
98 | 765kV D'JAIGARH- JHARSUGUDA II | LINE | 149.789 | WR1-IR6 | 2014-07-31 | Quad | Bersimis | WR1_L_098 | 98
99 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) I | LINE | 39.383 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_099 | 99
100 | 400kV KOLHAPUR (MSETCL)- KOLHAPUR (GIS) II | LINE | 39.383 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_100 | 100
101 | 400kV KOLHAPUR (GIS)-MAPUSA I | LINE | 156.039 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_101 | 101
102 | 400kV KOLHAPUR (GIS)-MAPUSA II | LINE | 156.039 |  | 2015-11-12 | Twin | ACSR Moose | WR1_L_102 | 102
103 | 400kV WARDHA-MAUDA I | LINE | 123.45 |  | 2015-12-05 | Quad | ACSR Moose | WR1_L_103 | 103
104 | 765kV D'JAIGARH-RANCHI II | LINE | 354 | WR1-IR7 | 2015-12-26 | Quad | Bersimis | WR1_L_104 | 104
105 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_3 | LINE | 14.373 |  |  |  |  | WR1_L_105 | 105
106 | 400Kv PUNE(GIS)-PUNE(TALEGOAN)_4 | LINE | 14.373 |  |  |  |  | WR1_L_106 | 106
107 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) I | LINE | 14.387 |  |  |  |  | WR1_L_107 | 107
108 | 400Kv AURANGABAD(MSETCL)-PUNE(GIS) II | LINE | 14.387 |  |  |  |  | WR1_L_108 | 108
109 | 400kV RAIPUR-RAIGARH II | LINE | 217.02 |  |  |  |  | WR1_L_109 | 109
110 | 400kV LARA(NTPC)-KOTRA PS I | LINE | 17.999 | MH(O&M) | 2016-05-05 | Twin | ACSR Moose | WR1_L_110 | 110
111 | 400kV LARA(NTPC)-KOTRA PS II | LINE | 17.999 | MH(O&M) | 2016-05-05 | Twin | ACSR Moose | WR1_L_111 | 111
112 | 400kV KORBA-BIRSINGHPUR | LINE | 226.642 | CG(O&M) | 2012-03-01 | Twin | ACSR Moose | WR1_L_112 | 112
113 | ICT1_400/220kv_RAIPUR | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_001 | 113
114 | ICT2_400/220kv_RAIPUR | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_002 | 114
115 | ICT1_400/220kv_MAPUSA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_003 | 115
116 | ICT2_400/220kv_MAPUSA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_004 | 116
117 | ICT1_400/220kv_BAHATAPARA | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_005 | 117
118 | ICT1_400/220kv_RAIGARH | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_006 | 118
119 | ICT2_400/220kv_RAIGARH | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_007 | 119
120 | ICT1_765/400kv_SEONI | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_008 | 120
121 | ICT2_765/400kv_SEONI | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_009 | 121
122 | ICT3_765/400kv_SEONI | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_010 | 122
123 | ICT1_400/220kv_SEONI | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_011 | 123
124 | ICT1_765/400kv_WARDHA | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_012 | 124
125 | ICT2_765/400kv_WARDHA | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_013 | 125
126 | ICT3_765/400kv_WARDHA | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_014 | 126
127 | ICT1_765/400kv_BILASPUR | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_015 | 127
128 | ICT2_765/400kv_BILASPUR | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_016 | 128
129 | ICT2_400/220kv_BAHATAPARA | ICT | 315 | CG(O&M) | 2013-04-01 | 315 | 315 | WR1_T_017 | 129
130 | ICT2_400/220kv_SEONI | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_018 | 130
131 | ICT3_400/220kv_RAIPUR | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_019 | 131
132 | ICT1_400/220kv_WARDHA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_020 | 132
133 | ICT2_400/220kv_WARDHA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_021 | 133
134 | ICT3_400/220kv_SOLAPUR | ICT | 500 | MH(O&M) | 2015-11-02 | 500 | 500 | WR1_T_022 | 134
135 | ICT1_400/220kv_SOLAPUR | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_023 | 135
136 | ICT2_400/220kv_SOLAPUR | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_024 | 136
137 | ICT1_400/220kv_PUNE | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_025 | 137
138 | ICT2_400/220kv_PUNE | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_026 | 138
139 | ICT3_400/220kv_PUNE | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_027 | 139
140 | ICT3_765/400kv_BILASPUR | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_028 | 140
141 | ICT1_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_029 | 141
142 | ICT2_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_030 | 142
143 | ICT4_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_031 | 143
144 | ICT3_400/220kv_MAPUSA | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_032 | 144
145 | ICT1_765/400kv_TAMNAR PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_033 | 145
146 | ICT2_765/400kv_TAMNAR PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_034 | 146
147 | ICT1_765/400kv_DURG PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_035 | 147
148 | ICT1_765/400kv_SOLAPUR | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_036 | 148
149 | ICT2_765/400kv_SOLAPUR | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_037 | 149
150 | ICT1_400/200kv_AURANGABAD | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_038 | 150
151 | ICT2_400/200kv_AURANGABAD | ICT | 315 | MH(O&M) | 2013-04-01 | 315 | 315 | WR1_T_039 | 151
152 | ICT2_765/400kv_AURANGABAD | ICT | 1500 | MH(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_040 | 152
153 | ICT3_765/400kv_TAMNAR PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_041 | 153
154 | ICT3_765/400kv_KOTRA PS | ICT | 1500 | CG(O&M) | 2013-04-01 | 1500 | 1500 | WR1_T_042 | 154
155 | ICT1_765/400kv_AURANGABAD | ICT | 1500 | MH(O&M) | 2014-07-01 | 1500 | 1500 | WR1_T_043 | 155
156 | ICT2_765/400kv_D'JAIGARH | ICT | 1500 | CG(O&M) | 2014-06-19 | 1500 | 1500 | WR1_T_044 | 156
157 | ICT1_765/400kv_D'JAIGARH | ICT | 1500 | CG(O&M) | 2014-07-09 | 1500 | 1500 | WR1_T_045 | 157
158 | ICT1_400/200kv_BHADRAWATI | ICT | 315 | MH(O&M) | 2015-03-19 | 315 | 315 | WR1_T_046 | 158
159 | ICT1_765/400kv_PUNE(GIS) | ICT | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | WR1_T_047 | 159
160 | ICT2_765/400kv_PUNE(GIS) | ICT | 1500 | MH(O&M) | 2015-03-02 | 1500 | 1500 | WR1_T_048 | 160
161 | ICT1_765/400kv_CHAMPA | ICT | 1500 | CG(O&M) | 2015-06-13 | 1500 | 1500 | WR1_T_049 | 161
162 | ICT2_765/400kv_CHAMPA | ICT | 1500 | CG(O&M) |  | 1500 | 1500 | WR1_T_050 | 162
163 | BUS REACTOR_400kV_63MVAR_RAIGARH | BR | 63 | CG(O&M) | 2013-04-01 | 63 | 63 | WR1_R_001 | 163
164 | BUS REACTOR_765kV_240MVAR_SEONI | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_002 | 164
165 | SWITCHABLE LR_400kV_KORBA 3_RAIPUR | BR | 50 | CG(O&M) | 2013-04-01 | 50 | 50 | WR1_R_003 | 165
166 | BUS REACTOR_400kV_50MVAR_WARDHA | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_004 | 166
167 | BUS REACTOR_400kV_63MVAR_SOLAPUR | BR | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | WR1_R_005 | 167
168 | BUS REACTOR_400kV_63MVAR_PARLI | BR | 63 | MH(O&M) | 2013-04-01 | 63 | 63 | WR1_R_006 | 168
169 | BUS REACTOR_400kV_50MVAR_PUNE | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_007 | 169
170 | BUS REACTOR_765kV_240MVAR_WARDHA | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_008 | 170
171 | BUS REACTOR_765kV_240MVAR_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_009 | 171
172 | SWITCHABLE LR_765kV_BINA_SEONI | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_010 | 172
173 | SWITCHABLE LR_765kV_SEONI 1_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_011 | 173
174 | SWITCHABLE LR_765kV_SEONI 2_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_012 | 174
175 | SWITCHABLE LR_765kV_D'GARH_BILASPUR | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_013 | 175
176 | BUS REACTOR_765kV_240MVAR_KOTRA PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_014 | 176
177 | BUS REACTOR_400kV_80MVAR_KOTRA PS | BR | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | WR1_R_015 | 177
178 | SWITCHABLE LR_765kV_DURG 1_KOTRA PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_016 | 178
179 | BUS REACTOR_400kV_50MVAR_BHADRAWATI | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_017 | 179
180 | BUS REACTOR_400kV_80MVAR_RAIPUR | BR | 80 | CG(O&M) | 2013-04-01 | 80 | 80 | WR1_R_018 | 180
181 | BUS REACTOR_400kV_50MVAR_MAPUSA | BR | 50 | MH(O&M) | 2013-04-01 | 50 | 50 | WR1_R_019 | 181
182 | BUS REACTOR_400kV_80MVAR_KOLHAPUR | BR | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | WR1_R_020 | 182
183 | SWITCHABLE LR_765kV_DURG 2_KOTRA PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_021 | 183
184 | BUS REACTOR_765kV_240MVAR_TAMNAR PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_022 | 184
185 | BUS REACTOR_765kV_240MVAR_DURG PS | BR | 240 | CG(O&M) | 2013-04-01 | 240 | 240 | WR1_R_023 | 185
186 | BUS REACTOR_765kV_240MVAR_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_024 | 186
187 | SWITCHABLE LR_765kV_RAICHUR 1_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_025 | 187
188 | SWITCHABLE LR_765kV_RAICHUR 2_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_026 | 188
189 | SWITCHABLE LR_765kV_A'BAD 1_WARDHA | BR | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | WR1_R_027 | 189
190 | SWITCHABLE LR_765kV_A'BAD 2_WARDHA | BR | 330 | MH(O&M) | 2013-04-01 | 330 | 330 | WR1_R_028 | 190
191 | SWITCHABLE LR_765kV_PUNE(GIS)_SOLAPUR | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_029 | 191
192 | SWITCHABLE LR_765kV_WARDHA 2_SEONI | BR | 240 | MH(O&M) | 2014-04-01 | 240 | 240 | WR1_R_030 | 192
193 | BUS REACTOR 1_765kV_330MVAR_D'JAIGARH | BR | 330 | CG(O&M) | 2014-04-01 | 240 | 240 | WR1_R_031 | 193
194 | BUS REACTOR 2_765kV_330MVAR_D'JAIGARH | BR | 330 | CG(O&M) | 2014-04-18 | 240 | 240 | WR1_R_032 | 194
195 | BUS REACTOR_765kV_240MVAR_AURANGABAD | BR | 240 | MH(O&M) | 2013-04-01 | 240 | 240 | WR1_R_033 | 195
196 | BUS REACTOR_400kV_125MVAR_AURANGABAD | BR | 125 | MH(O&M) | 2014-04-30 | 125 | 125 | WR1_R_034 | 196
197 | SWITCHABLE LR_765kV_CHAMPA 1_DURG PS | BR | 240 | CG(O&M) | 2014-05-26 | 240 | 240 | WR1_R_035 | 197
198 | BUS REACTOR_400kV_125MVAR_BHATAPARA | BR | 125 | CG(O&M) | 2014-07-26 | 125 | 125 | WR1_R_036 | 198
199 | SWITCHABLE LR_765kV_WARDHA 1_SEONI | BR | 240 | MH(O&M) | 2014-05-02 | 240 | 240 | WR1_R_037 | 199
200 | BUS REACTOR_400kV_125MVAR_RAIGARH | BR | 125 | CG(O&M) | 2014-08-01 | 125 | 125 | WR1_R_038 | 200
201 | SWITCHABLE LR_765kV_PADGHE1_AURANGABAD | BR | 240 | MH(O&M) | 2014-08-02 | 240 | 240 | WR1_R_039 | 201
202 | SWITCHABLE LR_765kV_PADGHE2_AURANGABAD | BR | 240 | MH(O&M) | 2014-08-07 | 240 | 240 | WR1_R_040 | 202
203 | SWITCHABLE LR_765kV_WARDHA 1_DURG PS | BR | 240 | CG(O&M) | 2014-08-21 | 240 | 240 | WR1_R_041 | 203
204 | SWITCHABLE LR_765kV_WARDHA 2_DURG PS | BR | 240 | CG(O&M) | 2014-08-29 | 240 | 240 | WR1_R_042 | 204
205 | SWITCHABLE LR_400kV_BOISAR2_AURANGABAD | BR | 80 | MH(O&M) | 2014-10-01 | 80 | 80 | WR1_R_043 | 205
206 | SWITCHABLE LR_400kV_BOISAR1_AURANGABAD | BR | 80 | MH(O&M) | 2014-10-02 | 80 | 80 | WR1_R_044 | 206
207 | BUS REACTOR_400kV_125MVAR_RAIPUR | BR | 125 | CG(O&M) | 2014-10-02 | 125 | 125 | WR1_R_045 | 207
208 | BUS REACTOR_765kV_330MVAR_WARDHA | BR | 330 | MH(O&M) | 2014-11-03 | 330 | 330 | WR1_R_046 | 208
209 | SWITCHABLE LR_400kV_KARAD_SOLAPUR | BR | 80 | MH(O&M) | 2014-11-26 | 80 | 80 | WR1_R_047 | 209
210 | BUS REACTOR_400kV_125MVAR_SEONI | BR | 125 | MH(O&M) | 2014-12-13 | 125 | 125 | WR1_R_048 | 210
211 | SWITCHABLE LR_400kV_PUNE(GIS) 1_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_049 | 211
212 | SWITCHABLE LR_400kV_PUNE(GIS) 2_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_050 | 212
213 | SWITCHABLE LR_400kV_PUNE(GIS) 3_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_051 | 213
214 | SWITCHABLE LR_400kV_PUNE(GIS) 4_PUNE | BR | 50 | MH(O&M) | 2014-12-13 | 50 | 50 | WR1_R_052 | 214
215 | BUS REACTOR_400kV_125MVAR_PARLI | BR | 125 | MH(O&M) | 2015-01-10 | 125 | 125 | WR1_R_053 | 215
216 | BUS REACTOR_765kV_240MVAR_PUNE(GIS) | BR | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | WR1_R_054 | 216
217 | SWITCHABLE LR_765kV_SOLAPUR_PUNE(GIS) | BR | 240 | MH(O&M) | 2015-03-02 | 240 | 240 | WR1_R_055 | 217
218 | BUS REACTOR_400kV_80MVAR_DHULE | BR | 80 | MH(O&M) | 2013-04-01 | 80 | 80 | WR1_R_056 | 218
219 | SWITCHABLE LR_765kV_A'BAD 3_WARDHA | BR | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | WR1_R_057 | 219
220 | SWITCHABLE LR_765kV_A'BAD 4_WARDHA | BR | 330 | MH(O&M) | 2015-04-01 | 330 | 330 | WR1_R_058 | 220
221 | SWITCHABLE LR_765kV_JABALPUR 3_D'JAIGARH | BR | 330 | CG(O&M) | 2015-09-14 | 330 | 330 | WR1_R_059 | 221
222 | SWITCHABLE LR_765kV_JABALPUR 4_D'JAIGARH | BR | 330 | CG(O&M) | 2015-09-15 | 330 | 330 | WR1_R_060 | 222
223 | SWITCHABLE LR_765kV_AURANGABAD 1_SOLAPUR | BR | 240 | MH(O&M) | 2015-10-07 | 240 | 240 | WR1_R_061 | 223
224 | SWITCHABLE LR_765kV_AURANGABAD 2_SOLAPUR | BR | 240 | MH(O&M) | 2015-10-07 | 240 | 240 | WR1_R_062 | 224
225 | SWITCHABLE LR_765kV_JABALPUR 2_D'JAIGARH | BR | 330 | CG(O&M) | 2015-10-17 | 330 | 330 | WR1_R_063 | 225
226 | SWITCHABLE LR_765kV_JABALPUR 1_D'JAIGARH | BR | 330 | CG(O&M) | 2015-10-17 | 330 | 330 | WR1_R_064 | 226
227 | BUS REACTOR_125MVAR_AT_KOLHAPUR(GIS) | BR | 125 | MH(O&M) | 2015-11-12 | 125 | 125 | WR1_R_065 | 227
228 | SWITCHABLE LR_400kV_WARDHA1_AURANGABAD | BR | 80 | MH(O&M) |  | 80 | 80 | WR1_R_066 | 228
229 | SWITCHABLE LR_400kV_WARDHA2_AURANGABAD | BR | 80 | MH(O&M) |  | 80 | 80 | WR1_R_067 | 229
230 | BUS REACTOR_765kV_240MVAR_CHAMPA | BR | 240 |  |  | 240 | 240 | WR1_R_068 | 230
231 | BUS REACTOR_400kV_80MVAR_CHAMPA | BR | 80 |  |  | 80 | 80 | WR1_R_069 | 231
232 | SWITCHABLE LR_JHARSUGUDA1_D'JAIGARH | BR | 330 |  |  |  |  | WR1_R_070 | 232
233 | SWITCHABLE LR_JHARSUGUDA2_D'JAIGARH | BR | 330 |  |  |  |  | WR1_R_071 | 233
234 | HVDC_POLE1_BHADRAWATI | HVDC | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | WR1_P_001 | 234
235 | HVDC_POLE2_BHADRAWATI | HVDC | 500 | MH(O&M) | 2013-04-01 | 500 | 500 | WR1_P_002 | 235
236 | 765kV AURANGABAD(PG)-PADGHE(GIS) I | LINE | 284.816
237 | 765kV AURANGABAD(PG)-PADGHE(GIS) II | LINE | 284.816
238 | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) I | LINE | 16.742
239 | 400kV PADGHE(GIS)-KUDUS( PADGHE MSETCL) II | LINE | 16.742
240 | ICT1_765/400kv_PADGHE(GIS) |  | 1
241 | ICT2_765/400kv_PADGHE(GIS) |  | 1
242 | BUS REACTOR_765kV_240MVAR_PADGHE(GIS) |  | 1
243 | 400kV RAIGARH-JHARSUGUDA II | LINE | 126.23
244 | 400kV JHARSUGUDA-ROURKELA II | LINE | 154.01
245 | 400kV RAIGARH-JHARSUGUDA IV | LINE | 122.49
246 | 400kV JHARSUGUDA-ROURKELA IV | LINE | 154.573
247 | SWITCHABLE LR_400kV_B'WATI 2_RAIPUR | BR | 80
248 | STATCOM_INDUCTIVE_AURANGABAD | STATCOM | 1
249 | STATCOM_CAPACITIVE_AURANGABAD | STATCOM | 1
250 | STATCOM_INDUCTIVE_SOLAPUR | STATCOM | 1
251 | STATCOM_CAPACITIVE_SOLAPUR | STATCOM | 1
252 | BUS REACTOR_400kV_63MVAR_BHADRAWATI | BR | 63
253 | 400kV WARDHA-WARORA-I_LILOPOINT_PG | LINE | 3.708
254 | 400kV WARDHA-WARORA-2_LILOPOINT_PG | LINE | 3.708
255 | 400kV WARORA-PARLI-I_LILOPOINT_PG | LINE | 333.231
256 | 400kV WARORA-PARLI-2_LILOPOINT_PG | LINE | 333.231
257 | 400kV KOLHAPUR-MAPUSA II | LINE | 150
258 | 400kV KOLHAPUR-MAPUSA I | LINE | 150
262 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_3 | LINE | 11.2
263 | 400Kv SOLAPUR(NTPC)-SOLAPUR(PG)_4 | LINE | 11.2
264 | 400kV KORBA-BIRSINGHPUR_2 | LINE | 226.642
265 | ICT5_765/400kv_CHAMPA | ICT | 1500
266 | ICT6_765/400kv_CHAMPA | ICT | 1500
267 | 400kV RAIPUR-RAIGARH III | LINE | 220.884
268 | 400kV RAIPUR-RAIGARH IV | LINE | 220.884
269 | ICT3_765/400kv_CHAMPA | ICT | 1500
270 | ICT4_765/400kv_CHAMPA | ICT | 1500
271 | 765kV DURG PS- CHAMPA_2 | LINE | 149.15
272 | 765KV D'JAIGARH- CHAMPA | LINE | 56.48
273 | 765kV DURG PS -WARDHA_3 | LINE | 357.27
274 | 765kV DURG PS -WARDHA_4 | LINE | 357.27
275 | SWITCHABLE LR_765kV_WARDHA 3_DURG PS | BR | 240
276 | SWITCHABLE LR_765kV_WARDHA 4_DURG PS | BR | 240
277 | 400kV RAIGARH-JHARSUGUDA I | LINE | 114.67
278 | ICT2_765/400kv_DURG PS | ICT | 1500
279 | ICT4_765/400kv_TAMNAR PS | ICT | 1500
281 | 400kV LARA(NTPC)-CHAMPA I | LINE | 113.527
282 | 400kV LARA(NTPC)-CHAMPA II | LINE | 113.527
283 | SWITCHABLE LR_JHARSUGUDA3_D'JAIGARH | BR | 330
284 | SWITCHABLE LR_JHARSUGUDA4_D'JAIGARH | BR | 330
285 | SWITCHABLE LR_765kV_SOLAPUR1_AURANGABAD | BR | 240
286 | SWITCHABLE LR_765kV_SOLAPUR2_AURANGABAD | BR | 240