## Tripping details JULY (hidden)
TRIPPING DETAILS OF WR-II FOR THE MONTH OF JULY' 2011
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | CAT. CODE | Details | WRLDC CODE FOR
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING
1 | 904070 | DAMOH-BHOPAL I 400KV | 2011-04-25 | 16:51 | 2011-04-25 | 16:51 | - | - | - | 9.7022e-13 | LVRD | Line H/T for Voltage Regulation as per WRLDC instruction. | LD 04/1432
2 | 904078 | DAMOH-BHOPAL II 400KV | 2011-04-26 | 17:54 | 2011-04-26 | 17:54 | - | - | - | -3.2337e-12 | LVRD | Line H/T for Voltage Regulation. | LD 04/1494
3 | 905010 | DAMOH BIRSINGHPUR II 400kV | 2011-05-02 | 15:05 | 2011-05-02 | 15:05 | - | - | - | -3.2337e-12 | LVRD | Line Kept out for voltage regulation on WRLDC Instruction. | LD 05 /83
4 | 905019 | DAMOH BIRSINGHPUR I 400kV | 2011-05-07 | 9:41 | 2011-05-07 | 9:41 | - | - | - | -1.7786e-12 | LVRD | Line H/T for Voltage Regulation. | LD/ 05/342
5 | 905114 | RAJGARH-NAGDA I 400kV | 2011-05-30 | 11:30 | 2011-05-30 | 11:30 | - | - | - | -2.4253e-12 | LVRD | Line H/T for Voltage Regulation. | LD 05/1718
6 | 906020 | NAGDA-DEHGAM II 400kV | 2011-06-04 | 5:07 | 2011-06-04 | 5:07 | - | - | - | -3.5571e-12 | LVRD | Line H/T for Voltage Regulation. | LD 06/189
7 | 906042 | SATNA-BINA(PG) I 400kV | 2011-06-08 | 18:17 | 2011-06-08 | 18:17 | - | - | 2.1019e-12 | - | LNCC | A/T on R- Ph to E/F due to Tower collapse at Loc No. 565 (A Type) due to heavy wind F/L - 57kM (Bina) & 78.9% (Satna)
8 | 906048 | KHANDWA-RAJGARH I 400kV | 2011-06-09 | 3:32 | 2011-06-09 | 3:32 | - | - | - | -3.2338e-13 | LVRD | Line kept out on O/V on WRLDC instruction. | LD 06/491
9 | 906068 | BINA-SHUJALPUR#1 400kV | 2011-06-15 | 6:00 | 2011-06-15 | 6:00 | - | - | 0 | - | GOVC | A/T on operation of O/V Protection at Shujalpur.Line kept out on O/V from 06:05hrs/15.06.11 vide ,WRLDC CODE LD 06/839
10 | 906069 | SHUJALPUR - NAGDA I 400kV | 2011-06-15 | 6:50 | 2011-06-15 | 6:50 | - | - | - | -3.2337e-12 | LVRD | Line H/T for Voltage regulation | LD 06/841
11 | 906072 | ITARSI-KHANDWA II 400kV | 2011-06-16 | 4:10 | 2011-06-16 | 4:10 | - | - | - | -1.6169e-12 | LVRD | Line H/T for Voltage regulation | LD 06/894
12 | 906089 | SHUJALPUR-NAGDA II 400kV | 2011-06-18 | 8:20 | 2011-06-18 | 8:20 | - | - | - | -3.2338e-12 | LVRD | Line H/T for voltage regulation | LD 06/1043
13 | 906093 | 220 kV KAWAS-HALDARWA # 1 | 2011-06-20 | 16:29 | 2011-06-20 | 16:29 | - | - | - | -2.2636e-12 | LPRD | H/T to control overloading of 220KV Kawas-icchapur line. | LD 06/1168
14 | 906095 | JABALPUR-ITARSI IV 400kV | 2011-06-21 | 17:38 | 2011-06-21 | 17:38 | - | - | - | 1.1319e-12 | LVRD | Line H/T for voltage regulation | LD 06/1225
15 | 906104 | 400/220 kV ICT BINA | 2011-06-24 | 8:20 | 2011-06-24 | 8:20 |  |  |  |  | SPRD | ICT H/T for Power Regulation due to non availibility of load . | LD 06/1364
16 | 906109 | VINDHYACHAL-JABALPUR III 400kV | 2011-06-24 | 22:07 | 2011-06-24 | 22:07 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1409
17 | 906121 | VINDHYACHAL-SATNA IV 400KV | 2011-06-26 | 7:04 | 2011-06-26 | 7:04 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1489
18 | 906124 | SEONI-BINA I(400kV) 765kV | 2011-06-26 | 8:04 | 2011-06-26 | 8:04 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1494
19 | 906125 | KHANDWA-RAJGARH II 400kV | 2011-06-27 | 0:11 | 2011-06-27 | 0:11 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1536
20 | 906133 | SARDAR SAROVAR-RAJGARH I 400kV | 2011-06-29 | 8:15 | 2011-06-29 | 8:15 |  |  |  |  | OSPD | H/T to avail S/D by GETCO. | LD 06/1649
21 | 906141 | KAWAS-ICHCHAPUR 220kV | 2011-06-30 | 17:30 | 2011-06-30 | 17:30 |  |  |  |  | OSPD | Line H/T to avail outage by NTPC for attending Hot Point at Kawas S/s. | LD 06/1740
22
23
24
25
26
27
28
29
30
31
32
33
34
34
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
Formulas:
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT. CODE, row below],1)="D"),[RESTORATION DATE, row below]+[RESTORATION TIME, row below]-[TRIPPING DATE, row below]-[TRIPPING TIME, row below],"-")
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT. CODE],1)="D"),[RESTORATION DATE]+[RESTORATION TIME]-[TRIPPING DATE]-[TRIPPING TIME],"-")

## List (hidden)
220 kV GANDHAR-HALDARWA # 1
220 kV GANDHAR-HALDARWA # 2
220 kV ICHCHAPUR-VAV
220 kV KAKRAPAR-HALDARWA # 1
220 kV KAKRAPAR-HALDARWA # 2
220 kV KAKRAPAR-VAPI # 1
220 kV KAKRAPAR-VAPI # 2
220 kV KAKRAPAR-VAV # 1
220 kV KAKRAPAR-VAV # 2
220 kV KAWAS-HALDARWA # 1
220 kV KAWAS-HALDARWA # 2
220 kV KAWAS-ICHCHAPUR
220 kV KAWAS-NAVSARI # 1
220 kV KAWAS-NAVSARI # 2
220 kV KAWAS-VAV # 1
220 kV VAPI-KHADOLI # 1
220 kV VAPI-KHADOLI#2
220 kV VAPI-KHARADPARA # 1
220 kV VAPI-KHARADPARA # 2
220 kV VAPI-MAGARWADA # 1
220 kV VAPI-MAGARWADA # 2
33 kV BUS REACTOR JABALPUR # 1
33 kV BUS REACTOR JABALPUR # 2
400 kV BINA(PG)-BINA(MPEB) # 1
400 kV BINA(PG)-BINA(MPEB) # 2
400 kV BINA-NAGDA # 1
400 kV BINA-NAGDA # 2
400 kV BUS REACTOR, BINA
400 kV BUS REACTOR, DAMOH
400 kV BUS REACTOR, DEHGAM
400 kV BUS REACTOR, GWALIOR
400 kV BUS REACTOR, ITARSI # 1
400 kV BUS REACTOR, ITARSI # 2
400 kV BUS REACTOR, ITARSI # 3
400 kV BUS REACTOR, JABALPUR # 3
400 kV BUS REACTOR, SATNA
400 kV DAMOH-BHOPAL # 1
400 kV DAMOH-BHOPAL # 2
400 kV GANDHAR(NTPC)-GANDHAR(GTEC)
400 kV GANDHAR-DEHGAM # 1
400 kV GANDHAR-DEHGAM # 2
400 kV GANDHAR-SUGEN # 1
400 kV GANDHAR-SUGEN # 2
400 kV INDORE-ASOJ # 1
400 kV INDORE-ASOJ # 2
400 kV JABALPUR-ITARSI # 1
400 kV JABALPUR-ITARSI#2
400 kV JABALPUR-ITARSI#3
400 kV JABALPUR-ITARSI#4
400 kV KHANDWA-DHULE#1
400 kV KHANDWA-DHULE#2
400 kV KHANDWA-RAJGARH#1
400 kV KHANDWA-RAJGARH#2
400 kV NAGDA-DEHGAM#1
400 kV NAGDA-DEHGAM#2
400 kV RAJGARH-NAGDA#1
400 kV RAJGARH-NAGDA#2
400 kV SARDAR SAROVAR-RAJGARH#1
400 kV SARDAR SAROVAR-RAJGARH#2
400 kV SATNA-BINA(PG)#1
400 kV SATNA-BINA(PG)#2
400 kV SATNA-BINA(PG)#3
400 kV SATNA-BINA(PG)#4
400 kV SATPURA-ITARSI
400 kV SEONI-KHANDWA#1
400 kV SEONI-KHANDWA#2
400 kV VAPI-SUGEN
400 kV VINDHYACHAL-JABALPUR#1
400 kV VINDHYACHAL-JABALPUR#2
400 kV VINDHYACHAL-JABALPUR#3
400 kV VINDHYACHAL-JABALPUR#4
400 kV VINDHYACHAL-SATNA#1
400 kV VINDHYACHAL-SATNA#2
400 kV VINDHYACHAL-SATNA#3
400 kV VINDHYACHAL-SATNA#4
400 kV#1TARSI-INDORE#1
400 kV#1TARSI-INDORE#2
400 kV#1TARSI-KHANDWA#1
400 kV#1TARSI-KHANDWA#2
400/220 kV ICT ITARSI
400/220 kV ICT#1 DAMOH
400/220 kV ICT#1 DEHGAM
400/220 kV ICT#1 GWALIOR
400/220 kV ICT#1 JABALPUR
400/220 kV ICT#1 KHANDWA
400/220 kV ICT#1 RAJGARH
400/220 kV ICT#1 SATNA
400/220 kV ICT#1 VAPI
400/220 kV ICT#2 DAMOH
400/220 kV ICT#2 DEHGAM
400/220 kV ICT#2 GWALIOR
400/220 kV ICT#2 JABALPUR
400/220 kV ICT#2 KHANDWA
400/220 kV ICT#2 RAJGARH
400/220 kV ICT#2 SATNA
400/220 kV ICT#2 VAPI
765 kV AGRA-GWALIOR#1 (400 kV)
765 kV AGRA-GWALIOR#2 (400 kV)
765 kV BINA-GWALIOR#1 (400 kV)
765 kV BINA-GWALIOR#2 (400 kV)
765 kV SEONI-BINA (400 kV)

## code (hidden)
POWER GRID CORPORATION OF INDIA LIMITED
400 / 220 kV SUB-STATION, JABALPUR
STANDARD LIST OF ELEMENT OUTAGE CATEGORIES
CATEGORY | Paertaining to | TYPE OF OUTAGE
GGDC | SYSTEM CONSTRAINTS | Power swings / trippings due to Grid disturbance / Under frequency islanding trippings / Reverse power flow blocking related tripping / Hand tripping due to loss of voltage
GOFC | SYSTEM CONSTRAINTS | ICT tripping on over fluxing
GOLC | SYSTEM CONSTRAINTS | ICT tripping on over loading / over-current
GOMD | SYSTEM CONSTRAINTS | Unable to restore after any outage ( other than grid disturbance ), due to system constraint
GOVC | SYSTEM CONSTRAINTS | Tripping on Over Voltage protection
LART | LINE FAULTS ON LINES OWNED BY POWERGRID | Auto Re-closure due to Earth faults
LCSD | OUTAGE OF ELEMENTS UNDER O&M TO FASCILITATE THE CONSTRUCTION ACTIVITIES OF NEW SYSTEM EXECUTED BY POWERGRID | Line shutdown taken to fascilitate construction activities of new system being executed by POWERGRID
LEFT | LINE FAULTS ON LINES OWNED BY POWERGRID | Tripping due to Earth faults
LHWT | LINE FAULTS ON LINES OWNED BY POWERGRID | Faults due to snapping of conductors, earth wire, jumper, insulator failure, failure of tower due to design & material deficiency etc.
LMAC | SYSTEM OUTAGE CAUSED BY MISCREANTS / MILITANT ACTIVITIES | Line breakdown caused by miscreants / militant activities
LNCC | OUTAGE OF SYSTEM DUE TO NATURAL CALAMITIES | Line outage due to Natural calamities
LPPT | LINE FAULTS ON LINES OWNED BY POWERGRID | Phase to phase faults, double line to Earth faults, 3-ph and 3-ph reath faults, but not due to Power Swings.
LPRD | SYSTEM CONSTRAINTS | Line hand tripped for Power Regulation on RLDC instruction
LVRD | SYSTEM CONSTRAINTS | Line hand tripped for Voltage Regulation on RLDC instruction
OMST | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Miscellaneous outages attributable to POWERGRID
OMSU | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Miscellaneous outages attributable to Other agency or force majeure condition.
OSFD | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Forced shutdown availed by other agency / agencies causing outage of POWERGRID element.
OSFT | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Forced shutdown ( e.g. E/W snapping / hotspots )
OSPD | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Planned shutdown availed by other agency / agencies for maintenance or construction of their transmission system causing outage of POWERGRID element.
OSPT | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Planned shutdown for maintenance work of POWERGRID elements
SBBT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Busbar protection operation (POWERGRID Substation only including the fault initiated in POWERGRID owned by other agency
SBBU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Busbar protection operation
SCSD | OUTAGE OF ELEMENTS UNDER O&M TO FASCILITATE THE CONSTRUCTION ACTIVITIES OF NEW SYSTEM EXECUTED BY POWERGRID | Substation equipment shutdown taken to fascilitate construction activities of new system being executed by POWERGRID
SEFT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Equipment failure
SEFU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Equipment failure
SEMT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Equipment Mal-operation
SEMU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Equipment Mal-operation
SICT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | REF, Differential, Buchholz protection operation, PRV, OTI, WTI on ICT
SICU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | REF, Differential, Buchholz protection operation, PRV, OTI, WTI on ICT
SMAC | SYSTEM OUTAGE CAUSED BY MISCREANTS / MILITANT ACTIVITIES | Substation equipment failure caused by miscreants / militant activities
SNCC | OUTAGE OF SYSTEM DUE TO NATURAL CALAMITIES | Substation equipment outage due to Natural calamities
SPLT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Line tripped due to PLCC mal-operation
SPLU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Line tripped due to PLCC mal-operation of other agency
SPRD | SYSTEM CONSTRAINTS | Transformer hand tripped for Power Regulation on RLDC instruction
SRET | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Reactor Differential, REF, Backup impedance, Buchholz protection including NGR protections
SREU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Reactor Differential, REF, Backup impedance, Buchholz protection including NGR protections
SRMT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Relay Mal-operation
SRMU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Relay Mal-operation
SVRD | SYSTEM CONSTRAINTS | Bus reactor hand tripped for Voltage Regulation on RLDC instruction

## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-II) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-II) Transmission System in Western Region for the month of JUNE 2014 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | SATPURA-ITARSI 400kV | 100% | 48 | BINA-BINA(MP) II 400kV | 100%
2 | ITARSI-INDORE I 400kV | 100% | 49 | BINA-GWALIOR I 765kV | 99.64%
3 | ITARSI-INDORE II 400kV | 100% | 50 | SATNA-BINA IV 400kV | 100%
4 | INDORE-ASOJ I 400kV | 100% | 51 | SATNA-BINA III 400kV | 100%
5 | INDORE-ASOJ II 400kV | 99.88% | 52 | BINA-SHUJALPUR I 400kV | 100%
6 | VINDHYACHAL-JABALPUR I 400kV | 99.96% | 53 | BINA-SHUJALPUR II 400kV | 100%
7 | VINDHYACHAL-JABALPUR II 400kV | 100% | 54 | SHUJALPUR-NAGDA I 400kV | 100%
8 | JABALPUR-ITARSI I 400kV | 100% | 55 | SHUJALPUR-NAGDA II 400kV | 100%
9 | JABALPUR-ITARSI II 400kV | 100% | 56 | NAGDA-DEHGAM II 400KV | 100%
10 | GANDHAR-DEHGAM I 400kV | 100% | 57 | NAGDA-DEHGAM I 400KV | 100%
11 | GANDHAR-DEHGAM II 400kV | 100% | 58 | SEONI-KHANDWA I 400kV | 100%
12 | VINDHYACHAL-SASAN III 400kV | 100% | 59 | SEONI-KHANDWA II 400kV | 100%
13 | SASAN-JABALPUR 400kV | 99.25% | 60 | KHANDWA-RAJGARH II 400kV | 99.97%
14 | VINDHYACHAL-JABALPUR IV 400kV | 99.15% | 61 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 100%
15 | JABALPUR-ITARSI III 400kV | 100% | 62 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | 100%
16 | JABALPUR-ITARSI IV 400kV | 100% | 63 | RAJGARH-NAGDA I 400kV(LILO) | 100%
17 | ITARSI-KHANDWA I 400kV | 100% | 64 | RAJGARH-NAGDA II 400kV(LILO) | 100%
18 | ITARSI-KHANDWA II 400kV | 100% | 65 | KHANDWA-RAJGARH I 400kV | 100%
19 | KHANDWA-DHULE I 400kV | 98.12% | 66 | VAPI-MAGARWADA I 220kV | 100%
20 | KHANDWA-DHULE II 400kV | 100% | 67 | VAPI-MAGARWADA II 220kV | 100%
21 | GANDHAR-SUGEN 400kV | 100% | 68 | VAPI-KHARADPARA I 220kV | 100%
22 | SUGEN-VAPI 400kV | 100% | 69 | VAPI-KHARADPARA II 220kV | 100%
23 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | 100% | 70 | BINA-GWALIOR II 765kV | 100%
24 | GANDHAR-HALDARWA I 220kV | 100% | 71 | SEONI-BINA I 765kV | 100%
25 | GANDHAR-HALDARWA II 220kV | 100% | 72 | DAMOH-BHOPAL I 400KV | 100%
26 | KAWAS-NAVSARI(GIS) I 220kV | 100% | 73 | DAMOH-BHOPAL II 400KV | 100%
27 | KAWAS-NAVSARI(GIS) II 220kV | 100% | 74 | VAPI-KHADOLI I 220kV | 100%
28 | NAVSARI(GIS)-NAVSARI I 220kV | 100% | 75 | VAPI-SAYALI 220kV | 100%
29 | NAVSARI(GIS)-NAVSARI II 220kV | 100% | 76 | SAYALI-KHADOLI 220kV | 100%
30 | KAWAS-VAV I 220kV | 100% | 77 | DAMOH-BIRSINGHPUR I 400kV | 99.86%
31 | KAWAS-VAV II 220kV | 99.93% | 78 | DAMOH-BIRSINGHPUR II 400kV | 100%
32 | KAWAS-HALDARWA I 220kV | 100% | 79 | DEHGAM-PIRANA I 400kV | 100%
33 | KAWAS-HALDARWA II 220kV | 100% | 80 | DEHGAM-PIRANA II 400kV | 100%
34 | KAKRAPAR-HALDARWA I 220kV | 97.73% | 81 | MUNDRA-BHACHAU I 400kV | 99.06%
35 | KAKRAPAR-HALDARWA II 220kV | 100% | 82 | MUNDRA-BHACHAU II 400kV | 99.06%
36 | KAKRAPAR-VAV I 220kV | 100% | 83 | BHACHAU-RANCHHODPURA I 400kV | 100%
37 | KAKRAPAR-VAV II 220kV | 100% | 84 | BHACHAU-RANCHHODPURA II 400kV | 100%
38 | KAKRAPAR-VAPI I 220kV | 100% | 85 | MUNDRA-LIMBDI I 400kV | 100%
39 | KAKRAPAR-VAPI II 220kV | 98.8% | 86 | MUNDRA-LIMBDI II 400kV | 100%
40 | VINDHYACHAL-SATNA I 400kV | 100% | 87 | SATNA-BINA I 765kV | 100%
41 | VINDHYACHAL-SATNA II 400kV | 100% | 88 | SATNA-BINA II 765kV | 100%
42 | VINDHYACHAL-SATNA III 400kV | 100% | 89 | BINA-INDORE I 765kV | 100%
43 | VINDHYACHAL-NIGRIE 400kV | 100% | 90 | GANDHAR-NAVSARI(GIS) II 400kV | 100%
44 | NIGRIE-SATNA 400kV | 100% | 91 | GANDHAR-NAVSARI(GIS) I 400kV | 100%
45 | SATNA-BINA I 400kV | 99.5% | 92 | MUNDRA-JETPUR I 400kV | 100%
46 | SATNA-BINA II 400kV | 100% | 93 | MUNDRA-JETPUR II 400kV | 100%
47 | BINA-BINA(MP) I 400kV | 100% | 94 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) I 400kV | 100%
95 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) II 400kV | 100% | 147 | ICT1 BINA 765/400KV | 100%
96 | VINDHYACHAL(POOLING)-SASAN I 400kV | 99.38% | 148 | ICT3 VAPI 400/220KV | 100%
97 | VINDHYACHAL(POOLING)-SASAN II 400kV | 100% | 149 | ICT2 BINA 765/400KV | 99.17%
98 | SASAN-SATNA I 765kV | 100% | 150 | ICT1 GWALIOR 765/400KV | 100%
99 | BINA-BINA(MP) III 400kV | 100% | 151 | ICT2 GWALIOR 765/400KV | 100%
100 | VAPI-NAVASARI(GIS) II 400kV | 98.63% | 152 | ICT2 INDORE 765/400KV | 100%
101 | SASAN-SATNA II 765kV | 99.88% | 153 | ICT1 INDORE 765/400KV | 100%
102 | BINA-BINA(MP) IV 400kV | 100% | 154 | ICT1 JABALPUR 765/400KV | 100%
103 | INDORE(MP)-INDORE I 400kV | 100% | 155 | ICT2 JABALPUR 765/400KV | 100%
104 | INDORE(MP)-INDORE II 400kV | 100% | 156 | ICT1 KALA(GIS) 400/220kV | 100%
105 | JABALPUR-JABALPUR(POOLING) I 400kV | 100% | 157 | ICT2 KALA(GIS) 400/220kV | 100%
106 | JABALPUR-JABALPUR(POOLING) II 400kV | 100% | 158 | BUS REACTOR I DEHGAM 400kV | 100%
107 | JABALPUR(POOLING)-BINA I 765kV | 100% | 159 | BUS REACTOR I JABALPUR 33kV | 100%
108 | JABALPUR(POOLING)-BINA II 765kV | 100% | 160 | BUS REACTOR II JABALPUR 33kV | 100%
109 | SATNA-GWALIOR I 765kV | 100% | 161 | BUS REACTOR I ITARSI 400kV | 100%
110 | PIRANA-ASOJ I 400KV | 100% | 162 | BUS REACTOR II ITARSI 400kV | 100%
111 | PIRANA-ASOJ II 400KV | 100% | 163 | BUS REACTOR III ITARSI 400kV | 100%
112 | NAVSARI(GIS)-KALA I 400kV | 100% | 164 | BUS REACTOR I JABALPUR 400kV | 100%
113 | KALA-VAPI I 400kV | 100% | 165 | BUS REACTOR DHULE 400kV | 100%
114 | INDORE-ASOJ III 400kV | 99.65% | 166 | BUS REACTOR I SATNA 400kV | 100%
115 | BINA-GWALIOR III 765kV | 99.66% | 167 | BUS REACTOR BINA 400kV | 100%
116 | AGRA-GWALIOR I 765kV | 99.84% | 168 | BUS REACTOR DAMOH 400kV | 100%
117 | AGRA-GWALIOR II 765kV | 100% | 169 | BUS REACTOR I GWALIOR 400kV | 100%
118 | ICT1 JABALPUR 400/220kV | 100% | 170 | BUS REACTOR I KHANDWA 400kV | 100%
119 | ICT2 JABALPUR 400/220kV | 100% | 171 | BUS REACTOR II DEHGAM 400kV | 100%
120 | ICT1 DEHGAM 400/220kV | 100% | 172 | BUS REACTOR BHACHAU 400kV | 100%
121 | ICT2 DEHGAM 400/220kV | 100% | 173 | BUS REACTOR I SHUJALPUR 400kV | 100%
122 | ICT1 SATNA 400/220kV | 100% | 174 | BUS REACTOR RAJGARH 400kV | 100%
123 | ICT2 SATNA 400/220KV | 99.58% | 175 | BUS REACTOR SATNA 765kV | 100%
124 | ICT1 KHANDWA 400/220kV | 100% | 176 | BUS REACTOR NAVSARI 400kV | 100%
125 | ICT2 KHANDWA 400/220kV | 100% | 177 | SWITCHABLE LINE REACTOR BINA I 765kV AT SATNA | 100%
126 | ICT1 VAPI 400/220KV | 100% | 178 | SWITCHABLE LINE REACTOR BINA II 765kV AT SATNA | 100%
127 | ICT2 VAPI 400/220KV | 100% | 179 | BUS REACTOR II SATNA 400kV | 100%
128 | ICT1 GWALIOR 400/220kV | 99.3% | 180 | SWITCHABLE LINE REACTOR BINA I 765kV AT GWALIOR | 100%
129 | ICT1 RAJGARH 400/220kV | 100% | 181 | SWITCHABLE LINE REACTOR BINA II 765kV AT GWALIOR | 100%
130 | ICT2 GWALIOR 400/220kV | 100% | 182 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT NAGDA | 100%
131 | ICT ITARSI 400/220kV | 100% | 183 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT NAGDA | 100%
132 | ICT1 DAMOH 400/220kV | 100% | 184 | BUS REACTOR II GWALIOR 400kV | 100%
133 | ICT2 DAMOH 400/220kV | 100% | 185 | BUS REACTOR III GWALIOR 400kV | 100%
134 | ICT2 RAJGARH 400/220KV | 98.44% | 186 | BUS REACTOR I INDORE 400kV | 100%
135 | ICT BINA 400/220kV | 99.73% | 187 | SWITCHABLE LINE REACTOR INDORE 765kV AT BINA | 100%
136 | ICT1 PIRANA 400/220kV | 100% | 188 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT BINA | 100%
137 | ICT2 PIRANA 400/220kV | 100% | 189 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT BINA | 100%
138 | ICT3 GWALIOR 400/220kV | 100% | 190 | BUS REACTOR I INDORE 765kV | 100%
139 | ICT1 SHUJALPUR 400/220kV | 100% | 191 | SWITCHABLE LINE REACTOR BINA I 765kV AT JABALPUR (POOLING) | 100%
140 | ICT1 BHACHAU 400/220kV | 100% | 192 | BUS REACTOR JABALPUR(POOLING) 400kV | 100%
141 | ICT2 BHACHAU 400/220kV | 100% | 193 | BUS REACTOR BINA 765kV | 100%
142 | ICT2 SHUJALPUR 400/220kV | 100% | 194 | BUS REACTOR JABALPUR POOLING 765kV | 100%
143 | ICT1 SATNA 765/400KV | 99.25% | 195 | BUS REACTOR II KHANDWA 400kV | 100%
144 | ICT2 NAVSARI(GIS) 400/220kV | 100% | 196 | BUS REACTOR II JABALPUR 400kV | 100%
145 | ICT1 NAVSARI(GIS) 400/220kV | 100% | 197 | BUS REACTOR KALA(GIS) 400kV | 100%
146 | ICT2 SATNA 765/400KV | 100% | 198 | BUS REACTOR II INDORE 400kV | 100%
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
Availability Bus Reactors =
System Availability :-
Note on B23: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B24: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B25: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B78: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B79: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## INDEX
WRTS-II TRANSMISSION SYSTEM AVAILABILITY FOR |  |  |  | 2014-06-30
SN | Element Name | TYPE | PG | OTHERS | SYSTEM | DEEMED | PG (TNAi) | OTHERS | SYSTEM | DEEMED | Total Hrs (Ti) | Line length/ MVA /(R) | SIL/ Set | Wi= CktKmX SIL | Wi x (Ti - TNAi) | =Wi x Ti | Individual Element Availability | Target Availability as per SOP
1 | SATPURA-ITARSI 400kV | INTRA | 0 | 0 | 0 | 0.40694 | 0 | 0 | 0 | 9.77 | 720 | 79 | 515 | 40685 | 29293200 | 29293200 | 100% | 90%
2 | ITARSI-INDORE I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 207 | 236.2774 | 48909.4171 | 35214780.3121 | 35214780.3121 | 100% | 90%
3 | ITARSI-INDORE II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 214 | 250.3527 | 53575.4744 | 38574341.5376 | 38574341.5376 | 100% | 90%
4 | INDORE-ASOJ I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 289 | 339.4716 | 98107.2913 | 70637249.7589 | 70637249.7589 | 100% | 90%
5 | INDORE-ASOJ II 400kV | INTRA | 0.034722 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 720 | 273 | 326.2678 | 89071.1154 | 64057274.0344 | 64131203.0602 | 99.88% | 90%
6 | VINDHYACHAL-JABALPUR I 400kV | INTRA | 0.011806 | 0.18611 | 0 | 0 | 0.28 | 4.47 | 0 | 0 | 715.53 | 360 | 444.645 | 160072.198 | 114491639.5846 | 114536459.8 | 99.96% | 90%
7 | VINDHYACHAL-JABALPUR II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 360 | 444.645 | 160072.198 | 115251982.5248 | 115251982.5248 | 100% | 90%
8 | JABALPUR-ITARSI I 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 06:18 | 0 | 0 | 0 | 54.3 | 720 | 232 | 291.974 | 67737.9752 | 48771342.1691 | 48771342.1691 | 100% | 90%
9 | JABALPUR-ITARSI II 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 06:24 | 0 | 0 | 0 | 54.4 | 720 | 232 | 291.974 | 67737.9752 | 48771342.1691 | 48771342.1691 | 100% | 90%
10 | GANDHAR-DEHGAM I 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 11:03 | 0 | 0 | 0 | 59.05 | 720 | 157 | 515 | 80855 | 58215600 | 58215600 | 100% | 90%
11 | GANDHAR-DEHGAM II 400kV | INTRA | 0 | 0 | 0 | 1899-12-31 20:50 | 0 | 0 | 0 | 44.83 | 720 | 157 | 515 | 80855 | 58215600 | 58215600 | 100% | 90%
12 | VINDHYACHAL-SASAN III 400kV | INTRA | 0 | 0.36111 | 0 | 0 | 0 | 8.67 | 0 | 0 | 711.33 | 21 | 515 | 10815 | 7693033.95 | 7693033.95 | 100% | 90%
13 | SASAN-JABALPUR 400kV | INTRA | 0.22431 | 0.038194 | 0 | 0 | 5.38 | 0.92 | 0 | 0 | 719.08 | 376 | 438.8604 | 165011.4981 | 117768706.2181 | 118656468.078 | 99.25% | 90%
14 | VINDHYACHAL-JABALPUR IV 400kV | INTRA | 0.25625 | 0 | 0 | 0 | 6.15 | 0 | 0 | 0 | 720 | 389 | 353.3073 | 137436.5477 | 98109079.5445 | 98954314.3126 | 99.15% | 90%
15 | JABALPUR-ITARSI III 400kV | INTRA | 0 | 0 | 0 | 0.99653 | 0 | 0 | 0 | 23.92 | 720 | 234 | 282.822 | 66180.3576 | 47649857.4532 | 47649857.4532 | 100% | 90%
16 | JABALPUR-ITARSI IV 400kV | INTRA | 0 | 0 | 0 | 0.89792 | 0 | 0 | 0 | 21.55 | 720 | 234 | 282.822 | 66180.3576 | 47649857.4532 | 47649857.4532 | 100% | 90%
17 | ITARSI-KHANDWA I 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 12:13 | 0 | 0 | 0 | 60.22 | 720 | 196.64 | 393.713 | 77419.723 | 55742200.5755 | 55742200.5755 | 100% | 90%
18 | ITARSI-KHANDWA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 196.64 | 515 | 101269.6 | 72914112 | 72914112 | 100% | 90%
19 | KHANDWA-DHULE I 400kV | INTRA | 0.56319 | 0.020139 | 0 | 0 | 13.52 | 0.48 | 0 | 0 | 719.52 | 261.78 | 315.6668 | 82635.2673 | 58340498.7012 | 59457727.5149 | 98.12% | 90%
20 | KHANDWA-DHULE II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 261.78 | 315.6668 | 82635.2673 | 59497392.4431 | 59497392.4431 | 100% | 90%
21 | GANDHAR-SUGEN 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 57 | 515 | 29355 | 21135600 | 21135600 | 100% | 90%
22 | SUGEN-VAPI 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 110 | 515 | 56650 | 40788000 | 40788000 | 100% | 90%
23 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | INTRA | 0 | 0 | 0 | 0.53819 | 0 | 0 | 0 | 12.92 | 720 | 13 | 515 | 6695 | 4820400 | 4820400 | 100% | 90%
24 | GANDHAR-HALDARWA I 220kV | INTRA | 0 | 0 | 0 | 0.26111 | 0 | 0 | 0 | 6.27 | 720 | 13 | 132 | 1716 | 1235520 | 1235520 | 100% | 90%
25 | GANDHAR-HALDARWA II 220kV | INTRA | 0 | 0.06875 | 0 | 0.1625 | 0 | 1.65 | 0 | 3.9 | 718.35 | 13 | 132 | 1716 | 1232688.6 | 1232688.6 | 100% | 90%
26 | KAWAS-NAVSARI(GIS) I 220kV | INTRA | 0 | 0 | 0 | 0.63611 | 0 | 0 | 0 | 15.27 | 720 | 58.15 | 132 | 7675.8 | 5526576 | 5526576 | 100% | 90%
27 | KAWAS-NAVSARI(GIS) II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 58.15 | 132 | 7675.8 | 5526576 | 5526576 | 100% | 90%
28 | NAVSARI(GIS)-NAVSARI I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 31.33 | 132 | 4135.56 | 2977603.2 | 2977603.2 | 100% | 90%
29 | NAVSARI(GIS)-NAVSARI II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 31.33 | 132 | 4135.56 | 2977603.2 | 2977603.2 | 100% | 90%
30 | KAWAS-VAV I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 37 | 132 | 4884 | 3516480 | 3516480 | 100% | 90%
31 | KAWAS-VAV II 220kV | INTRA | 0.022222 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 720 | 37 | 132 | 4884 | 3513891.48 | 3516480 | 99.93% | 90%
32 | KAWAS-HALDARWA I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 81 | 132 | 10692 | 7698240 | 7698240 | 100% | 90%
33 | KAWAS-HALDARWA II 220kV | INTRA | 0 | 0 | 0 | 0.13056 | 0 | 0 | 0 | 3.13 | 720 | 81 | 132 | 10692 | 7698240 | 7698240 | 100% | 90%
34 | KAKRAPAR-HALDARWA I 220kV | INTRA | 0.67847 | 0.13472 | 0 | 0.40764 | 16.28 | 3.23 | 0 | 9.78 | 716.77 | 74 | 132 | 9768 | 6842386.32 | 7001409.36 | 97.73% | 90%
35 | KAKRAPAR-HALDARWA II 220kV | INTRA | 0 | 0.15972 | 0 | 0.40764 | 0 | 3.83 | 0 | 9.78 | 716.17 | 74 | 132 | 9768 | 6995548.56 | 6995548.56 | 100% | 90%
36 | KAKRAPAR-VAV I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 43 | 132 | 5676 | 4086720 | 4086720 | 100% | 90%
37 | KAKRAPAR-VAV II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 43 | 132 | 5676 | 4086720 | 4086720 | 100% | 90%
38 | KAKRAPAR-VAPI I 220kV | INTRA | 0 | 0.045139 | 0 | 0 | 0 | 1.08 | 0 | 0 | 718.92 | 117 | 132 | 15444 | 11103000.48 | 11103000.48 | 100% | 90%
39 | KAKRAPAR-VAPI II 220kV | INTRA | 0.35903 | 0.065278 | 0 | 0 | 8.62 | 1.57 | 0 | 0 | 718.43 | 117 | 132 | 15444 | 10962305.64 | 11095432.92 | 98.8% | 90%
40 | VINDHYACHAL-SATNA I 400kV | INTRA | 0 | 1900-01-02 13:00 | 0 | 0 | 0 | 85 | 0 | 0 | 635 | 267 | 429.015 | 114547.0033 | 72737347.1009 | 72737347.1009 | 100% | 90%
41 | VINDHYACHAL-SATNA II 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 11:35 | 0 | 0 | 0 | 59.58 | 720 | 267 | 429.015 | 114547.0033 | 82473842.3821 | 82473842.3821 | 100% | 90%
42 | VINDHYACHAL-SATNA III 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 258.31 | 425.8205 | 109993.7017 | 79195465.2583 | 79195465.2583 | 100% | 90%
43 | VINDHYACHAL-NIGRIE 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 100.32 | 221.7868 | 22249.6514 | 16019749.0031 | 16019749.0031 | 100% | 90%
44 | NIGRIE-SATNA 400kV | INTRA | 0 | 1900-01-02 23:33 | 0 | 0 | 0 | 95.55 | 0 | 0 | 624.45 | 161.11 | 515 | 82971.65 | 51811646.8425 | 51811646.8425 | 100% | 90%
45 | SATNA-BINA I 400kV | INTRA | 0.15139 | 0 | 0 | 0 | 3.63 | 0 | 0 | 0 | 720 | 276 | 328.902 | 90776.9409 | 65029877.1878 | 65359397.4835 | 99.5% | 90%
46 | SATNA-BINA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 276 | 328.902 | 90776.9409 | 65359397.4835 | 65359397.4835 | 100% | 90%
47 | BINA-BINA(MP) I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.742 | 515 | 382.13 | 275133.6 | 275133.6 | 100% | 90%
48 | BINA-BINA(MP) II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.742 | 515 | 382.13 | 275133.6 | 275133.6 | 100% | 90%
49 | BINA-GWALIOR I 765kV | INTRA | 0.10694 | 0 | 0 | 0 | 2.57 | 0 | 0 | 0 | 720 | 234.931 | 867.5966 | 203825.3474 | 146230418.9585 | 146754250.1012 | 99.64% | 90%
50 | SATNA-BINA IV 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 272.586 | 325.8981 | 88835.2493 | 63961379.5041 | 63961379.5041 | 100% | 90%
51 | SATNA-BINA III 400kV | INTRA | 0 | 0 | 0 | 0.0055556 | 0 | 0 | 0 | 0.13 | 720 | 272.586 | 325.8981 | 88835.2493 | 63961379.5041 | 63961379.5041 | 100% | 90%
52 | BINA-SHUJALPUR I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 199.936 | 142.2855 | 28448.0014 | 20482560.9987 | 20482560.9987 | 100% | 90%
53 | BINA-SHUJALPUR II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 199.936 | 142.2855 | 28448.0014 | 20482560.9987 | 20482560.9987 | 100% | 90%
54 | SHUJALPUR-NAGDA I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 152.229 | 292.9847 | 44600.7689 | 32112553.6417 | 32112553.6417 | 100% | 90%
55 | SHUJALPUR-NAGDA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 152.229 | 292.9847 | 44600.7689 | 32112553.6417 | 32112553.6417 | 100% | 90%
56 | NAGDA-DEHGAM II 400KV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 331.442 | 366.6699 | 121529.8006 | 87501456.4578 | 87501456.4578 | 100% | 90%
57 | NAGDA-DEHGAM I 400KV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 331.442 | 366.6699 | 121529.8006 | 87501456.4578 | 87501456.4578 | 100% | 90%
58 | SEONI-KHANDWA I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 351.729 | 533.8287 | 187763.0449 | 135189392.3556 | 135189392.3556 | 100% | 90%
59 | SEONI-KHANDWA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 351.729 | 533.8287 | 187763.0449 | 135189392.3556 | 135189392.3556 | 100% | 90%
60 | KHANDWA-RAJGARH II 400kV | INTRA | 0.0069444 | 1900-01-06 16:43 | 0 | 1900-01-01 02:22 | 0.17 | 184.72 | 0 | 50.37 | 535.28 | 220.588 | 515 | 113602.82 | 60790005.0102 | 60809317.4896 | 99.97% | 90%
61 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | INTRA | 0 | 1900-01-05 16:55 | 0.0069444 | 1900-01-03 17:54 | 0 | 160.92 | 0.17 | 113.9 | 558.91 | 4.01 | 515 | 2065.15 | 1154232.9865 | 1154232.9865 | 100% | 90%
62 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | INTRA | 0 | 0.31597 | 0.10347 | 0 | 0 | 7.58 | 2.48 | 0 | 709.94 | 4.01 | 515 | 2065.15 | 1466132.591 | 1466132.591 | 100% | 90%
63 | RAJGARH-NAGDA I 400kV(LILO) | INTRA | 0 | 0 | 0.0069444 | 1900-01-04 18:59 | 0 | 0 | 0.17 | 138.98 | 719.83 | 4.12 | 515 | 2121.8 | 1527335.294 | 1527335.294 | 100% | 90%
64 | RAJGARH-NAGDA II 400kV(LILO) | INTRA | 0 | 0 | 0.0069444 | 1900-01-11 17:20 | 0 | 0 | 0.17 | 305.33 | 719.83 | 4.12 | 515 | 2121.8 | 1527335.294 | 1527335.294 | 100% | 90%
65 | KHANDWA-RAJGARH I 400kV | INTRA | 0 | 0 | 0 | 1900-01-05 18:13 | 0 | 0 | 0 | 162.22 | 720 | 220.588 | 515 | 113602.82 | 81794030.4 | 81794030.4 | 100% | 90%
66 | VAPI-MAGARWADA I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25.71 | 132 | 3393.72 | 2443478.4 | 2443478.4 | 100% | 90%
67 | VAPI-MAGARWADA II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25.71 | 132 | 3393.72 | 2443478.4 | 2443478.4 | 100% | 90%
68 | VAPI-KHARADPARA I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 29.66 | 132 | 3915.12 | 2818886.4 | 2818886.4 | 100% | 90%
69 | VAPI-KHARADPARA II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 29.66 | 132 | 3915.12 | 2818886.4 | 2818886.4 | 100% | 90%
70 | BINA-GWALIOR II 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 233.652 | 853.8925 | 199513.694 | 143649859.6718 | 143649859.6718 | 100% | 90%
71 | SEONI-BINA I 765kV | INTRA | 0 | 0 | 0 | 1899-12-31 08:41 | 0 | 0 | 0 | 32.68 | 720 | 292.046 | 1263.1629 | 368901.6599 | 265609195.1624 | 265609195.1624 | 100% | 90%
72 | DAMOH-BHOPAL I 400KV | INTRA | 0 | 0 | 0 | 1900-01-04 15:24 | 0 | 0 | 0 | 135.4 | 720 | 214.471 | 405.1828 | 86899.971 | 62567979.0917 | 62567979.0917 | 100% | 90%
73 | DAMOH-BHOPAL II 400KV | INTRA | 0 | 0 | 0.063194 | 0.53958 | 0 | 0 | 1.52 | 12.95 | 718.48 | 213.8 | 404.7913 | 86544.3797 | 62180405.953 | 62180405.953 | 100% | 90%
74 | VAPI-KHADOLI I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 28.549 | 132 | 3768.468 | 2713296.96 | 2713296.96 | 100% | 90%
75 | VAPI-SAYALI 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 18.3 | 132 | 2415.6 | 1739232 | 1739232 | 100% | 90%
76 | SAYALI-KHADOLI 220kV | INTRA | 0 | 0 | 0 | 1899-12-31 02:34 | 0 | 0 | 0 | 26.57 | 720 | 12.235 | 132 | 1615.02 | 1162814.4 | 1162814.4 | 100% | 90%
77 | DAMOH-BIRSINGHPUR I 400kV | INTRA | 0.040972 | 0 | 0 | 0 | 0.98 | 0 | 0 | 0 | 720 | 228.474 | 412.7548 | 94303.7428 | 67806277.119 | 67898694.7869 | 99.86% | 90%
78 | DAMOH-BIRSINGHPUR II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 228.474 | 412.7548 | 94303.7428 | 67898694.7869 | 67898694.7869 | 100% | 90%
79 | DEHGAM-PIRANA I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46.656 | 515 | 24027.84 | 17300044.8 | 17300044.8 | 100% | 90%
80 | DEHGAM-PIRANA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46.656 | 515 | 24027.84 | 17300044.8 | 17300044.8 | 100% | 90%
81 | MUNDRA-BHACHAU I 400kV | INTRA | 0.28125 | 0 | 0 | 0 | 6.75 | 0 | 0 | 0 | 720 | 99.468 | 605 | 60178.14 | 42922058.355 | 43328260.8 | 99.06% | 90%
82 | MUNDRA-BHACHAU II 400kV | INTRA | 0.28194 | 0 | 0 | 0.061111 | 6.77 | 0 | 0 | 1.47 | 720 | 99.468 | 605 | 60178.14 | 42920854.7922 | 43328260.8 | 99.06% | 90%
83 | BHACHAU-RANCHHODPURA I 400kV | INTRA | 0 | 0 | 0 | 0.33056 | 0 | 0 | 0 | 7.93 | 720 | 282.856 | 528.1603 | 149393.3178 | 107563188.7839 | 107563188.7839 | 100% | 90%
84 | BHACHAU-RANCHHODPURA II 400kV | INTRA | 0 | 0 | 0 | 0.1875 | 0 | 0 | 0 | 4.5 | 720 | 282.856 | 528.1603 | 149393.3178 | 107563188.7839 | 107563188.7839 | 100% | 90%
85 | MUNDRA-LIMBDI I 400kV | INTRA | 0 | 0 | 0 | 0.51875 | 0 | 0 | 0 | 12.45 | 720 | 314.053 | 516.9265 | 162342.3045 | 116886459.2743 | 116886459.2743 | 100% | 90%
86 | MUNDRA-LIMBDI II 400kV | INTRA | 0 | 0 | 0 | 0.27917 | 0 | 0 | 0 | 6.7 | 720 | 314.053 | 516.9265 | 162342.3045 | 116886459.2743 | 116886459.2743 | 100% | 90%
87 | SATNA-BINA I 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 274.164 | 1170.2371 | 320836.8949 | 231002564.3638 | 231002564.3638 | 100% | 90%
88 | SATNA-BINA II 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 275.635 | 1178.628 | 324871.1198 | 233907206.2244 | 233907206.2244 | 100% | 90%
89 | BINA-INDORE I 765kV | INTRA | 0 | 0 | 0 | 1899-12-31 12:34 | 0 | 0 | 0 | 36.57 | 720 | 311.81 | 1347.3419 | 420114.6841 | 302482572.5176 | 302482572.5176 | 100% | 90%
90 | GANDHAR-NAVSARI(GIS) II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 102.152 | 515 | 52608.28 | 37877961.6 | 37877961.6 | 100% | 90%
91 | GANDHAR-NAVSARI(GIS) I 400kV | INTRA | 0 | 0 | 0 | 0.70903 | 0 | 0 | 0 | 17.02 | 720 | 102.152 | 515 | 52608.28 | 37877961.6 | 37877961.6 | 100% | 90%
92 | MUNDRA-JETPUR I 400kV | INTRA | 0 | 0 | 0.66944 | 0.28403 | 0 | 0 | 16.07 | 6.82 | 703.93 | 336.742 | 523.3266 | 176226.0422 | 124050797.8648 | 124050797.8648 | 100% | 90%
93 | MUNDRA-JETPUR II 400kV | INTRA | 0 | 0 | 0.975 | 0.54653 | 0 | 0 | 23.4 | 13.12 | 696.6 | 336.742 | 523.3266 | 176226.0422 | 122759060.9757 | 122759060.9757 | 100% | 90%
94 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 28.55 | 687 | 19613.85 | 14121972 | 14121972 | 100% | 90%
95 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 28.55 | 687 | 19613.85 | 14121972 | 14121972 | 100% | 90%
96 | VINDHYACHAL(POOLING)-SASAN I 400kV | INTRA | 0.18542 | 0 | 0 | 1900-01-07 15:34 | 4.45 | 0 | 0 | 207.57 | 720 | 5.443 | 515 | 2803.145 | 2005790.4047 | 2018264.4 | 99.38% | 90%
97 | VINDHYACHAL(POOLING)-SASAN II 400kV | INTRA | 0 | 0 | 0 | 0.49167 | 0 | 0 | 0 | 11.8 | 720 | 5.443 | 515 | 2803.145 | 2018264.4 | 2018264.4 | 100% | 90%
98 | SASAN-SATNA I 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 245.7 | 1732.6455 | 425711.0001 | 306511920.0879 | 306511920.0879 | 100% | 90%
99 | BINA-BINA(MP) III 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.62 | 515 | 319.3 | 229896 | 229896 | 100% | 90%
100 | VAPI-NAVASARI(GIS) II 400kV | INTRA | 0.41042 | 0 | 0 | 0 | 9.85 | 0 | 0 | 0 | 720 | 116.879 | 515 | 60192.685 | 42745835.2528 | 43338733.2 | 98.63% | 90%
101 | SASAN-SATNA II 765kV | INTRA | 0.034722 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 720 | 242.23 | 1724.1068 | 417630.3842 | 300347243.4044 | 300693876.6233 | 99.88% | 90%
102 | BINA-BINA(MP) IV 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.62 | 515 | 319.3 | 229896 | 229896 | 100% | 90%
103 | INDORE(MP)-INDORE I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 49.73 | 687 | 34164.51 | 24598447.2 | 24598447.2 | 100% | 90%
104 | INDORE(MP)-INDORE II 400kV | INTRA | 0 | 0 | 0 | 1899-12-31 13:55 | 0 | 0 | 0 | 37.92 | 720 | 49.73 | 687 | 34164.51 | 24598447.2 | 24598447.2 | 100% | 90%
105 | JABALPUR-JABALPUR(POOLING) I 400kV | INTRA | 0 | 0 | 0 | 0.14722 | 0 | 0 | 0 | 3.53 | 720 | 15.456 | 687 | 10618.272 | 7645155.84 | 7645155.84 | 100% | 90%
106 | JABALPUR-JABALPUR(POOLING) II 400kV | INTRA | 0 | 0 | 0 | 0.056944 | 0 | 0 | 0 | 1.37 | 720 | 15.456 | 687 | 10618.272 | 7645155.84 | 7645155.84 | 100% | 90%
107 | JABALPUR(POOLING)-BINA I 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 229.74 | 809.5333 | 185982.1691 | 133907161.7556 | 133907161.7556 | 100% | 90%
108 | JABALPUR(POOLING)-BINA II 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 229.74 | 809.5333 | 185982.1691 | 133907161.7556 | 133907161.7556 | 100% | 90%
109 | SATNA-GWALIOR I 765kV | INTRA | 0 | 0 | 0 | 1900-01-01 14:52 | 0 | 0 | 0 | 62.87 | 720 | 336.63 | 1433.4388 | 482538.49 | 347427712.7812 | 347427712.7812 | 100% | 90%
110 | PIRANA-ASOJ I 400KV | INTRA | 0 | 0.0097222 | 0 | 0 | 0 | 0.23 | 0 | 0 | 719.77 | 143.539 | 687 | 98611.293 | 70977450.3626 | 70977450.3626 | 100% | 90%
111 | PIRANA-ASOJ II 400KV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 143.539 | 687 | 98611.293 | 71000130.96 | 71000130.96 | 100% | 90%
112 | NAVSARI(GIS)-KALA I 400kV | INTRA | 0 | 0 | 0 | 0.036806 | 0 | 0 | 0 | 0.88 | 720 | 140 | 515 | 72100 | 51912000 | 51912000 | 100% | 90%
113 | KALA-VAPI I 400kV | INTRA | 0 | 0 | 0 | 0.090278 | 0 | 0 | 0 | 2.17 | 720 | 49 | 515 | 25235 | 18169200 | 18169200 | 100% | 90%
114 | INDORE-ASOJ III 400kV | INTRA | 0.10556 | 0 | 0 | 1900-01-01 23:38 | 2.53 | 0 | 0 | 71.63 | 720 | 321.203 | 160.0813 | 51418.5789 | 36891287.7691 | 37021376.7736 | 99.65% | 90%
115 | BINA-GWALIOR III 765kV | INTRA | 0.10278 | 0 | 0 | 0 | 2.47 | 0 | 0 | 0 | 720 | 231.27 | 827.3453 | 191340.1495 | 137292297.4624 | 137764907.6317 | 99.66% | 90%
116 | AGRA-GWALIOR I 765kV | WR2-IR-1 | 0.049306 | 0 | 0 | 0 | 1.18 | 0 | 0 | 0 | 720 | 129.435 | 2250 | 291228.75 | 209341050.075 | 209684700 | 99.84% | 90%
117 | AGRA-GWALIOR II 765kV | WR2-IR-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 127.934 | 2250 | 287851.5 | 207253080 | 207253080 | 100% | 90%
118 | ICT1 JABALPUR 400/220kV | ICT | 0 | 0 | 0 | 0.034028 | 0 | 0 | 0 | 0.82 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
119 | ICT2 JABALPUR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
120 | ICT1 DEHGAM 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
121 | ICT2 DEHGAM 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
122 | ICT1 SATNA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
123 | ICT2 SATNA 400/220KV | ICT | 0.12639 | 0 | 0 | 0 | 3.03 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 225845.55 | 226800 | 99.58% | 90%
124 | ICT1 KHANDWA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
125 | ICT2 KHANDWA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
126 | ICT1 VAPI 400/220KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
127 | ICT2 VAPI 400/220KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
128 | ICT1 GWALIOR 400/220kV | ICT | 0.20903 | 0 | 0 | 0 | 5.02 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 225218.7 | 226800 | 99.3% | 90%
129 | ICT1 RAJGARH 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
130 | ICT2 GWALIOR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
131 | ICT ITARSI 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
132 | ICT1 DAMOH 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
133 | ICT2 DAMOH 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
134 | ICT2 RAJGARH 400/220KV | ICT | 0.46806 | 0 | 0 | 0 | 11.23 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 223262.55 | 226800 | 98.44% | 90%
135 | ICT BINA 400/220kV | ICT | 0.08125 | 0 | 0 | 0 | 1.95 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226185.75 | 226800 | 99.73% | 90%
136 | ICT1 PIRANA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
137 | ICT2 PIRANA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
138 | ICT3 GWALIOR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
139 | ICT1 SHUJALPUR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
140 | ICT1 BHACHAU 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
141 | ICT2 BHACHAU 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
142 | ICT2 SHUJALPUR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
143 | ICT1 SATNA 765/400KV | ICT | 0.22639 | 0 | 0 | 0 | 5.43 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 714570 | 720000 | 99.25% | 90%
144 | ICT2 NAVSARI(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
145 | ICT1 NAVSARI(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
146 | ICT2 SATNA 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 720000 | 720000 | 100% | 90%
147 | ICT1 BINA 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 720000 | 720000 | 100% | 90%
148 | ICT3 VAPI 400/220KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
149 | ICT2 BINA 765/400KV | ICT | 0.24931 | 0 | 0 | 0 | 5.98 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 714020 | 720000 | 99.17% | 90%
150 | ICT1 GWALIOR 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100% | 90%
151 | ICT2 GWALIOR 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100% | 90%
152 | ICT2 INDORE 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100% | 90%
153 | ICT1 INDORE 765/400KV | ICT | 0 | 0 | 0 | 0.38889 | 0 | 0 | 0 | 9.33 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100% | 90%
154 | ICT1 JABALPUR 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100% | 90%
155 | ICT2 JABALPUR 765/400KV | ICT | 0 | 0 | 0 | 0.34236 | 0 | 0 | 0 | 8.22 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100% | 90%
156 | ICT1 KALA(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
157 | ICT2 KALA(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100% | 90%
158 | BUS REACTOR I DEHGAM 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
159 | BUS REACTOR I JABALPUR 33kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25 | 1 | 25 | 18000 | 18000 | 100% | 90%
160 | BUS REACTOR II JABALPUR 33kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25 | 1 | 25 | 18000 | 18000 | 100% | 90%
161 | BUS REACTOR I ITARSI 400kV | BR | 0 | 0 | 0 | 1900-01-29 | 0 | 0 | 0 | 720 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100% | 90%
162 | BUS REACTOR II ITARSI 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100% | 90%
163 | BUS REACTOR III ITARSI 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100% | 90%
164 | BUS REACTOR I JABALPUR 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
165 | BUS REACTOR DHULE 400kV | BR | 0 | 0 | 0 | 1900-01-08 08:59 | 0 | 0 | 0 | 224.98 | 720 | 80 | 1 | 80 | 57600 | 57600 | 100% | 90%
166 | BUS REACTOR I SATNA 400kV | BR | 0 | 0 | 0 | 1899-12-31 04:44 | 0 | 0 | 0 | 28.73 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100% | 90%
167 | BUS REACTOR BINA 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
168 | BUS REACTOR DAMOH 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
169 | BUS REACTOR I GWALIOR 400kV | BR | 0 | 0 | 0 | 1900-01-28 17:35 | 0 | 0 | 0 | 713.58 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100% | 90%
170 | BUS REACTOR I KHANDWA 400kV | BR | 0 | 0 | 0 | 0.325 | 0 | 0 | 0 | 7.8 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
171 | BUS REACTOR II DEHGAM 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
172 | BUS REACTOR BHACHAU 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
173 | BUS REACTOR I SHUJALPUR 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
174 | BUS REACTOR RAJGARH 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
175 | BUS REACTOR SATNA 765kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
176 | BUS REACTOR NAVSARI 400kV | BR | 0 | 0 | 0 | 1900-01-04 02:57 | 0 | 0 | 0 | 122.95 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
177 | SWITCHABLE LINE REACTOR BINA I 765kV AT SATNA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
178 | SWITCHABLE LINE REACTOR BINA II 765kV AT SATNA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
179 | BUS REACTOR II SATNA 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
180 | SWITCHABLE LINE REACTOR BINA I 765kV AT GWALIOR | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
181 | SWITCHABLE LINE REACTOR BINA II 765kV AT GWALIOR | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
182 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT NAGDA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
183 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT NAGDA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
184 | BUS REACTOR II GWALIOR 400kV | BR | 0 | 0 | 0 | 1900-01-11 03:19 | 0 | 0 | 0 | 291.32 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
185 | BUS REACTOR III GWALIOR 400kV | BR | 0 | 0 | 0 | 0.64306 | 0 | 0 | 0 | 15.43 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
186 | BUS REACTOR I INDORE 400kV | BR | 0 | 0 | 0 | 1900-01-02 18:38 | 0 | 0 | 0 | 90.63 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
187 | SWITCHABLE LINE REACTOR INDORE 765kV AT BINA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
188 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT BINA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
189 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT BINA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
190 | BUS REACTOR I INDORE 765kV | BR | 0 | 0 | 0 | 0.5375 | 0 | 0 | 0 | 12.9 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
191 | SWITCHABLE LINE REACTOR BINA I 765kV AT JABALPUR (POOLING) | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
192 | BUS REACTOR JABALPUR(POOLING) 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
193 | BUS REACTOR BINA 765kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
194 | BUS REACTOR JABALPUR POOLING 765kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100% | 90%
195 | BUS REACTOR II KHANDWA 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
196 | BUS REACTOR II JABALPUR 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100% | 90%
197 | BUS REACTOR KALA(GIS) 400kV | BR | 0 | 0 | 0 | 1900-01-03 13:55 | 0 | 0 | 0 | 109.92 | 720 | 80 | 1 | 80 | 57600 | 57600 | 100% | 90%
198 | BUS REACTOR II INDORE 400kV | BR | 0 | 0 | 0 | 0.29653 | 0 | 0 | 0 | 7.12 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100% | 90%
| GRAND TOTAL= |  | 1900-01-04 06:26 | 1900-01-22 07:54 | 1899-12-31 19:58 | 1900-06-27 01:14 | 126.41 | 559.9 | 43.98 | 4297.25
A | AVAILABILITY OF LINES= |  |  | IR Lines | [5 empty] | ∑Wi (Ti - TNAi) = |  | 6899202266.0487
| No. of lines= O= |  | 115 | 2 | [5 empty] | (Ti x Wi) = |  | 6905799373.9451
| Line Outages Hrs = |  | 92.59 | 1.18 |  |  |  |  | AVAILABILITY OF LINES=Avo= |  |  | 99.9%
| Total Line Ckt.kM |  | 18170.507 | 257.369
B | AVAILABILITY OF ICTs= | [8 empty] | ∑Wk (Tk - TNAk) = |  | 16145902.55
| No. of ICTs= q= |  | 40 | [6 empty] | (Tk x Wk) = |  | 16164000
| ICTs Outages Hrs = |  | 32.64 | [5 empty] | AVAILABILITY OF ICTs=Avq= |  |  | 99.89%
C | AVAILABILITY OF BUS REACTORS= | [8 empty] | ∑Wm (Tm - TNAm) = |  | 3458880
| No. of Reactors= r = |  | 41 | [6 empty] | (Tm x Wm) = |  | 3458880
| Reactors Outages Hrs = |  | 0 | [5 empty] | AVAILABILITY OF BRs=Avr= |  |  | 100%
D | % TAFM OF AC SYSTEM= ( o X Avo + q X Avq + r X Avr) / (o+q+r) = | [10 empty] | 99.92%
E | AVAILABILITY OF 765KV AGRA - GWALIOR # 1 LINE= | [8 empty] | ∑Wi (Ti - TNAi) = |  | 209341050.075
| No. of lines= O= |  | 1 | [6 empty] | (Ti x Wi) = |  | 209684700
| Line Outages Hrs = |  | 1.18 | [5 empty] | AVAILABILITY OF LINES=Avo= |  |  | 99.84%
| Total Line Ckt.kM |  | 129.435
F | AVAILABILITY OF 765KV AGRA - GWALIOR # 2, 400KV ZERDA-KANKROLI, 400KV ZERDA-BHINMAL & 400KV BHINMAL-KANKROLI LINE= | [8 empty] | ∑Wi (Ti - TNAi) = |  | 207253080
| No. of lines= O= |  | 1 | [6 empty] | (Ti x Wi) = |  | 207253080
| Line Outages Hrs = |  | 0 | [5 empty] | AVAILABILITY OF LINES=Avo= |  |  | 100%
| Total Line Ckt.kM |  | 127.934
Formulas:
PG = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$J6:J219)
OTHERS = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$K6:K219)
SYSTEM = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$L6:L219)
DEEMED = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$M6:M219)

## TRIP-WR-II
L
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF JUNE -2014 | [17 empty] | O | Y
[18 empty] | S | N
|  | WRTS-II | MONTH: | 2014-06-14 |  |  |  |  | ATTRIBUTED TO ( IN HRS:MIN) | [5 empty] | UNIT OUT DUE TO TRIPPING OF LINE |  |  | D
SN | EVENT NO. | NAME OF LINE/ICT | OWNERSHIP | Cumulative Tripping till last months | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | LICENCEE | OTHERS | SYSTEM CONSTR. | DEEMED AVAILABLE | OUTAGE CATEGORY | OUTAGE CATEGORY |  | REASON | Tripping Code | Charging Code
1 | 903002 | BUS REACTOR I GWALIOR 400kV | WRTS-II | 1 | 2014-03-01 | 15:59 | 2014-06-30 | 16:02 | 0 | 0 | 0 | 1900-01-28 16:02 | D | SCSD | N | Reactor H/T to avail OCC Approved S/D for replacement of existing 50MVAR reactor with new 125MVAR Reactor. | LD 03/69 | LD 06/3310
2 | 904082 | BUS REACTOR I ITARSI 400kV | WRTS-II | 1 | 2014-04-20 | 13:30 |  |  | 0 | 0 | 0 | 1900-01-29 | D | SCSD | N | Reactor H/T to avail OCC Approved S/D for replacement of existing 50MVAR reactor with new 125MVAR Reactor. | LD 04/2036
3 | 905164 | KHANDWA-RAJGARH II 400kV | WRTS-II | 1 | 2014-05-26 | 09:34 | 2014-06-01 | 09:32 | 0 | 0 | 0 | 0.39722 | D | LPRD | N | Line H/T for Power Regulation on WRLDC Instruction. | LD 05/2825 | LD 06/34
4 | 905183 | KHANDWA-RAJGARH I 400kV | WRTS-II | 1 | 2014-05-29 | 10:20 | 2014-06-02 | 20:14 | 0 | 0 | 0 | 1899-12-31 20:14 | D | OSPD | N | Line H/T to avail S/D for Line Crossing works by MPPTCL. | LD 05/3189 | LD 06/219
5 | 905187 | BUS REACTOR NAVSARI 400kV | WRTS-II | 1 | 2014-05-29 | 12:33 | 2014-06-01 | 17:28 | 0 | 0 | 0 | 0.72778 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 05/3210 | LD 06/65
6 | 906001 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | WRTS-II | 1 | 2014-06-01 | 17:03 | 2014-06-01 | 19:32 | 0 | 0 | 0.10347 | 0 | S | GOVC | N | A/T on operation of O/V stage - I protection at SSP end. |  | LD 06/73
7 | 906002 | KHANDWA-RAJGARH II 400kV | WRTS-II | 1 | 2014-06-01 | 17:12 | 2014-06-09 | 09:55 | 0 | 1900-01-06 16:43 | 0 | 0 | O | OMSU | N | Line A/T due to collapse of crossing towers of 400 kV Chegaon-Julvania (MPEB Line) under construction, due to heavy storm in the region. |  | LD 06/808
8 | 906003 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | WRTS-II | 1 | 2014-06-01 | 20:07 | 2014-06-01 | 20:07 | 0 | 0 | 0 | 0 | L | LART | N | Line successfully A/R on R-ph to E/F, F/L- 03 km and F/C- 4.7 kA from Rajgarh end.
9 | 906004 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-02 | 09:11 | 2014-06-02 | 18:55 | 0 | 0 | 0 | 0.40556 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/127 | LD 06/213
10 | 906005 | MUNDRA-BHACHAU I 400kV | WRTS-II | 1 | 2014-06-02 | 10:06 | 2014-06-02 | 16:51 | 0.28125 | 0 | 0 | 0 | L | OSPT | N | Line H/T to avail OCC Approved S/D for attending Hot Spot. | LD 06/135 | LD 06/182
11 | 906006 | VINDHYACHAL-SATNA II 400kV | WRTS-II | 1 | 2014-06-02 | 10:15 | 2014-06-02 | 19:15 | 0 | 0 | 0 | 0.375 | D | SCSD | N | Line H/T to avail OCC Approved S/D for commissioning of CSD relay at Satna. | LD 06/133 | LD 06/211
12 | 906007 | INDORE-ASOJ I 400kV | WRTS-II | 1 | 2014-06-02 | 16:02 | 2014-06-02 | 16:02 | 0 | 0 | 0 | 0 | L | LART | N | Line A/R successfully at both ends on Y-ph to E/F, F/L 130.9kms from Indore & 193kms from Asoj. F/C- 1.57 Ka.
13 | 906008 | KHANDWA-DHULE I 400kV | WRTS-II | 1 | 2014-06-02 | 16:07 | 2014-06-02 | 16:07 | 0 | 0 | 0 | 0 | L | LART | N | Line A/R Successfully at Khandwa end only on R-ph to E/F. F/L - 117kms from Khandwa, F/C- 2.03 kA. A/R failed at Dhule end.
14 | 906009 | KHANDWA-DHULE I 400kV | WRTS-II | 1 | 2014-06-02 | 16:07 | 2014-06-02 | 16:36 | 0 | 0.020139 | 0 | 0 | O | OMSU | N | AR attempt failed at Dhule due to some problem at Dhule(MSEB) end. |  | LD 06/183
15 | 906010 | INDORE-ASOJ III 400kV | WRTS-II | 1 | 2014-06-02 | 16:44 | 2014-06-02 | 18:36 | 0.077778 | 0 | 0 | 0 | L | LEFT | N | Line A/T on R-ph to E/F, F/L - 271.82kms from Indore. F/C - 1.43kAmp. |  | LD 06/193
16 | 906011 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | WRTS-II | 1 | 2014-06-02 | 17:35 | 2014-06-02 | 17:35 | 0 | 0 | 0 | 0 | O | OMSU | N | Line A/R successfully at both ends on R-ph to E/F. F/L - 71kms from Rajgarh & 111kms from SSP end. Fault section lies beyond the jourisdiction of POWERGRID.
17 | 906012 | BINA-GWALIOR I 765kV | WRTS-II | 1 | 2014-06-02 | 17:44 | 2014-06-02 | 19:17 | 0.064583 | 0 | 0 | 0 | L | OMST | N | Line H/T to avail S/D for swapping of R-ph Unit with Spare one due to DGA violation in Bushing. | WR 06/191 NLD 06/22 | WR 06/210 NLD 06/25
18 | 906013 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | WRTS-II | 1 | 2014-06-02 | 17:56 | 2014-06-09 | 10:51 | 0 | 1900-01-05 16:55 | 0 | 0 | O | OMSU | N | Line A/R successfully at both ends on R-ph to E/F. F/L - 70kms from Rajgarh. Fault section lies beyond the jourisdiction of POWERGRID. |  | LD 06//821
19 | 906014 | INDORE-ASOJ II 400kV | WRTS-II | 1 | 2014-06-02 | 18:18 | 2014-06-02 | 19:08 | 0.034722 | 0 | 0 | 0 | L | LEFT | N | Line A/T on Y-ph to E/F, F/L - 153kms from Asoj. F/C - 1.53kamp. |  | LD 06/207
20 | 906015 | VINDHYACHAL-SATNA I 400kV | WRTS-II | 1 | 2014-06-03 | 09:47 | 2014-06-06 | 22:47 | 0 | 1900-01-02 13:00 | 0 | 0 | O | OMSU | N | H/T to avail OCC S/D by NTPC VSTPP for Retrofitting of Numerical Distance Protection relays (Main-I and II) at VSTPP end. | LD 06/248 | LD 06/635
21 | 906016 | MUNDRA-BHACHAU II 400kV | WRTS-II | 1 | 2014-06-03 | 10:42 | 2014-06-03 | 17:28 | 0.28194 | 0 | 0 | 0 | L | OSPT | N | Line H/T to avail OCC Approved S/D for attending Hot Spot. | LD 06/255 | LD 06/292
22 | 906017 | ICT1 JABALPUR 400/220kV | WRTS-II | 1 | 2014-06-03 | 19:40 | 2014-06-03 | 20:29 | 0 | 0 | 0 | 0.034028 | D | SPRD | N | ICT H/T for power regulation on WRLDC instructions. | LD 06/312 | LD 06/319
23 | 906018 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-04 | 09:52 | 2014-06-04 | 17:25 | 0 | 0 | 0 | 0.31458 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/356 | LD 06/407
24 | 906019 | MUNDRA-LIMBDI I 400kV | WRTS-II | 1 | 2014-06-05 | 11:40 | 2014-06-05 | 19:45 | 0 | 0 | 0 | 0.33681 | D | OSPD | N | Line H/T to avail OCC approved S/D by CGPL. | LD 06/466 | LD 06/525
25 | 906020 | INDORE-ASOJ II 400kV | WRTS-II | 1 | 2014-06-05 | 17:47 | 2014-06-05 | 17:47 | 0 | 0 | 0 | 0 | L | LART | N | Line A/R successfully at both ends on R-ph to E/F, F/L - 249kms from Asoj. F/C -1.4kAmp.
26 | 906021 | NAGDA-DEHGAM I 400KV | WRTS-II | 1 | 2014-06-05 | 18:00 | 2014-06-05 | 18:00 | 0 | 0 | 0 | 0 | L | LART | N | Line A/R successfully at both ends on B-ph to E/F, F/L - 299kms from Dehgam. F/C -1.459 kAmp.
27 | 906022 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-06 | 09:20 | 2014-06-06 | 17:56 | 0 | 0 | 0 | 0.35833 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/559 | LD 06/612
28 | 906023 | ICT2 SATNA 400/220KV | WRTS-II | 1 | 2014-06-06 | 10:36 | 2014-06-06 | 13:38 | 0.12639 | 0 | 0 | 0 | L | OSPT | N | H/T to avail OCC approved S/D by Powergrid for AMP work. | LD 06/568 | LD 06/586
29 | 906024 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-07 | 08:15 | 2014-06-07 | 18:25 | 0 | 0 | 0 | 0.42361 | D | OSPD | N | Line H/T to avail OCC Approved S/D by CGPL for insulator replacement & maintenance work at CGPL mundra end. | LD 06/653 | LD 06/691
30 | 906025 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-07 | 10:26 | 2014-06-07 | 18:13 | 0 | 0 | 0 | 0.32431 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/658 | LD 06/693
31 | 906026 | BINA-GWALIOR III 765kV | WRTS-II | 1 | 2014-06-07 | 11:02 | 2014-06-07 | 13:30 | 0.10278 | 0 | 0 | 0 | L | OSPT | N | Line H/T to avail S/D for attending hot spot in R-ph wave trap at Bina end. | WR 06/659 NLD 06/92 | WR 06/672 NLD 06/95
32 | 906027 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-08 | 08:45 | 2014-06-08 | 17:29 | 0 | 0 | 0 | 0.36389 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/730 | LD 06/764
33 | 906028 | JABALPUR-ITARSI I 400kV | WRTS-II | 1 | 2014-06-08 | 09:15 | 2014-06-10 | 15:33 | 0 | 0 | 0 | 1900-01-01 06:18 | D | OSPD | N | Line H/T to avail OCC Approved S/D by Sterlite for crossing work of 765kV Jabalpur - Bina Line. | LD 06/731 | LD 06/976
34 | 906029 | JABALPUR-ITARSI II 400kV | WRTS-II | 1 | 2014-06-08 | 09:16 | 2014-06-10 | 15:40 | 0 | 0 | 0 | 1900-01-01 06:24 | D | OSPD | N | Line H/T to avail OCC Approved S/D by Sterlite for crossing work of 765kV Jabalpur - Bina Line. | LD 06/731 | LD 06/980
35 | 906030 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-09 | 09:26 | 2014-06-09 | 17:14 | 0 | 0 | 0 | 0.325 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/805 | LD 06/859
36 | 906031 | BUS REACTOR KALA(GIS) 400kV | WRTS-II | 1 | 2014-06-09 | 10:08 | 2014-06-09 | 18:34 | 0 | 0 | 0 | 0.35139 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/810 | LD 06/881
37 | 906032 | BUS REACTOR NAVSARI 400kV | WRTS-II | 1 | 2014-06-09 | 10:20 | 2014-06-09 | 18:30 | 0 | 0 | 0 | 0.34028 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/810 | LD 06/880
38 | 906033 | BUS REACTOR I KHANDWA 400kV | WRTS-II | 1 | 2014-06-09 | 10:22 | 2014-06-09 | 18:10 | 0 | 0 | 0 | 0.325 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/815 | LD 06/873
39 | 906034 | BUS REACTOR I INDORE 400kV | WRTS-II | 1 | 2014-06-09 | 11:15 | 2014-06-09 | 18:18 | 0 | 0 | 0 | 0.29375 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/828 | LD 06/872
40 | 906035 | BUS REACTOR II INDORE 400kV | WRTS-II | 1 | 2014-06-09 | 11:15 | 2014-06-09 | 18:22 | 0 | 0 | 0 | 0.29653 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/826 | LD 06/878
41 | 906036 | BUS REACTOR II GWALIOR 400kV | WRTS-II | 1 | 2014-06-09 | 11:29 | 2014-06-09 | 17:51 | 0 | 0 | 0 | 0.26528 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/828 | LD 06/863
42 | 906037 | BUS REACTOR III GWALIOR 400kV | WRTS-II | 1 | 2014-06-09 | 11:29 | 2014-06-09 | 18:02 | 0 | 0 | 0 | 0.27292 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/828 | LD 06/868
43 | 906038 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-10 | 08:56 | 2014-06-10 | 18:30 | 0 | 0 | 0 | 0.39861 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/928 | LD 06/997
44 | 906039 | BUS REACTOR I INDORE 765kV | WRTS-II | 1 | 2014-06-10 | 10:44 | 2014-06-10 | 19:00 | 0 | 0 | 0 | 0.34444 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/940 LD 06/141 | LD 06/1001 LD 06/153
45 | 906040 | ICT2 RAJGARH 400/220KV | WRTS-II | 1 | 2014-06-10 | 11:45 | 2014-06-10 | 13:32 | 0.074306 | 0 | 0 | 0 | L | OSPT | N | H/T to avail S/D by PG for attending oil Leakage in B-ph 220kV side Bushing. | LD 06/952 | LD 06/963
46 | 906041 | KAKRAPAR-HALDARWA I 220kV | WRTS-II | 1 | 2014-06-10 | 14:58 | 2014-06-10 | 18:12 | 0 | 0.13472 | 0 | 0 | O | OMSU | N | H/T as per WRLDC instructions for installation of PMU at Haldarwa s/s.. | LD 06/971 | LD 06/994
47 | 906042 | SASAN-JABALPUR 400kV | WRTS-II | 1 | 2014-06-10 | 16:33 | 2014-06-10 | 16:43 | 0.0069444 | 0 | 0 | 0 | L | LEFT | N | A/T on R-ph to E/F from both ends, F/L - 356.8km from Jabalpur & 13.03km from Sasan. Test charging delayed by SASAN end.
48 | 906043 | SASAN-JABALPUR 400kV | WRTS-II | 1 | 2014-06-10 | 16:43 | 2014-06-10 | 17:38 | 0 | 0.038194 | 0 | 0 | O | OMSU | N | As Line tripped on R-ph to E/F (1-ph transeint fault), Test charging delayed by SASAN end. |  | LD 06/987
49 | 906044 | INDORE-ASOJ III 400kV | WRTS-II | 1 | 2014-06-11 | 07:50 | 2014-06-12 | 18:18 | 0 | 0 | 0 | 1899-12-31 10:28 | D | LCSD | N | H/T to avail S/D by PG for completion of stringing work in double circuit portion. | LD 06/1029 | LD 06/1244
50 | 906045 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-11 | 09:25 | 2014-06-11 | 17:07 | 0 | 0 | 0 | 0.32083 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1045 | LD 06/1085
51 | 906046 | VINDHYACHAL-SATNA II 400kV | WRTS-II | 1 | 2014-06-11 | 11:57 | 2014-06-13 | 14:32 | 0 | 0 | 0 | 1900-01-01 02:35 | D | OSPD | N | H/T to avail S/D by NTPC VSTPP. | LD 06/1063 | LD 06/1334
52 | 906047 | ICT2 BINA 765/400KV | WRTS-II | 1 | 2014-06-11 | 15:24 | 2014-06-11 | 21:23 | 0.24931 | 0 | 0 | 0 | L | OMST | N | S/D availed by Powergrid for swapping R phase unit with spare unit . | LD 06/1073 LD 06/157 | LD 06/1120 LD 06/162
53 | 906048 | RAJGARH-NAGDA I 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:05 | 2014-06-11 | 17:15 | 0 | 0 | 0.0069444 | 0 | S | GOVC | N | A/T on operation of O/V stage - I protection at Rajgarh end.
54 | 906049 | RAJGARH-NAGDA I 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:15 | 2014-06-17 | 12:14 | 0 | 0 | 0 | 1900-01-04 18:59 | D | LVRD | N | Line kept out on Voltage regulation on WRLDC instructions. |  | LD 06/1766
55 | 906050 | RAJGARH-NAGDA II 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:34 | 2014-06-11 | 17:44 | 0 | 0 | 0.0069444 | 0 | S | GOVC | N | A/T on operation of O/V stage - I protection at Rajgarh end.
56 | 906051 | RAJGARH-NAGDA II 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:44 | 2014-06-24 | 11:04 | 0 | 0 | 0 | 1900-01-11 17:20 | D | LVRD | N | Line kept out on Voltage regulation on WRLDC instructions. |  | LD 06/2582
57 | 906052 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:46 | 2014-06-11 | 17:56 | 0 | 0 | 0.0069444 | 0 | S | GOVC | N | A/T on operation of O/V stage - I protection at Rajgarh end.
58 | 906053 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:56 | 2014-06-11 | 17:56 | 0 | 0 | 0 | 0 | O | OMSU | N | A/R successfully from both ends on B-ph to E/F, F/L - 145km from Rajgarh. Fault section lies beyond the jourisdiction of POWERGRID.
59 | 906054 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:56 | 2014-06-16 | 11:50 | 0 | 0 | 0 | 1900-01-03 17:54 | D | LVRD | N | Line kept out on Voltage regulation on WRLDC instructions. |  | LD 06/1655
60 | 906055 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 17:59 | 2014-06-11 | 17:59 | 0 | 0 | 0 | 0 | O | OMSU | N | A/R successfully from both ends on B-ph to E/F, F/L - 140km from Rajgarh. Fault section lies beyond the jourisdiction of POWERGRID.
61 | 906056 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | WRTS-II | 1 | 2014-06-11 | 18:00 | 2014-06-11 | 18:46 | 0 | 0.031944 | 0 | 0 | O | OMSU | N | A/T on reciept of D/T from SSP end. |  | LD 06/1101
62 | 906057 | DAMOH-BHOPAL I 400KV | WRTS-II | 1 | 2014-06-11 | 18:07 | 2014-06-17 | 09:31 | 0 | 0 | 0 | 1900-01-04 15:24 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/1096 | LD 06/1746
63 | 906058 | DAMOH-BHOPAL II 400KV | WRTS-II | 1 | 2014-06-11 | 18:07 | 2014-06-11 | 19:38 | 0 | 0 | 0.063194 | 0 | S | GOVC | N | A/T on operation of O/V stage - I protection at Damoh end. |  | LD 06/1112
64 | 906059 | KHANDWA-RAJGARH II 400kV | WRTS-II | 1 | 2014-06-11 | 18:21 | 2014-06-11 | 18:31 | 0.0069444 | 0 | 0 | 0 | L | LEFT | N | A/T on R-ph to E/F from both ends, F/L - 125.4km from Khandwa.Test charging delayed due to persisiting of high voltage.
65 | 906060 | KHANDWA-RAJGARH II 400kV | WRTS-II | 1 | 2014-06-11 | 18:31 | 2014-06-11 | 19:33 | 0 | 0 | 0 | 0.043056 | D | LVRD | N | Line kept out on Voltage regulation on WRLDC instructions. |  | LD 06/1111
66 | 906061 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-12 | 09:20 | 2014-06-12 | 18:18 | 0 | 0 | 0 | 0.37361 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1166 | LD 06/1243
67 | 906062 | KAKRAPAR-HALDARWA II 220kV | WRTS-II | 1 | 2014-06-12 | 12:42 | 2014-06-12 | 16:32 | 0 | 0.15972 | 0 | 0 | O | OMSU | N | Line H/T to avail S/D by Getco. | LD 06/1194 | LD 06/1217
68 | 906063 | INDORE(MP)-INDORE II 400kV | WRTS-II | 1 | 2014-06-12 | 12:58 | 2014-06-12 | 13:50 | 0 | 0 | 0 | 0.036111 | D | OSFD | N | Line H/T in emergency to attend Hot spot & continuos sparking in Y ph isolator at Indore MPPTCL end. | LD 06/1199 | LD 06/1203
69 | 906064 | BUS REACTOR KALA(GIS) 400kV | WRTS-II | 1 | 2014-06-12 | 14:45 | 2014-06-14 | 02:11 | 0 | 0 | 0 | 1899-12-31 11:26 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1210 | LD 06/1397
70 | 906065 | BUS REACTOR NAVSARI 400kV | WRTS-II | 1 | 2014-06-12 | 14:46 | 2014-06-13 | 00:58 | 0 | 0 | 0 | 0.425 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1210 | LD 06/1284
71 | 906066 | BINA-GWALIOR I 765kV | WRTS-II | 1 | 2014-06-12 | 15:51 | 2014-06-12 | 16:52 | 0.042361 | 0 | 0 | 0 | L | OSPT | N | H/T to avail S/D for replacement of L/R Y phase unit with spare unit at Bina end. | LD 06/1215 NLDC 167 | LD 06/1234 NLDC 172
72 | 906067 | AGRA-GWALIOR I 765kV | WRTS-II | 1 | 2014-06-12 | 18:29 | 2014-06-12 | 19:40 | 0.049306 | 0 | 0 | 0 | L | OSFT | N | H/T to avail emergency S/D for attending Hot spot in B phase Line isolator at Agra SS. | LD 06/1250 NRLDC 738 NLDC 174 | LD 06/1260 NRLDC 750 NLDC 178
73 | 906068 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-13 | 09:25 | 2014-06-13 | 18:26 | 0 | 0 | 0 | 0.37569 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1311 | LD 06/1364
74 | 906069 | NIGRIE-SATNA 400kV | WRTS-II | 1 | 2014-06-13 | 18:18 | 2014-06-14 | 16:34 | 0 | 0.92778 | 0 | 0 | O | OMSU | N | Line A/T on Y ph to E/F during installation of OPGW by JP Power in LILO portion owned by JP Power. |  | LD 06/1462
75 | 906070 | KAWAS-VAV II 220kV | WRTS-II | 1 | 2014-06-14 | 00:57 | 2014-06-14 | 01:29 | 0.022222 | 0 | 0 | 0 | L | LEFT | N | Line A/T on B ph to E/F, 28.16km from Vav, F/C: 4.97kA, 6km from Kawas. |  | LD 06/1394
76 | 906071 | KAKRAPAR-VAPI II 220kV | WRTS-II | 1 | 2014-06-14 | 04:21 | 2014-06-14 | 04:53 | 0.022222 | 0 | 0 | 0 | L | LHWT | N | Line A/T on R ph to E/F, F/L 15.16km from Vapi, due to failure of R phase insulator string at location no. 335. |  | LD 06/1401
77 | 906072 | KALA-VAPI I 400kV | WRTS-II | 1 | 2014-06-14 | 05:26 | 2014-06-14 | 06:05 | 0 | 0 | 0 | 0.027083 | D | LCSD | N | Line A/T on Y ph to E/F, F/L 45.7km from Vapi. F/C:5.6kA// 8.97km from Kala, due to hanging of PP rope at location no. 43/0 used for OPGW installation work for ULDC work. |  | LD 06/1404
78 | 906073 | KALA-VAPI I 400kV | WRTS-II | 1 | 2014-06-14 | 09:35 | 2014-06-14 | 10:13 | 0 | 0 | 0 | 0.026389 | D | LCSD | N | Line A/T on Y-ph to E/F, F/L - 45kms from Vapi end. F/C - 5.6kAmp, due to hanging of PP rope location no. 43/0 used for OPGW installation work for ULDC work. |  | LD 06/1431
79 | 906074 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-14 | 09:41 | 2014-06-14 | 17:34 | 0 | 0 | 0 | 0.32847 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1426 | LD 06/1475
80 | 906075 | KAKRAPAR-VAPI II 220kV | WRTS-II | 1 | 2014-06-14 | 13:59 | 2014-06-14 | 22:04 | 0.33681 | 0 | 0 | 0 | L | OSPT | N | Line H/T to avail S/D for replacement of flashed over insulator of R phase at Location no 335. | LD 06/1451 | LD 06/1495
81 | 906076 | KAWAS-HALDARWA II 220kV | WRTS-II | 1 | 2014-06-14 | 14:28 | 2014-06-14 | 17:36 | 0 | 0 | 0 | 0.13056 | D | OSPD | N | Line H/T to avail S/D by GETCO | LD 06/1428 | LD 06/1474
82 | 906077 | SASAN-SATNA II 765kV | WRTS-II | 1 | 2014-06-14 | 14:37 | 2014-06-14 | 15:27 | 0.034722 | 0 | 0 | 0 | L | LEFT | N | Line A/T on Y-ph to E/F, F/L - 100% from Sasan & Satna - Nil |  | WR 06/1459 NLD 06/196
83 | 906078 | KALA-VAPI I 400kV | WRTS-II | 1 | 2014-06-14 | 15:05 | 2014-06-14 | 15:58 | 0 | 0 | 0 | 0.036806 | D | LCSD | N | Line H/T to avail S/D for removal of Quad rope layed for installation of OPGW for ULDC system. | LD 06/1457 | LD 06/1464
84 | 906079 | NAVSARI(GIS)-KALA I 400kV | WRTS-II | 1 | 2014-06-14 | 15:05 | 2014-06-14 | 15:58 | 0 | 0 | 0 | 0.036806 | D | LCSD | N | Line H/T to avail S/D for removal of Quad rope layed for installation of OPGW, of 400kV Kala - vapi # 1 on multicircuit tower. | LD 06/1458 | LD 06/1465
85 | 906080 | SASAN-JABALPUR 400kV | WRTS-II | 1 | 2014-06-14 | 16:46 | 2014-06-14 | 21:59 | 0.21736 | 0 | 0 | 0 | L | OSPT | N | Line H/T to avail S/D for rectification of jumper at location no. 80. | LD 06/1471 | LD 06/1496
86 | 906081 | DAMOH-BIRSINGHPUR I 400kV | WRTS-II | 1 | 2014-06-14 | 17:11 | 2014-06-14 | 18:10 | 0.040972 | 0 | 0 | 0 | L | LEFT | N | Line A/T at both ends on Y-ph to E/F, F/L - 137kms from Damoh. |  | LD 06/1479
87 | 906082 | NIGRIE-SATNA 400kV | WRTS-II | 1 | 2014-06-14 | 17:54 | 2014-06-15 | 06:42 | 0 | 0.53333 | 0 | 0 | O | OMSU | N | Line A/T on Y-ph to E/F, due to problem in ongoing OPGW work by JP Power in their LILO section. |  | LD 06/1525
88 | 906083 | KHANDWA-RAJGARH I 400kV | WRTS-II | 1 | 2014-06-14 | 18:18 | 2014-06-15 | 06:24 | 0 | 0 | 0 | 0.50417 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/1483 | LD 06/1522
89 | 906084 | JABALPUR-JABALPUR(POOLING) I 400kV | WRTS-II | 1 | 2014-06-15 | 03:39 | 2014-06-15 | 04:35 | 0 | 0 | 0 | 0.038889 | D | LCSD | N | Line A/T on Y&B phase phase fault . F/L - 13.33kms from Jabalpur due to hanging of PP rope at location no. AP2/0-AP2/1 used for OPGW installation for ULDC Work. |  | LD 06/1515
90 | 906085 | GANDHAR-NAVSARI(GIS) I 400kV | WRTS-II | 1 | 2014-06-15 | 04:21 | 2014-06-15 | 05:33 | 0 | 0 | 0 | 0.05 | D | LCSD | N | Line A/T on R&Y phase to phase fault. F/L 2.48kms from Navsari. F/L - 10.0kAmp., due to hanging of PP rope used for OPGW installation for ULDC work between location no.279-281. |  | LD 06/1519
91 | 906086 | KAKRAPAR-HALDARWA I 220kV | WRTS-II | 1 | 2014-06-15 | 05:53 | 2014-06-15 | 22:10 | 0.67847 | 0 | 0 | 0 | L | LHWT | N | Line A/T on R-ph to E/F, F/L - 6.5kms from Haldarwa due to failure of insulator string at Location no. 204. |  | LD 06/1599
92 | 906087 | ICT2 RAJGARH 400/220KV | WRTS-II | 1 | 2014-06-15 | 07:08 | 2014-06-15 | 16:35 | 0.39375 | 0 | 0 | 0 | L | OSPT | N | S/D availed for replacement of 220kV side B-ph Bushing due to high Tan delta value. | LD 06/1529 | LD 06/1570
93 | 906088 | SATNA-BINA I 400kV | WRTS-II | 1 | 2014-06-15 | 09:50 | 2014-06-15 | 13:28 | 0.15139 | 0 | 0 | 0 | L | OSPT | N | S/D availed for rectification of failed inner V string at location no. 483. | LD 06/1541 | LD 06/1557
94 | 906089 | JABALPUR-JABALPUR(POOLING) I 400kV | WRTS-II | 1 | 2014-06-15 | 10:36 | 2014-06-15 | 11:34 | 0 | 0 | 0 | 0.040278 | D | LCSD | N | S/D availed for replacement work of PP rope used for OPGW installation for ULDC work. | LD 06/1543 | LD 06/1554
95 | 906090 | GANDHAR-NAVSARI(GIS) I 400kV | WRTS-II | 1 | 2014-06-15 | 12:37 | 2014-06-15 | 14:03 | 0 | 0 | 0 | 0.059722 | D | LCSD | N | A/T on Y&B phase to phase fault, F/L 36KM from Navsari due to hanging of PP rope between location no. 279-281 during OPGW installation for ULDC work. |  | LD 06/1559
96 | 906091 | ITARSI-KHANDWA I 400kV | WRTS-II | 1 | 2014-06-15 | 17:21 | 2014-06-16 | 08:36 | 0 | 0 | 0 | 0.63542 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/1577 | LD 06/1630
97 | 906092 | GANDHAR-NAVSARI(GIS) I 400kV | WRTS-II | 1 | 2014-06-16 | 03:43 | 2014-06-16 | 18:06 | 0 | 0 | 0 | 0.59931 | D | LCSD | N | A/T on Y&R phase to phase fault, F/L 37.7 KM F/c- 4.7 kA from Navsari end due to hanging of PP rope at location no. 183 used for OPGW installation work for ULDC. |  | LD 06/1692
98 | 906093 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-16 | 09:50 | 2014-06-16 | 18:04 | 0 | 0 | 0 | 0.34306 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1642 | LD 06/1694
99 | 906094 | BUS REACTOR I SATNA 400kV | WRTS-II | 1 | 2014-06-16 | 11:15 | 2014-06-17 | 15:59 | 0 | 0 | 0 | 1899-12-31 04:44 | D | SCSD | N | Reactor H/T to avail OCC Approved S/D for commissioning of CSD relay at Satna. | LD 06/1653 | LD 06/1785
100 | 906095 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | WRTS-II | 1 | 2014-06-16 | 12:16 | 2014-06-16 | 19:05 | 0 | 0.28403 | 0 | 0 | O | OMSU | N | Line H/T to avail S/D by MPPTCL. | LD 06/1661 | LD 06/1704
101 | 906096 | MUNDRA-LIMBDI II 400kV | WRTS-II | 1 | 2014-06-16 | 18:30 | 2014-06-16 | 18:30 | 0 | 0 | 0 | 0 | L | LART | N | Line A/R successfully at both ends on Y-ph to E/F, F/L - 89.5 kms from Limbdi, F/C:4.2KA & 231KM from Mundra.
102 | 906097 | KHANDWA-RAJGARH I 400kV | WRTS-II | 1 | 2014-06-16 | 22:04 | 2014-06-17 | 07:08 | 0 | 0 | 0 | 0.37778 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/1717 | LD 06/1733
103 | 906098 | NIGRIE-SATNA 400kV | WRTS-II | 1 | 2014-06-16 | 23:36 | 2014-06-17 | 20:58 | 0 | 0.89028 | 0 | 0 | O | OMSU | N | A/T on Y-ph To E/F , F/L- 160 km , F/C- 2.6 KA from Satna end. Fault pertains to LILO section of the line pertaining to JP power. |  | LD 06/1819
104 | 906099 | KAKRAPAR-HALDARWA I 220kV | WRTS-II | 1 | 2014-06-17 | 10:23 | 2014-06-17 | 20:10 | 0 | 0 | 0 | 0.40764 | D | OSPD | N | H/T to avail S/D by GETCO for Line crossing work. | LD 06/1754 | LD 06/1813
105 | 906100 | KAKRAPAR-HALDARWA II 220kV | WRTS-II | 1 | 2014-06-17 | 10:24 | 2014-06-17 | 20:11 | 0 | 0 | 0 | 0.40764 | D | OSPD | N | H/T to avail S/D by GETCO for Line crossing work. | LD 06/1754 | LD 06/1813
106 | 906101 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-17 | 10:35 | 2014-06-17 | 17:57 | 0 | 0 | 0 | 0.30694 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1756 | LD 06/1800
107 | 906102 | BUS REACTOR II GWALIOR 400kV | WRTS-II | 1 | 2014-06-17 | 12:19 | 2014-06-22 | 01:25 | 0 | 0 | 0 | 1900-01-03 13:06 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1768
108 | 906103 | VINDHYACHAL-JABALPUR I 400kV | WRTS-II | 1 | 2014-06-17 | 16:11 | 2014-06-17 | 16:28 | 0.011806 | 0 | 0 | 0 | L | LPPT | N | A/T on R&B ph to E/F, F/L - 144.7km from Jabalpur & 210kms from VSTPP, Test charging delyed by NTPC VSTPP due to isolator problem. |  | LD 06/1790
109 | 906104 | VINDHYACHAL-JABALPUR II 400kV | WRTS-II | 1 | 2014-06-17 | 16:11 | 2014-06-17 | 16:11 | 0 | 0 | 0 | 0 | L | LART | N | A/R successfully from both ends on R-ph to E/F, F/L - 150.3kms from Jabalpur & 192.8kms from VSTPP.
110 | 906105 | VINDHYACHAL-JABALPUR I 400kV | WRTS-II | 1 | 2014-06-17 | 16:28 | 2014-06-17 | 20:56 | 0 | 0.18611 | 0 | 0 | O | OMSU | N | After tripping of Line on R&B ph to E/F, Test charging delyed by NTPC VSTPP due to isolator problem. |  | LD 06/1890
111 | 906106 | DAMOH-BHOPAL II 400KV | WRTS-II | 1 | 2014-06-17 | 20:07 | 2014-06-17 | 20:07 | 0 | 0 | 0 | 0 | L | LART | N | A/R successfully from both ends on R-ph to E/F, F/L - 154.9kms from Damoh.
112 | 906107 | KHANDWA-RAJGARH I 400kV | WRTS-II | 1 | 2014-06-18 | 04:14 | 2014-06-19 | 12:22 | 0 | 0 | 0 | 1899-12-31 08:08 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/1851 | LD 06/1987
113 | 906108 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-18 | 09:01 | 2014-06-18 | 18:03 | 0 | 0 | 0 | 0.37639 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1872 | LD 06/1929
114 | 906109 | BUS REACTOR KALA(GIS) 400kV | WRTS-II | 1 | 2014-06-18 | 10:11 | 2014-06-21 | 04:14 | 0 | 0 | 0 | 1900-01-01 18:03 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1885 | LD 06/2172
115 | 906110 | BUS REACTOR NAVSARI 400kV | WRTS-II | 1 | 2014-06-18 | 10:14 | 2014-06-22 | 01:21 | 0 | 0 | 0 | 1900-01-02 15:07 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1886
116 | 906111 | GANDHAR-HALDARWA I 220kV | WRTS-II | 1 | 2014-06-18 | 10:16 | 2014-06-18 | 16:32 | 0 | 0 | 0 | 0.26111 | D | OSPD | N | H/T to avail OCC S/D by by GETCO. | LD 06/1873 | LD 06/1913
117 | 906112 | ICT BINA 400/220kV | WRTS-II | 1 | 2014-06-18 | 10:39 | 2014-06-18 | 12:36 | 0.08125 | 0 | 0 | 0 | L | OSPT | N | H/T to avail S/D for attending oil Leakege from 220kV side Bphase Bushing. | LD 06/1891 | LD 06/1903
118 | 906113 | BUS REACTOR I INDORE 400kV | WRTS-II | 1 | 2014-06-18 | 15:53 | 2014-06-19 | 17:45 | 0 | 0 | 0 | 1899-12-31 01:52 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1913 | LD 06/2020
119 | 906114 | GANDHAR-HALDARWA II 220kV | WRTS-II | 1 | 2014-06-18 | 17:39 | 2014-06-18 | 19:18 | 0 | 0.06875 | 0 | 0 | O | OMSU | N | H/T as per instructions of WRLDC for installation of PMU at Haldarwa end. | LD 06/1920 | LD 06/1936
120 | 906115 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-19 | 07:46 | 2014-06-19 | 17:35 | 0 | 0 | 0 | 0.40903 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/1965 | LD 06/2018
121 | 906116 | KAKRAPAR-VAPI II 220kV | WRTS-II | 1 | 2014-06-19 | 14:17 | 2014-06-19 | 15:51 | 0 | 0.065278 | 0 | 0 | O | OMSU | N | Line H/T for installation of PMU at Haldarwa end on WRLDC instruction. | LD 06/2000 | LD 06/2008
122 | 906117 | BUS REACTOR I INDORE 765kV | WRTS-II | 1 | 2014-06-19 | 14:33 | 2014-06-19 | 19:11 | 0 | 0 | 0 | 0.19306 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2003 NLDC : 269 | LD 06/2030 NLDC : 271
123 | 906118 | KHANDWA-RAJGARH II 400kV | WRTS-II | 1 | 2014-06-19 | 17:34 | 2014-06-21 | 09:22 | 0 | 0 | 0 | 1899-12-31 15:48 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/2019 | LD 06/2190
124 | 906119 | NIGRIE-SATNA 400kV | WRTS-II | 1 | 2014-06-19 | 18:41 | 2014-06-19 | 19:12 | 0 | 0.021528 | 0 | 0 | O | OMSU | N | Line A/T on Y ph E/F, 124.4km from Satna due to problem in ongoing OPGW work by JP Nigrie. |  | LD 06/2032
125 | 906120 | GANDHAR-DEHGAM I 400kV | WRTS-II | 1 | 2014-06-20 | 08:24 | 2014-06-20 | 21:26 | 0 | 0 | 0 | 0.54306 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2072 | LD 06/2151
126 | 906121 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-20 | 09:36 | 2014-06-20 | 17:50 | 0 | 0 | 0 | 0.34306 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2081 | LD 06/2130
127 | 906122 | VINDHYACHAL-SASAN III 400kV | WRTS-II | 1 | 2014-06-20 | 11:30 | 2014-06-20 | 20:10 | 0 | 0.36111 | 0 | 0 | O | OMSU | N | Line H/T to avail S/D by NTPC. | LD 06/2092 | LD 06/2146
128 | 906123 | ICT2 JABALPUR 765/400KV | WRTS-II | 1 | 2014-06-20 | 11:51 | 2014-06-20 | 20:04 | 0 | 0 | 0 | 0.34236 | D | SCSD | N | H/T to avail OCC approved S/D for erection of single phase isolator structure. | LD 06/2096 NLDC : 281 | LD 06/2147 NLDC : 292
129 | 906124 | KAKRAPAR-VAPI I 220kV | WRTS-II | 1 | 2014-06-20 | 12:20 | 2014-06-20 | 13:25 | 0 | 0.045139 | 0 | 0 | O | OMSU | N | Line H/T to avail S/D by GETCO for PMU installation work at Vapi end. | LD 06/2098 | LD 06/2104
130 | 906125 | NIGRIE-SATNA 400kV | WRTS-II | 1 | 2014-06-20 | 20:42 | 2014-06-20 | 21:27 | 0 | 0.03125 | 0 | 0 | O | OMSU | N | Line A/T on Y ph E, 119.9km from Satna, F/C:2.7kA ( Suspected OPGW works). |  | LD 06/2153
131 | 906126 | NIGRIE-SATNA 400kV | WRTS-II | 1 | 2014-06-20 | 22:59 | 2014-06-22 | 12:50 | 0 | 1899-12-31 13:51 | 0 | 0 | O | OMSU | N | Line A/T on Y ph E/F, 160kM from Satna, F/C:2.24kA// Y ph E, 4 km from Nigrie, F/C:4.093kA ( Nigrie Jurisdiction, Suspected OPGW works ). |  | LD 06/2375
132 | 906127 | VINDHYACHAL(POOLING)-SASAN I 400kV | WRTS-II | 1 | 2014-06-21 | 07:57 | 2014-06-21 | 12:24 | 0.18542 | 0 | 0 | 0 | L | LHWT | N | Line A/T on R & Y Phase to Phase fault due to opening of Y phase jumper at location no. 107. |  | LD 06/2218
133 | 906128 | GANDHAR-DEHGAM I 400kV | WRTS-II | 1 | 2014-06-21 | 08:52 | 2014-06-21 | 21:30 | 0 | 0 | 0 | 0.52639 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2185 | LD 06/2285
134 | 906129 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-21 | 08:56 | 2014-06-21 | 17:56 | 0 | 0 | 0 | 0.375 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2189 | LD 06/2259
135 | 906130 | ICT1 INDORE 765/400KV | WRTS-II | 1 | 2014-06-21 | 10:28 | 2014-06-21 | 19:48 | 0 | 0 | 0 | 0.38889 | D | SCSD | N | H/T to avail OCC Approved S/D for commissioning of CSD relay at Indore. | LD 06/2205 NLD06/307 | LD 06/2269 NLD06/319
136 | 906131 | ICT1 SATNA 765/400KV | WRTS-II | 1 | 2014-06-21 | 10:47 | 2014-06-21 | 16:13 | 0.22639 | 0 | 0 | 0 | L | OSPT | N | H/T to avail OCC approved S/D by Powergrid for AMP work. | LD 06/2206 NLD06/308 | LD 06/2249 NLD06/313
137 | 906132 | MUNDRA-BHACHAU II 400kV | WRTS-II | 1 | 2014-06-21 | 12:10 | 2014-06-21 | 13:38 | 0 | 0 | 0 | 0.061111 | D | OSFD | N | Line H/T to avail emergency S/D by CGPL for attending isolator alignment at CGPL switch yard. | LD 06/2220 | LD 06/2236
138 | 906133 | ICT1 GWALIOR 400/220kV | WRTS-II | 1 | 2014-06-21 | 13:44 | 2014-06-21 | 18:45 | 0.20903 | 0 | 0 | 0 | L | OSPT | N | ICT H/T to avail S/D for replacement of 220kV side Y phase bushing. | LD 06/2221 | LD 06/2266
139 | 906134 | KHANDWA-RAJGARH I 400kV | WRTS-II | 1 | 2014-06-21 | 18:34 | 2014-06-24 | 11:15 | 0 | 0 | 0 | 1900-01-01 16:41 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/2019 | LD 06/2581
140 | 906135 | VINDHYACHAL(POOLING)-SASAN I 400kV | WRTS-II | 1 | 2014-06-22 | 08:26 |  |  | 0 | 0 | 0 | 1900-01-07 15:34 | D | LCSD | N | Line H/T to avail S/D by POWERGRID for interim contigency arrangement for V'chal IV & Rihand III. Line ideal charged as V'chal - Rihand since 11:52hrs/27.06.14 | LD 06/2329
141 | 906136 | VINDHYACHAL(POOLING)-SASAN II 400kV | WRTS-II | 1 | 2014-06-22 | 08:38 | 2014-06-22 | 20:26 | 0 | 0 | 0 | 0.49167 | D | LCSD | N | Line H/T to avail S/D by POWERGRID for interim contigency arrangement for V'chal IV & Rihand III. | LD 06/2333 | LD 06/2403
142 | 906137 | GANDHAR-DEHGAM I 400kV | WRTS-II | 1 | 2014-06-22 | 08:42 | 2014-06-22 | 20:23 | 0 | 0 | 0 | 0.48681 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2334 | LD 06/2404
143 | 906138 | SATNA-GWALIOR I 765kV | WRTS-II | 1 | 2014-06-22 | 09:02 | 2014-06-24 | 23:54 | 0 | 0 | 0 | 1900-01-01 14:52 | D | LCSD | N | Line H/T to avail S/D by POWERGRID for stringig work of 765kV Satna - Gwalior # 2 (D/C portion). | LD 06/2336 NLD06/323 | LD 06/2646 LD 06/367
144 | 906139 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-22 | 10:34 | 2014-06-22 | 17:22 | 0 | 0 | 0 | 0.28333 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2357 | LD 06/2389
145 | 906140 | ITARSI-KHANDWA I 400kV | WRTS-II | 1 | 2014-06-22 | 18:07 | 2014-06-24 | 15:05 | 0 | 0 | 0 | 1899-12-31 20:58 | D | LVRD | N | Line H/T on Voltage regulation on WRLDC instructions. | LD 06/2393
146 | 906141 | INDORE-ASOJ III 400kV | WRTS-II | 1 | 2014-06-22 | 21:24 | 2014-06-22 | 22:04 | 0.027778 | 0 | 0 | 0 | L | LEFT | N | Line A/T on B ph E/F, F/L-312.1 kM from Indore(MP). |  | LD 06/2413
147 | 906142 | GANDHAR-DEHGAM I 400kV | WRTS-II | 1 | 2014-06-23 | 08:03 | 2014-06-23 | 20:18 | 0 | 0 | 0 | 0.51042 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2443 | LD 06/2514
148 | 906143 | PIRANA-ASOJ I 400kV | WRTS-II | 1 | 2014-06-23 | 08:49 | 2014-06-23 | 09:03 | 0 | 0.0097222 | 0 | 0 | O | OMSU | N | Line H/T as per WRLDC instructions. | LD 06/2445 | LD 06/2451
149 | 906144 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-23 | 10:14 | 2014-06-23 | 17:18 | 0 | 0 | 0 | 0.29444 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2460 | LD 06/2495
150 | 906145 | BUS REACTOR I INDORE 400kV | WRTS-II | 1 | 2014-06-23 | 14:50 | 2014-06-26 | 00:33 | 0 | 0 | 0 | 1900-01-01 09:43 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2479 | LD 06/2672
151 | 906146 | BUS REACTOR II GWALIOR 400kV | WRTS-II | 1 | 2014-06-23 | 16:09 |  |  | 0 | 0 | 0 | 1900-01-06 07:51 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2489
152 | 906147 | GANDHAR-DEHGAM II 400kV | WRTS-II | 1 | 2014-06-24 | 08:01 | 2014-06-24 | 21:57 | 0 | 0 | 0 | 0.58056 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2557 | LD 06/2640
153 | 906148 | SAYALI-KHADOLI 220kV | WRTS-II | 1 | 2014-06-24 | 08:44 | 2014-06-25 | 11:18 | 0 | 0 | 0 | 1899-12-31 02:34 | D | LCSD | N | Line H/T to avail OCC Approved S/D by POWERGRID for LILO of Sayali - Khadoli line at Kala S/S. | LD 06/2563 | LD 06/2693
154 | 906149 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-24 | 09:36 | 2014-06-24 | 17:47 | 0 | 0 | 0 | 0.34097 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2569 | LD 06/2619
155 | 906150 | BINA-INDORE I 765kV | WRTS-II | 1 | 2014-06-24 | 10:11 | 2014-06-25 | 22:45 | 0 | 0 | 0 | 1899-12-31 12:34 | D | LPRD | N | Line H/T for power regulation on WRLDC Instruction on outage of 400kV Indore - Indore # 2 & Indore - Asoj # 3 for construction work of 765kV Indore - Vadodara line. | LD 06/2577 | LD 06/2756 LD 06/383
156 | 906151 | INDORE-ASOJ III 400kV | WRTS-II | 1 | 2014-06-24 | 10:28 | 2014-06-25 | 23:38 | 0 | 0 | 0 | 1899-12-31 13:10 | D | LCSD | N | Line H/T to avail S/D by POWERGRID for construction work of 765kV Indore - Vadodara line. | LD 06/2583 | LD 06/2755
157 | 906152 | INDORE(MP)-INDORE II 400kV | WRTS-II | 1 | 2014-06-24 | 10:30 | 2014-06-25 | 23:33 | 0 | 0 | 0 | 1899-12-31 13:03 | D | LCSD | N | Line H/T to avail S/D by POWERGRID for construction work of 765kV Indore - Vadodara line. | LD 06/2584 | LD 06/2754
158 | 906153 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-24 | 23:52 | 2014-06-24 | 23:52 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully at both ends on R-ph to E/F, F/L - 311km from Mundra & 30.10km from Jetpur end. Due to tracking along insulator due to deposition of dust & salt particles.
159 | 906154 | DAMOH-BHOPAL II 400KV | WRTS-II | 1 | 2014-06-25 | 03:19 | 2014-06-25 | 16:16 | 0 | 0 | 0 | 0.53958 | D | OSFD | N | H/T to avail S/D by MPPTCL to attend heavy sparking at Bhopal end. | LD 06/2657 | LD 06/2714
160 | 906155 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-25 | 04:05 | 2014-06-25 | 04:05 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully at both ends on R-ph to E/F, F/L - 292km from Mundra & 30.17km from Jetpur end.Due to tracking along insulator due to deposition of dust & salt particles.
161 | 906156 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-25 | 04:42 | 2014-06-25 | 04:42 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully at both ends on R-ph to E/F, F/L - 395.5km from Mundra & 30.14km from Jetpur end. Due to tracking along insulator due to deposition of dust & salt particles.
162 | 906157 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-25 | 04:49 | 2014-06-25 | 04:49 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully at both ends on R-ph to E/F, F/L - 367.5km from Mundra & 42.66km from Jetpur end. Due to tracking along insulator due to deposition of dust & salt particles.
163 | 906158 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-25 | 05:07 | 2014-06-25 | 05:07 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully at both ends on R-ph to E/F, F/L - 400km from Mundra & 30.44km from Jetpur end. Due to tracking along insulator due to deposition of dust & salt particles.
164 | 906159 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-25 | 05:57 | 2014-06-25 | 05:57 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully at both ends on R-ph to E/F, F/L - 321Km from Mundra & 42.94km from Jetpur end. Due to tracking along insulator due to deposition of dust & salt particles.
165 | 906160 | DAMOH-BIRSINGHPUR I 400kV | WRTS-II | 1 | 2014-06-25 | 07:23 | 2014-06-25 | 07:23 | 0 | 0 | 0 | 0 | L | LART | N | A/R successfully at both ends on B-ph to E/F, F/L - 136Km from Damoh end.
166 | 906161 | GANDHAR-DEHGAM II 400kV | WRTS-II | 1 | 2014-06-25 | 08:01 | 2014-06-25 | 20:42 | 0 | 0 | 0 | 0.52847 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2668 | LD 06/2743
167 | 906162 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-25 | 09:19 | 2014-06-25 | 18:13 | 0 | 0 | 0 | 0.37083 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2676 | LD 06/2731
168 | 906163 | VAPI-NAVASARI(GIS) II 400kV | WRTS-II | 1 | 2014-06-25 | 09:23 | 2014-06-25 | 19:14 | 0.41042 | 0 | 0 | 0 | L | OSPT | N | H/T to avail S/D by PG for attending insulator flashover at Location no. -14. | LD 06/2680 | LD 06/2727
169 | 906164 | SATPURA-ITARSI 400kV | WRTS-II | 1 | 2014-06-25 | 09:34 | 2014-06-25 | 19:20 | 0 | 0 | 0 | 0.40694 | D | OSPD | N | H/T to avail OCC S/D by MPPTCL for Line crossing work of 400kV Astha-Satpura Line. | LD 06/2679 | LD 06/2734
170 | 906165 | VINDHYACHAL-JABALPUR IV 400kV | WRTS-II | 1 | 2014-06-25 | 14:05 | 2014-06-25 | 20:14 | 0.25625 | 0 | 0 | 0 | L | OSPT | N | H/T to avail S/D by PG for attending hot spot at Location no -82. | LD 06/2702 | LD 06/2741
171 | 906166 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-26 | 01:50 | 2014-06-26 | 02:28 | 0 | 0 | 0.026389 | 0 | S | LNCC | N | A/T from both ends on B-ph to E/F,F/L - 34.91kms from Jetpur & 285km from Mundra due to tracking across porcelain long rod insulators in certain stratches of Line. |  | LD 06/2771
172 | 906167 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-26 | 02:31 | 2014-06-26 | 02:31 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on Y-ph to E/F,F/L - 42.40kms from Jetpur due to tracking across porcelain long rod insulators in certain stratches of Line.
173 | 906168 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-26 | 02:33 | 2014-06-26 | 02:33 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on Y-ph to E/F,F/L - 36.83kms from Jetpur due to tracking across porcelain long rod insulators in certain stratches of Line. .
174 | 906169 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-26 | 03:07 | 2014-06-26 | 18:33 | 0 | 0 | 0.64306 | 0 | S | LNCC | N | A/T from both ends on Y-B-ph to ph fault,F/L - 33.38kms from Jetpur & 275.6km from Mundra due to tracking across porcelain long rod insulators in certain stratches of Line.
175 | 906170 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-26 | 04:33 | 2014-06-26 | 04:33 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on Y-ph to E/F,F/L - 44.6kms from Jetpur & 327km from Mundra due to tracking across porcelain long rod insulators in certain stratches of Line.
176 | 906171 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-26 | 06:01 | 2014-06-26 | 09:38 | 0 | 0 | 0.15069 | 0 | S | LNCC | N | A/T from both ends on Y-B-ph to ph fault,F/L - 107.5kms from Jetpur & 278km from Mundra due to tracking across porcelain long rod insulators in certain stratches of Line.
177 | 906172 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-26 | 05:57 | 2014-06-26 | 18:11 | 0 | 0 | 0 | 0.50972 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/2779 | LD 06/2992
178 | 906173 | JABALPUR-ITARSI III 400kV | WRTS-II | 1 | 2014-06-26 | 11:09 | 2014-06-27 | 00:58 | 0 | 0 | 0 | 0.57569 | D | OSPD | N | Line H/T to avail OCC approved S/D by BDTCL for crossing work of 765kV JBP - Bhopal Line. | LD 06/2811 | LD 06/2888
179 | 906174 | JABALPUR-ITARSI IV 400kV | WRTS-II | 1 | 2014-06-26 | 11:09 | 2014-06-26 | 22:37 | 0 | 0 | 0 | 0.47778 | D | OSPD | N | Line H/T to avail OCC approved S/D by BDTCL for crossing work of 765kV JBP - Bhopal Line. | LD 06/2811 | LD 06/2880
180 | 906175 | GANDHAR-DEHGAM II 400kV | WRTS-II | 1 | 2014-06-26 | 11:40 | 2014-06-26 | 21:49 | 0 | 0 | 0 | 0.42292 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2812 | LD 06/2871
181 | 906176 | KAWAS-NAVSARI(GIS) I 220kV | WRTS-II | 1 | 2014-06-26 | 12:00 | 2014-06-26 | 21:34 | 0 | 0 | 0 | 0.39861 | D | OSPD | N | Line H/T to avail OCC approved S/D by NTPC. | LD 06/2826 | LD 06/2873
182 | 906177 | GANDHAR-HALDARWA II 220kV | WRTS-II | 1 | 2014-06-26 | 22:38 | 2014-06-27 | 02:32 | 0 | 0 | 0 | 0.1625 | D | OSPD | N | Line H/T to avail OCC approved S/D by GETCO. | LD 06/2882 | LD 06/2894
183 | 906178 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-27 | 00:17 | 2014-06-27 | 00:17 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on B-ph to E/F,F/L - 47.34kms from Jetpur due to tracking across porcelain long rod insulators in certain stretches of Line.
184 | 906179 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-27 | 00:31 | 2014-06-27 | 01:10 | 0 | 0 | 0.027083 | 0 | S | LNCC | N | A/T from both ends on B-ph to E,F/L - 45.68kms from Jetpur ,F/C: 1.603kA & 333km from Mundra due to tracking across porcelain long rod insulators in certain stretches of Line. |  | LD 06/2891
185 | 906180 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-27 | 01:30 | 2014-06-27 | 20:38 | 0 | 0 | 0.79722 | 0 | S | LNCC | N | A/T from both ends on B-ph to E,F/L - 316.2km from Mundra, F/C: 1.66kA due to tracking across porcelain long rod insulators in certain stretches of Line. |  | LD 06/3013
186 | 906181 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-27 | 06:52 | 2014-06-27 | 06:52 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on B-ph to E/F,F/L - 95.62kms from Jetpur, F/C:3.465kA due to tracking across porcelain long rod insulators in certain stretches of Line.
187 | 906182 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-27 | 07:02 | 2014-06-27 | 07:02 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on Y-ph to E/F,F/L - 96.63kms from Jetpur, F/C:3.538kA due to tracking across porcelain long rod insulators in certain stretches of Line.
188 | 906183 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-27 | 07:53 | 2014-06-27 | 17:44 | 0 | 0 | 0 | 0.41042 | D | SVRD | N | Bus Reactor H/T on voltage regulation as per instruction of WRLDC. | LD 06/2913 | LD 06/2992
189 | 906184 | GANDHAR-DEHGAM I 400kV | WRTS-II | 1 | 2014-06-27 | 11:10 | 2014-06-27 | 20:37 | 0 | 0 | 0 | 0.39375 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/2940 | LD 06/3008
190 | 906185 | KHANDWA-DHULE I 400kV | WRTS-II | 1 | 2014-06-27 | 15:24 | 2014-06-27 | 21:33 | 0.25625 | 0 | 0 | 0 | L | OSPT | N | S/D availed by WR-I for replacement of failed insulator inner V string at location no:854. | LD 06/2973 | LD 06/3017
191 | 906186 | SATNA-BINA III 400kV | WRTS-II | 1 | 2014-06-27 | 16:34 | 2014-06-27 | 16:42 | 0 | 0 | 0 | 0.0055556 | D | SCSD | N | Line H/T to take out Line Reactor at Bina for replacement of LR 390kV LA with 336kV LA & line charged without L/R. | LD 06/2981 | LD 06/2982
192 | 906187 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-28 | 05:35 | 2014-06-28 | 05:35 | 0 | 0 | 0 | 0 | S | LNCC | N | A/R successfully from both ends on Y-ph to E/F,F/L - 90.94kms from Jetpur, F/C:9.609kA//282.9km from Mundra,F/C: 1.77kA due to tracking across porcelain long rod insulators in certain stretches of Line.
193 | 906188 | MUNDRA-JETPUR I 400kV | WRTS-II | 1 | 2014-06-28 | 07:39 | 2014-06-28 | 14:28 | 0 | 0 | 0 | 0.28403 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3039 | LD 06/3080
194 | 906189 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-28 | 08:51 | 2014-06-28 | 18:16 | 0 | 0 | 0 | 0.39236 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/3048 | LD 06/3105
195 | 906190 | SEONI-BINA I 765kV | WRTS-II | 1 | 2014-06-28 | 09:59 | 2014-06-28 | 20:40 | 0 | 0 | 0 | 0.44514 | D | LCSD | N | Line H/T to avail OCC Approved S/D for Erection of new 400KV TC and TE Tower of NHPTL & 400kV bay extension related to NHPTL at Bina. | WR 06/3058 NLD 06/423 | WR 06/3119 NLD 06/427
196 | 906191 | GANDHAR-DEHGAM II 400kV | WRTS-II | 1 | 2014-06-28 | 10:39 | 2014-06-28 | 18:43 | 0 | 0 | 0 | 0.33611 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3061 | LD 06/3103
197 | 906192 | MUNDRA-JETPUR II 400kV | WRTS-II | 1 | 2014-06-28 | 14:35 | 2014-06-28 | 17:32 | 0 | 0 | 0 | 0.12292 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3083 | LD 06/3098
198 | 906193 | KHANDWA-DHULE I 400kV | WRTS-II | 1 | 2014-06-28 | 17:39 | 2014-06-29 | 01:01 | 0.30694 | 0 | 0 | 0 | L | OSPT | N | S/D availed by WR-I for replacement of failed insulator inner V string at location no:854. | LD 06/3099 | LD 06/3130
199 | 906194 | MUNDRA-LIMBDI II 400kV | WRTS-II | 1 | 2014-06-29 | 07:35 | 2014-06-29 | 14:17 | 0 | 0 | 0 | 0.27917 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3130
200 | 906195 | SEONI-BINA I 765kV | WRTS-II | 1 | 2014-06-29 | 08:15 | 2014-06-29 | 20:00 | 0 | 0 | 0 | 0.48958 | D | LCSD | N | Line H/T to avail OCC Approved S/D for Erection of new 400KV TC and TE Tower of NHPTL & 400kV bay extension related to NHPTL at Bina. | LD 06/3153 NLD 06/431 | LD 06/3216 NLD 06/439
201 | 906196 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-29 | 09:31 | 2014-06-29 | 18:03 | 0 | 0 | 0 | 0.35556 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/3164 | LD 06/3205
202 | 906197 | MUNDRA-LIMBDI I 400kV | WRTS-II | 1 | 2014-06-29 | 16:03 | 2014-06-29 | 20:25 | 0 | 0 | 0 | 0.18194 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3189 | LD 06/3221
203 | 906198 | JABALPUR-JABALPUR(POOLING) I 400kV | WRTS-II | 1 | 2014-06-29 | 16:09 | 2014-06-29 | 17:47 | 0 | 0 | 0 | 0.068056 | D | LCSD | N | Line A/T on B-ph to E/F, F/L - 08kms from Jabalpur. Fault initiated due to problem in OPGW hardware used for Online OPGW installation work. |  | LD 06/3204
204 | 906199 | JABALPUR-JABALPUR(POOLING) II 400kV | WRTS-II | 1 | 2014-06-29 | 16:10 | 2014-06-29 | 17:32 | 0 | 0 | 0 | 0.056944 | D | LCSD | N | Line A/T on B-ph to E/F, F/L - 08kms from Jabalpur. Fault initiated due to problem in OPGW hardware used for Online OPGW installation work. |  | LD 06/3193
205 | 906199 | BHACHAU-RANCHHODPURA I 400kV | WRTS-II | 1 | 2014-06-30 | 08:02 | 2014-06-30 | 15:58 | 0 | 0 | 0 | 0.33056 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3246 | LD 06/3312
206 | 906200 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | WRTS-II | 1 | 2014-06-30 | 08:30 | 2014-06-30 | 21:25 | 0 | 0 | 0 | 0.53819 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3244 | LD 06/3349
207 | 906201 | BUS REACTOR DHULE 400kV | WRTS-II | 1 | 2014-06-30 | 08:51 | 2014-06-30 | 17:50 | 0 | 0 | 0 | 0.37431 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/3254 | LD 06/3326
208 | 906202 | SEONI-BINA I 765kV | WRTS-II | 1 | 2014-06-30 | 10:01 | 2014-06-30 | 20:16 | 0 | 0 | 0 | 0.42708 | D | LCSD | N | Line H/T to avail OCC Approved S/D for Erection of new 400KV TC and TE Tower of NHPTL & 400kV bay extension related to NHPTL at Bina. | LD 06/3263 NLD 06/450 | LD 06/3346 NLD 06/465
209 | 906203 | KAWAS-NAVSARI(GIS) I 220kV | WRTS-II | 1 | 2014-06-30 | 12:52 | 2014-06-30 | 18:34 | 0 | 0 | 0 | 0.2375 | D | OSPD | N | Line H/T to avail S/D by NTPC. | LD 06/3291 | LD 06/3337
210 | 906204 | JABALPUR-ITARSI III 400kV | WRTS-II | 1 | 2014-06-30 | 13:54 |  |  | 0 | 0 | 0 | 0.42083 | D | OSPD | N | Line H/T to avail OCC Approved S/d by M/S BDTCL for crossing work of 765kV Jabalpur - Bhopal Line | LD 06/3297
211 | 906205 | JABALPUR-ITARSI IV 400kV | WRTS-II | 1 | 2014-06-30 | 13:55 |  |  | 0 | 0 | 0 | 0.42014 | D | OSPD | N | Line H/T to avail OCC Approved S/d by M/S BDTCL for crossing work of 765kV Jabalpur - Bhopal Line | LD 06/3298
212 | 906206 | BUS REACTOR III GWALIOR 400kV | WRTS-II | 1 | 2014-06-30 | 15:07 |  |  | 0 | 0 | 0 | 0.37014 | D | SVRD | N | Reactor H/T for Voltage Regulation on WRLDC Instruction. | LD 06/3306
213 | 906207 | BHACHAU-RANCHHODPURA II 400kV | WRTS-II | 1 | 2014-06-30 | 16:10 | 2014-06-30 | 20:40 | 0 | 0 | 0 | 0.1875 | D | LCSD | N | Line H/T to avail OCC approved S/D for replacement of porcelain insulator strings by polymer insulators. | LD 06/3315 | LD 06/3348
214 | 906208 | BUS REACTOR I GWALIOR 400kV | WRTS-II | 1 | 2014-06-30 | 18:00 | 2014-06-30 | 19:33 | 0 | 0 | 0 | 0.064583 | D | SCSD | N | Reactor H/T to avail OCC Approved S/D for commissioning of CSD relay at Gwalior end. | LD 06/3321 | LD 06/3340
[9 empty] | 1900-01-04 06:26 | 1900-01-22 07:54 | 1899-12-31 19:58 | 1900-06-27 01:14
Note on C4: Enter company name here
Note on E4: Enter Month for which data is sent in date format

## AV-WR-II
WRTS-II TRANSMISSION SYSTEM AVAILABILITY FOR |  |  |  | 2014-06-30
SN | Element Name | TYPE | PG | OTHERS | SYSTEM | DEEMED | PG (TNAi) | OTHERS | SYSTEM | DEEMED | Total Hrs (Ti) | Line length/ MVA /(R) | SIL/ Set | Wi= CktKmX SIL | Wi x (Ti - TNAi) | =Wi x Ti | Individual Element Availability
1 | SATPURA-ITARSI 400kV | INTRA | 0 | 0 | 0 | 0.40694 | 0 | 0 | 0 | 9.77 | 720 | 79 | 515 | 40685 | 29293200 | 29293200 | 100%
2 | ITARSI-INDORE I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 207 | 236.2774 | 48909.4171 | 35214780.3121 | 35214780.3121 | 100%
3 | ITARSI-INDORE II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 214 | 250.3527 | 53575.4744 | 38574341.5376 | 38574341.5376 | 100%
4 | INDORE-ASOJ I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 289 | 339.4716 | 98107.2913 | 70637249.7589 | 70637249.7589 | 100%
5 | INDORE-ASOJ II 400kV | INTRA | 0.034722 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 720 | 273 | 326.2678 | 89071.1154 | 64057274.0344 | 64131203.0602 | 99.88%
6 | VINDHYACHAL-JABALPUR I 400kV | INTRA | 0.011806 | 0.18611 | 0 | 0 | 0.28 | 4.47 | 0 | 0 | 715.53 | 360 | 444.645 | 160072.198 | 114491639.5846 | 114536459.8 | 99.96%
7 | VINDHYACHAL-JABALPUR II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 360 | 444.645 | 160072.198 | 115251982.5248 | 115251982.5248 | 100%
8 | JABALPUR-ITARSI I 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 06:18 | 0 | 0 | 0 | 54.3 | 720 | 232 | 291.974 | 67737.9752 | 48771342.1691 | 48771342.1691 | 100%
9 | JABALPUR-ITARSI II 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 06:24 | 0 | 0 | 0 | 54.4 | 720 | 232 | 291.974 | 67737.9752 | 48771342.1691 | 48771342.1691 | 100%
10 | GANDHAR-DEHGAM I 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 11:03 | 0 | 0 | 0 | 59.05 | 720 | 157 | 515 | 80855 | 58215600 | 58215600 | 100%
11 | GANDHAR-DEHGAM II 400kV | INTRA | 0 | 0 | 0 | 1899-12-31 20:50 | 0 | 0 | 0 | 44.83 | 720 | 157 | 515 | 80855 | 58215600 | 58215600 | 100%
12 | VINDHYACHAL-SASAN III 400kV | INTRA | 0 | 0.36111 | 0 | 0 | 0 | 8.67 | 0 | 0 | 711.33 | 21 | 515 | 10815 | 7693033.95 | 7693033.95 | 100%
13 | SASAN-JABALPUR 400kV | INTRA | 0.22431 | 0.038194 | 0 | 0 | 5.38 | 0.92 | 0 | 0 | 719.08 | 376 | 438.8604 | 165011.4981 | 117768706.2181 | 118656468.078 | 99.25%
14 | VINDHYACHAL-JABALPUR IV 400kV | INTRA | 0.25625 | 0 | 0 | 0 | 6.15 | 0 | 0 | 0 | 720 | 389 | 353.3073 | 137436.5477 | 98109079.5445 | 98954314.3126 | 99.15%
15 | JABALPUR-ITARSI III 400kV | INTRA | 0 | 0 | 0 | 0.99653 | 0 | 0 | 0 | 23.92 | 720 | 234 | 282.822 | 66180.3576 | 47649857.4532 | 47649857.4532 | 100%
16 | JABALPUR-ITARSI IV 400kV | INTRA | 0 | 0 | 0 | 0.89792 | 0 | 0 | 0 | 21.55 | 720 | 234 | 282.822 | 66180.3576 | 47649857.4532 | 47649857.4532 | 100%
17 | ITARSI-KHANDWA I 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 12:13 | 0 | 0 | 0 | 60.22 | 720 | 196.64 | 393.713 | 77419.723 | 55742200.5755 | 55742200.5755 | 100%
18 | ITARSI-KHANDWA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 196.64 | 515 | 101269.6 | 72914112 | 72914112 | 100%
19 | KHANDWA-DHULE I 400kV | INTRA | 0.56319 | 0.020139 | 0 | 0 | 13.52 | 0.48 | 0 | 0 | 719.52 | 261.78 | 315.6668 | 82635.2673 | 58340498.7012 | 59457727.5149 | 98.12%
20 | KHANDWA-DHULE II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 261.78 | 315.6668 | 82635.2673 | 59497392.4431 | 59497392.4431 | 100%
21 | GANDHAR-SUGEN 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 57 | 515 | 29355 | 21135600 | 21135600 | 100%
22 | SUGEN-VAPI 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 110 | 515 | 56650 | 40788000 | 40788000 | 100%
23 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | INTRA | 0 | 0 | 0 | 0.53819 | 0 | 0 | 0 | 12.92 | 720 | 13 | 515 | 6695 | 4820400 | 4820400 | 100%
24 | GANDHAR-HALDARWA I 220kV | INTRA | 0 | 0 | 0 | 0.26111 | 0 | 0 | 0 | 6.27 | 720 | 13 | 132 | 1716 | 1235520 | 1235520 | 100%
25 | GANDHAR-HALDARWA II 220kV | INTRA | 0 | 0.06875 | 0 | 0.1625 | 0 | 1.65 | 0 | 3.9 | 718.35 | 13 | 132 | 1716 | 1232688.6 | 1232688.6 | 100%
26 | KAWAS-NAVSARI(GIS) I 220kV | INTRA | 0 | 0 | 0 | 0.63611 | 0 | 0 | 0 | 15.27 | 720 | 58.15 | 132 | 7675.8 | 5526576 | 5526576 | 100%
27 | KAWAS-NAVSARI(GIS) II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 58.15 | 132 | 7675.8 | 5526576 | 5526576 | 100%
28 | NAVSARI(GIS)-NAVSARI I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 31.33 | 132 | 4135.56 | 2977603.2 | 2977603.2 | 100%
29 | NAVSARI(GIS)-NAVSARI II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 31.33 | 132 | 4135.56 | 2977603.2 | 2977603.2 | 100%
30 | KAWAS-VAV I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 37 | 132 | 4884 | 3516480 | 3516480 | 100%
31 | KAWAS-VAV II 220kV | INTRA | 0.022222 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 720 | 37 | 132 | 4884 | 3513891.48 | 3516480 | 99.93%
32 | KAWAS-HALDARWA I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 81 | 132 | 10692 | 7698240 | 7698240 | 100%
33 | KAWAS-HALDARWA II 220kV | INTRA | 0 | 0 | 0 | 0.13056 | 0 | 0 | 0 | 3.13 | 720 | 81 | 132 | 10692 | 7698240 | 7698240 | 100%
34 | KAKRAPAR-HALDARWA I 220kV | INTRA | 0.67847 | 0.13472 | 0 | 0.40764 | 16.28 | 3.23 | 0 | 9.78 | 716.77 | 74 | 132 | 9768 | 6842386.32 | 7001409.36 | 97.73%
35 | KAKRAPAR-HALDARWA II 220kV | INTRA | 0 | 0.15972 | 0 | 0.40764 | 0 | 3.83 | 0 | 9.78 | 716.17 | 74 | 132 | 9768 | 6995548.56 | 6995548.56 | 100%
36 | KAKRAPAR-VAV I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 43 | 132 | 5676 | 4086720 | 4086720 | 100%
37 | KAKRAPAR-VAV II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 43 | 132 | 5676 | 4086720 | 4086720 | 100%
38 | KAKRAPAR-VAPI I 220kV | INTRA | 0 | 0.045139 | 0 | 0 | 0 | 1.08 | 0 | 0 | 718.92 | 117 | 132 | 15444 | 11103000.48 | 11103000.48 | 100%
39 | KAKRAPAR-VAPI II 220kV | INTRA | 0.35903 | 0.065278 | 0 | 0 | 8.62 | 1.57 | 0 | 0 | 718.43 | 117 | 132 | 15444 | 10962305.64 | 11095432.92 | 98.8%
40 | VINDHYACHAL-SATNA I 400kV | INTRA | 0 | 1900-01-02 13:00 | 0 | 0 | 0 | 85 | 0 | 0 | 635 | 267 | 429.015 | 114547.0033 | 72737347.1009 | 72737347.1009 | 100%
41 | VINDHYACHAL-SATNA II 400kV | INTRA | 0 | 0 | 0 | 1900-01-01 11:35 | 0 | 0 | 0 | 59.58 | 720 | 267 | 429.015 | 114547.0033 | 82473842.3821 | 82473842.3821 | 100%
42 | VINDHYACHAL-SATNA III 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 258.31 | 425.8205 | 109993.7017 | 79195465.2583 | 79195465.2583 | 100%
43 | VINDHYACHAL-NIGRIE 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 100.32 | 221.7868 | 22249.6514 | 16019749.0031 | 16019749.0031 | 100%
44 | NIGRIE-SATNA 400kV | INTRA | 0 | 1900-01-02 23:33 | 0 | 0 | 0 | 95.55 | 0 | 0 | 624.45 | 161.11 | 515 | 82971.65 | 51811646.8425 | 51811646.8425 | 100%
45 | SATNA-BINA I 400kV | INTRA | 0.15139 | 0 | 0 | 0 | 3.63 | 0 | 0 | 0 | 720 | 276 | 328.902 | 90776.9409 | 65029877.1878 | 65359397.4835 | 99.5%
46 | SATNA-BINA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 276 | 328.902 | 90776.9409 | 65359397.4835 | 65359397.4835 | 100%
47 | BINA-BINA(MP) I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.742 | 515 | 382.13 | 275133.6 | 275133.6 | 100%
48 | BINA-BINA(MP) II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.742 | 515 | 382.13 | 275133.6 | 275133.6 | 100%
49 | BINA-GWALIOR I 765kV | INTRA | 0.10694 | 0 | 0 | 0 | 2.57 | 0 | 0 | 0 | 720 | 234.931 | 867.5966 | 203825.3474 | 146230418.9585 | 146754250.1012 | 99.64%
50 | SATNA-BINA IV 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 272.586 | 325.8981 | 88835.2493 | 63961379.5041 | 63961379.5041 | 100%
51 | SATNA-BINA III 400kV | INTRA | 0 | 0 | 0 | 0.0055556 | 0 | 0 | 0 | 0.13 | 720 | 272.586 | 325.8981 | 88835.2493 | 63961379.5041 | 63961379.5041 | 100%
52 | BINA-SHUJALPUR I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 199.936 | 142.2855 | 28448.0014 | 20482560.9987 | 20482560.9987 | 100%
53 | BINA-SHUJALPUR II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 199.936 | 142.2855 | 28448.0014 | 20482560.9987 | 20482560.9987 | 100%
54 | SHUJALPUR-NAGDA I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 152.229 | 292.9847 | 44600.7689 | 32112553.6417 | 32112553.6417 | 100%
55 | SHUJALPUR-NAGDA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 152.229 | 292.9847 | 44600.7689 | 32112553.6417 | 32112553.6417 | 100%
56 | NAGDA-DEHGAM II 400KV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 331.442 | 366.6699 | 121529.8006 | 87501456.4578 | 87501456.4578 | 100%
57 | NAGDA-DEHGAM I 400KV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 331.442 | 366.6699 | 121529.8006 | 87501456.4578 | 87501456.4578 | 100%
58 | SEONI-KHANDWA I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 351.729 | 533.8287 | 187763.0449 | 135189392.3556 | 135189392.3556 | 100%
59 | SEONI-KHANDWA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 351.729 | 533.8287 | 187763.0449 | 135189392.3556 | 135189392.3556 | 100%
60 | KHANDWA-RAJGARH II 400kV | INTRA | 0.0069444 | 1900-01-06 16:43 | 0 | 1900-01-01 02:22 | 0.17 | 184.72 | 0 | 50.37 | 535.28 | 220.588 | 515 | 113602.82 | 60790005.0102 | 60809317.4896 | 99.97%
61 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | INTRA | 0 | 1900-01-05 16:55 | 0.0069444 | 1900-01-03 17:54 | 0 | 160.92 | 0.17 | 113.9 | 558.91 | 4.01 | 515 | 2065.15 | 1154232.9865 | 1154232.9865 | 100%
62 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | INTRA | 0 | 0.31597 | 0.10347 | 0 | 0 | 7.58 | 2.48 | 0 | 709.94 | 4.01 | 515 | 2065.15 | 1466132.591 | 1466132.591 | 100%
63 | RAJGARH-NAGDA I 400kV(LILO) | INTRA | 0 | 0 | 0.0069444 | 1900-01-04 18:59 | 0 | 0 | 0.17 | 138.98 | 719.83 | 4.12 | 515 | 2121.8 | 1527335.294 | 1527335.294 | 100%
64 | RAJGARH-NAGDA II 400kV(LILO) | INTRA | 0 | 0 | 0.0069444 | 1900-01-11 17:20 | 0 | 0 | 0.17 | 305.33 | 719.83 | 4.12 | 515 | 2121.8 | 1527335.294 | 1527335.294 | 100%
65 | KHANDWA-RAJGARH I 400kV | INTRA | 0 | 0 | 0 | 1900-01-05 18:13 | 0 | 0 | 0 | 162.22 | 720 | 220.588 | 515 | 113602.82 | 81794030.4 | 81794030.4 | 100%
66 | VAPI-MAGARWADA I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25.71 | 132 | 3393.72 | 2443478.4 | 2443478.4 | 100%
67 | VAPI-MAGARWADA II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25.71 | 132 | 3393.72 | 2443478.4 | 2443478.4 | 100%
68 | VAPI-KHARADPARA I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 29.66 | 132 | 3915.12 | 2818886.4 | 2818886.4 | 100%
69 | VAPI-KHARADPARA II 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 29.66 | 132 | 3915.12 | 2818886.4 | 2818886.4 | 100%
70 | BINA-GWALIOR II 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 233.652 | 853.8925 | 199513.694 | 143649859.6718 | 143649859.6718 | 100%
71 | SEONI-BINA I 765kV | INTRA | 0 | 0 | 0 | 1899-12-31 08:41 | 0 | 0 | 0 | 32.68 | 720 | 292.046 | 1263.1629 | 368901.6599 | 265609195.1624 | 265609195.1624 | 100%
72 | DAMOH-BHOPAL I 400KV | INTRA | 0 | 0 | 0 | 1900-01-04 15:24 | 0 | 0 | 0 | 135.4 | 720 | 214.471 | 405.1828 | 86899.971 | 62567979.0917 | 62567979.0917 | 100%
73 | DAMOH-BHOPAL II 400KV | INTRA | 0 | 0 | 0.063194 | 0.53958 | 0 | 0 | 1.52 | 12.95 | 718.48 | 213.8 | 404.7913 | 86544.3797 | 62180405.953 | 62180405.953 | 100%
74 | VAPI-KHADOLI I 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 28.549 | 132 | 3768.468 | 2713296.96 | 2713296.96 | 100%
75 | VAPI-SAYALI 220kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 18.3 | 132 | 2415.6 | 1739232 | 1739232 | 100%
76 | SAYALI-KHADOLI 220kV | INTRA | 0 | 0 | 0 | 1899-12-31 02:34 | 0 | 0 | 0 | 26.57 | 720 | 12.235 | 132 | 1615.02 | 1162814.4 | 1162814.4 | 100%
77 | DAMOH-BIRSINGHPUR I 400kV | INTRA | 0.040972 | 0 | 0 | 0 | 0.98 | 0 | 0 | 0 | 720 | 228.474 | 412.7548 | 94303.7428 | 67806277.119 | 67898694.7869 | 99.86%
78 | DAMOH-BIRSINGHPUR II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 228.474 | 412.7548 | 94303.7428 | 67898694.7869 | 67898694.7869 | 100%
79 | DEHGAM-PIRANA I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46.656 | 515 | 24027.84 | 17300044.8 | 17300044.8 | 100%
80 | DEHGAM-PIRANA II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46.656 | 515 | 24027.84 | 17300044.8 | 17300044.8 | 100%
81 | MUNDRA-BHACHAU I 400kV | INTRA | 0.28125 | 0 | 0 | 0 | 6.75 | 0 | 0 | 0 | 720 | 99.468 | 605 | 60178.14 | 42922058.355 | 43328260.8 | 99.06%
82 | MUNDRA-BHACHAU II 400kV | INTRA | 0.28194 | 0 | 0 | 0.061111 | 6.77 | 0 | 0 | 1.47 | 720 | 99.468 | 605 | 60178.14 | 42920854.7922 | 43328260.8 | 99.06%
83 | BHACHAU-RANCHHODPURA I 400kV | INTRA | 0 | 0 | 0 | 0.33056 | 0 | 0 | 0 | 7.93 | 720 | 282.856 | 528.1603 | 149393.3178 | 107563188.7839 | 107563188.7839 | 100%
84 | BHACHAU-RANCHHODPURA II 400kV | INTRA | 0 | 0 | 0 | 0.1875 | 0 | 0 | 0 | 4.5 | 720 | 282.856 | 528.1603 | 149393.3178 | 107563188.7839 | 107563188.7839 | 100%
85 | MUNDRA-LIMBDI I 400kV | INTRA | 0 | 0 | 0 | 0.51875 | 0 | 0 | 0 | 12.45 | 720 | 314.053 | 516.9265 | 162342.3045 | 116886459.2743 | 116886459.2743 | 100%
86 | MUNDRA-LIMBDI II 400kV | INTRA | 0 | 0 | 0 | 0.27917 | 0 | 0 | 0 | 6.7 | 720 | 314.053 | 516.9265 | 162342.3045 | 116886459.2743 | 116886459.2743 | 100%
87 | SATNA-BINA I 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 274.164 | 1170.2371 | 320836.8949 | 231002564.3638 | 231002564.3638 | 100%
88 | SATNA-BINA II 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 275.635 | 1178.628 | 324871.1198 | 233907206.2244 | 233907206.2244 | 100%
89 | BINA-INDORE I 765kV | INTRA | 0 | 0 | 0 | 1899-12-31 12:34 | 0 | 0 | 0 | 36.57 | 720 | 311.81 | 1347.3419 | 420114.6841 | 302482572.5176 | 302482572.5176 | 100%
90 | GANDHAR-NAVSARI(GIS) II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 102.152 | 515 | 52608.28 | 37877961.6 | 37877961.6 | 100%
91 | GANDHAR-NAVSARI(GIS) I 400kV | INTRA | 0 | 0 | 0 | 0.70903 | 0 | 0 | 0 | 17.02 | 720 | 102.152 | 515 | 52608.28 | 37877961.6 | 37877961.6 | 100%
92 | MUNDRA-JETPUR I 400kV | INTRA | 0 | 0 | 0.66944 | 0.28403 | 0 | 0 | 16.07 | 6.82 | 703.93 | 336.742 | 523.3266 | 176226.0422 | 124050797.8648 | 124050797.8648 | 100%
93 | MUNDRA-JETPUR II 400kV | INTRA | 0 | 0 | 0.975 | 0.54653 | 0 | 0 | 23.4 | 13.12 | 696.6 | 336.742 | 523.3266 | 176226.0422 | 122759060.9757 | 122759060.9757 | 100%
94 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 28.55 | 687 | 19613.85 | 14121972 | 14121972 | 100%
95 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) II 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 28.55 | 687 | 19613.85 | 14121972 | 14121972 | 100%
96 | VINDHYACHAL(POOLING)-SASAN I 400kV | INTRA | 0.18542 | 0 | 0 | 1900-01-07 15:34 | 4.45 | 0 | 0 | 207.57 | 720 | 5.443 | 515 | 2803.145 | 2005790.4047 | 2018264.4 | 99.38%
97 | VINDHYACHAL(POOLING)-SASAN II 400kV | INTRA | 0 | 0 | 0 | 0.49167 | 0 | 0 | 0 | 11.8 | 720 | 5.443 | 515 | 2803.145 | 2018264.4 | 2018264.4 | 100%
98 | SASAN-SATNA I 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 245.7 | 1732.6455 | 425711.0001 | 306511920.0879 | 306511920.0879 | 100%
99 | BINA-BINA(MP) III 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.62 | 515 | 319.3 | 229896 | 229896 | 100%
100 | VAPI-NAVASARI(GIS) II 400kV | INTRA | 0.41042 | 0 | 0 | 0 | 9.85 | 0 | 0 | 0 | 720 | 116.879 | 515 | 60192.685 | 42745835.2528 | 43338733.2 | 98.63%
101 | SASAN-SATNA II 765kV | INTRA | 0.034722 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 720 | 242.23 | 1724.1068 | 417630.3842 | 300347243.4044 | 300693876.6233 | 99.88%
102 | BINA-BINA(MP) IV 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 0.62 | 515 | 319.3 | 229896 | 229896 | 100%
103 | INDORE(MP)-INDORE I 400kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 49.73 | 687 | 34164.51 | 24598447.2 | 24598447.2 | 100%
104 | INDORE(MP)-INDORE II 400kV | INTRA | 0 | 0 | 0 | 1899-12-31 13:55 | 0 | 0 | 0 | 37.92 | 720 | 49.73 | 687 | 34164.51 | 24598447.2 | 24598447.2 | 100%
105 | JABALPUR-JABALPUR(POOLING) I 400kV | INTRA | 0 | 0 | 0 | 0.14722 | 0 | 0 | 0 | 3.53 | 720 | 15.456 | 687 | 10618.272 | 7645155.84 | 7645155.84 | 100%
106 | JABALPUR-JABALPUR(POOLING) II 400kV | INTRA | 0 | 0 | 0 | 0.056944 | 0 | 0 | 0 | 1.37 | 720 | 15.456 | 687 | 10618.272 | 7645155.84 | 7645155.84 | 100%
107 | JABALPUR(POOLING)-BINA I 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 229.74 | 809.5333 | 185982.1691 | 133907161.7556 | 133907161.7556 | 100%
108 | JABALPUR(POOLING)-BINA II 765kV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 229.74 | 809.5333 | 185982.1691 | 133907161.7556 | 133907161.7556 | 100%
109 | SATNA-GWALIOR I 765kV | INTRA | 0 | 0 | 0 | 1900-01-01 14:52 | 0 | 0 | 0 | 62.87 | 720 | 336.63 | 1433.4388 | 482538.49 | 347427712.7812 | 347427712.7812 | 100%
110 | PIRANA-ASOJ I 400KV | INTRA | 0 | 0.0097222 | 0 | 0 | 0 | 0.23 | 0 | 0 | 719.77 | 143.539 | 687 | 98611.293 | 70977450.3626 | 70977450.3626 | 100%
111 | PIRANA-ASOJ II 400KV | INTRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 143.539 | 687 | 98611.293 | 71000130.96 | 71000130.96 | 100%
112 | NAVSARI(GIS)-KALA I 400kV | INTRA | 0 | 0 | 0 | 0.036806 | 0 | 0 | 0 | 0.88 | 720 | 140 | 515 | 72100 | 51912000 | 51912000 | 100%
113 | KALA-VAPI I 400kV | INTRA | 0 | 0 | 0 | 0.090278 | 0 | 0 | 0 | 2.17 | 720 | 49 | 515 | 25235 | 18169200 | 18169200 | 100%
114 | INDORE-ASOJ III 400kV | INTRA | 0.10556 | 0 | 0 | 1900-01-01 23:38 | 2.53 | 0 | 0 | 71.63 | 720 | 321.203 | 160.0813 | 51418.5789 | 36891287.7691 | 37021376.7736 | 99.65%
115 | BINA-GWALIOR III 765kV | INTRA | 0.10278 | 0 | 0 | 0 | 2.47 | 0 | 0 | 0 | 720 | 231.27 | 827.3453 | 191340.1495 | 137292297.4624 | 137764907.6317 | 99.66%
116 | AGRA-GWALIOR I 765kV | WR2-IR-1 | 0.049306 | 0 | 0 | 0 | 1.18 | 0 | 0 | 0 | 720 | 129.435 | 2250 | 291228.75 | 209341050.075 | 209684700 | 99.84%
117 | AGRA-GWALIOR II 765kV | WR2-IR-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 127.934 | 2250 | 287851.5 | 207253080 | 207253080 | 100%
118 | KANKROLI-ZERDA 400kV | WR2-IR-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 233.707 | 235.8922 | 55129.6505 | 39693348.3365 | 39693348.3365 | 100%
119 | BHINMAL-ZERDA 400kV | WR2-IR-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 142.8 | 272.0209 | 38844.5806 | 27968098.0106 | 27968098.0106 | 100%
120 | KANKROLI-BHINMAL 400kV | WR2-IR-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 201.8 | 224.5689 | 45318.014 | 32628970.0834 | 32628970.0834 | 100%
121 | ICT1 JABALPUR 400/220kV | ICT | 0 | 0 | 0 | 0.034028 | 0 | 0 | 0 | 0.82 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
122 | ICT2 JABALPUR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
123 | ICT1 DEHGAM 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
124 | ICT2 DEHGAM 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
125 | ICT1 SATNA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
126 | ICT2 SATNA 400/220KV | ICT | 0.12639 | 0 | 0 | 0 | 3.03 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 225845.55 | 226800 | 99.58%
127 | ICT1 KHANDWA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
128 | ICT2 KHANDWA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
129 | ICT1 VAPI 400/220KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
130 | ICT2 VAPI 400/220KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
131 | ICT1 GWALIOR 400/220kV | ICT | 0.20903 | 0 | 0 | 0 | 5.02 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 225218.7 | 226800 | 99.3%
132 | ICT1 RAJGARH 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
133 | ICT2 GWALIOR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
134 | ICT ITARSI 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
135 | ICT1 DAMOH 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
136 | ICT2 DAMOH 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
137 | ICT2 RAJGARH 400/220KV | ICT | 0.46806 | 0 | 0 | 0 | 11.23 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 223262.55 | 226800 | 98.44%
138 | ICT BINA 400/220kV | ICT | 0.08125 | 0 | 0 | 0 | 1.95 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226185.75 | 226800 | 99.73%
139 | ICT1 PIRANA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
140 | ICT2 PIRANA 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
141 | ICT3 GWALIOR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
142 | ICT1 SHUJALPUR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
143 | ICT1 BHACHAU 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
144 | ICT2 BHACHAU 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
145 | ICT2 SHUJALPUR 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
146 | ICT1 SATNA 765/400KV | ICT | 0.22639 | 0 | 0 | 0 | 5.43 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 714570 | 720000 | 99.25%
147 | ICT2 NAVSARI(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
148 | ICT1 NAVSARI(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
149 | ICT2 SATNA 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 720000 | 720000 | 100%
150 | ICT1 BINA 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 720000 | 720000 | 100%
151 | ICT3 VAPI 400/220KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
152 | ICT2 BINA 765/400KV | ICT | 0.24931 | 0 | 0 | 0 | 5.98 | 0 | 0 | 0 | 720 | 1000 | 1 | 1000 | 714020 | 720000 | 99.17%
153 | ICT1 GWALIOR 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100%
154 | ICT2 GWALIOR 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100%
155 | ICT2 INDORE 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100%
156 | ICT1 INDORE 765/400KV | ICT | 0 | 0 | 0 | 0.38889 | 0 | 0 | 0 | 9.33 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100%
157 | ICT1 JABALPUR 765/400KV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100%
158 | ICT2 JABALPUR 765/400KV | ICT | 0 | 0 | 0 | 0.34236 | 0 | 0 | 0 | 8.22 | 720 | 1500 | 1 | 1500 | 1080000 | 1080000 | 100%
159 | ICT1 KALA(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
160 | ICT2 KALA(GIS) 400/220kV | ICT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 315 | 1 | 315 | 226800 | 226800 | 100%
161 | BUS REACTOR I DEHGAM 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
162 | BUS REACTOR I JABALPUR 33kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25 | 1 | 25 | 18000 | 18000 | 100%
163 | BUS REACTOR II JABALPUR 33kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 25 | 1 | 25 | 18000 | 18000 | 100%
164 | BUS REACTOR I ITARSI 400kV | BR | 0 | 0 | 0 | 1900-01-29 | 0 | 0 | 0 | 720 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100%
165 | BUS REACTOR II ITARSI 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100%
166 | BUS REACTOR III ITARSI 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100%
167 | BUS REACTOR I JABALPUR 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
168 | BUS REACTOR DHULE 400kV | BR | 0 | 0 | 0 | 1900-01-08 08:59 | 0 | 0 | 0 | 224.98 | 720 | 80 | 1 | 80 | 57600 | 57600 | 100%
169 | BUS REACTOR I SATNA 400kV | BR | 0 | 0 | 0 | 1899-12-31 04:44 | 0 | 0 | 0 | 28.73 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100%
170 | BUS REACTOR BINA 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
171 | BUS REACTOR DAMOH 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
172 | BUS REACTOR I GWALIOR 400kV | BR | 0 | 0 | 0 | 1900-01-28 17:35 | 0 | 0 | 0 | 713.58 | 720 | 50 | 1 | 50 | 36000 | 36000 | 100%
173 | BUS REACTOR I KHANDWA 400kV | BR | 0 | 0 | 0 | 0.325 | 0 | 0 | 0 | 7.8 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
174 | BUS REACTOR II DEHGAM 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
175 | BUS REACTOR BHACHAU 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
176 | BUS REACTOR I SHUJALPUR 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
177 | BUS REACTOR RAJGARH 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
178 | BUS REACTOR SATNA 765kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
179 | BUS REACTOR NAVSARI 400kV | BR | 0 | 0 | 0 | 1900-01-04 02:57 | 0 | 0 | 0 | 122.95 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
180 | SWITCHABLE LINE REACTOR BINA I 765kV AT SATNA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
181 | SWITCHABLE LINE REACTOR BINA II 765kV AT SATNA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
182 | BUS REACTOR II SATNA 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
183 | SWITCHABLE LINE REACTOR BINA I 765kV AT GWALIOR | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
184 | SWITCHABLE LINE REACTOR BINA II 765kV AT GWALIOR | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
185 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT NAGDA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
186 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT NAGDA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
187 | BUS REACTOR II GWALIOR 400kV | BR | 0 | 0 | 0 | 1900-01-11 03:19 | 0 | 0 | 0 | 291.32 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
188 | BUS REACTOR III GWALIOR 400kV | BR | 0 | 0 | 0 | 0.64306 | 0 | 0 | 0 | 15.43 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
189 | BUS REACTOR I INDORE 400kV | BR | 0 | 0 | 0 | 1900-01-02 18:38 | 0 | 0 | 0 | 90.63 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
190 | SWITCHABLE LINE REACTOR INDORE 765kV AT BINA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
191 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT BINA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
192 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT BINA | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
193 | BUS REACTOR I INDORE 765kV | BR | 0 | 0 | 0 | 0.5375 | 0 | 0 | 0 | 12.9 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
194 | SWITCHABLE LINE REACTOR BINA I 765kV AT JABALPUR (POOLING) | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
195 | BUS REACTOR JABALPUR(POOLING) 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
196 | BUS REACTOR BINA 765kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
197 | BUS REACTOR JABALPUR POOLING 765kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 240 | 1 | 240 | 172800 | 172800 | 100%
198 | BUS REACTOR II KHANDWA 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
199 | BUS REACTOR II JABALPUR 400kV | BR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 125 | 1 | 125 | 90000 | 90000 | 100%
200 | BUS REACTOR KALA(GIS) 400kV | BR | 0 | 0 | 0 | 1900-01-03 13:55 | 0 | 0 | 0 | 109.92 | 720 | 80 | 1 | 80 | 57600 | 57600 | 100%
201 | BUS REACTOR II INDORE 400kV | BR | 0 | 0 | 0 | 0.29653 | 0 | 0 | 0 | 7.12 | 720 | 63 | 1 | 63 | 45360 | 45360 | 100%
| GRAND TOTAL= |  | 1900-01-04 06:26 | 1900-01-22 07:54 | 1899-12-31 19:58 | 1900-06-27 01:14 | 126.41 | 559.9 | 43.98 | 4297.25
A | AVAILABILITY OF LINES= |  |  | IR Lines | [5 empty] | ∑Wi (Ti - TNAi) = |  | 6899202266.0487
| No. of lines= O= |  | 115 | 2 | [5 empty] | (Ti x Wi) = |  | 6905799373.9451
| Line Outages Hrs = |  | 92.59 | 1.18 |  |  |  |  | AVAILABILITY OF LINES=Avo= |  |  | 99.9%
| Total Line Ckt.kM |  | 18170.507 | 257.369
B | AVAILABILITY OF ICTs= | [8 empty] | ∑Wk (Tk - TNAk) = |  | 16145902.55
| No. of ICTs= q= |  | 40 | [6 empty] | (Tk x Wk) = |  | 16164000
| ICTs Outages Hrs = |  | 32.64 | [5 empty] | AVAILABILITY OF ICTs=Avq= |  |  | 99.89%
C | AVAILABILITY OF BUS REACTORS= | [8 empty] | ∑Wm (Tm - TNAm) = |  | 3458880
| No. of Reactors= r = |  | 41 | [6 empty] | (Tm x Wm) = |  | 3458880
| Reactors Outages Hrs = |  | 0 | [5 empty] | AVAILABILITY OF BRs=Avr= |  |  | 100%
D | % TAFM OF AC SYSTEM= ( o X Avo + q X Avq + r X Avr) / (o+q+r) = | [10 empty] | 99.92%
E | AVAILABILITY OF 765KV AGRA - GWALIOR # 1 LINE= | [8 empty] | ∑Wi (Ti - TNAi) = |  | 209341050.075
| No. of lines= O= |  | 1 | [6 empty] | (Ti x Wi) = |  | 209684700
| Line Outages Hrs = |  | 1.18 | [5 empty] | AVAILABILITY OF LINES=Avo= |  |  | 99.84%
| Total Line Ckt.kM |  | 129.435
F | AVAILABILITY OF 765KV AGRA - GWALIOR # 2, 400KV ZERDA-KANKROLI, 400KV ZERDA-BHINMAL & 400KV BHINMAL-KANKROLI LINE= | [8 empty] | ∑Wi (Ti - TNAi) = |  | 307543496.4304
| No. of lines= O= |  | 4 | [6 empty] | (Ti x Wi) = |  | 307543496.4304
| Line Outages Hrs = |  | 0 | [5 empty] | AVAILABILITY OF LINES=Avo= |  |  | 100%
| Total Line Ckt.kM |  | 706.241
Formulas:
PG = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$J6:J219)
OTHERS = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$K6:K219)
SYSTEM = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$L6:L219)
DEEMED = SUMIF('TRIP-WR-II'!$C6:C219,[Element Name],'TRIP-WR-II'!$M6:M219)

## ANX-II
MONTH : JUN 2014
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : JUN 2014
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
JUN 2014
Sl. No. | Name of Elements | Type of failures | Restoration Time (Days) |  |  | Remarks
A |  | Elements of transmission line for Single, Double and Multi circuit towers for each KV class seperately.
1 |  | Insualtor Failure | Terrain Type
|  |  | Plain | River bed | Hilly
i | KAKRAPAR-VAPI II 220kV | Insualtor Failure in single phase | Less than 1 day
| KAKRAPAR-VAPI II 220kV |  | Less than 1 day
| KAKRAPAR-HALDARWA I 220kV |  | Less than 1 day
| SATNA-BINA I 400kV |  | Less than 1 day
| VAPI-NAVASARI(GIS) II 400kV |  | Less than 1 day
| KHANDWA-DHULE I 400kV |  | Less than 1 day
| KHANDWA-DHULE I 400kV |  | Less than 1 day
ii |  | Insualtor Failure in two phases | NIL
ii |  | Insualtor Failure in three phases
2 |  | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 |  | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 |  | Tower Damage ( not collapse)
i |  | One arm damage
ii |  | Two arm damage
5 |  | Snapping of phase conductor
i |  | Conductor snapping in single phase
ii |  | Conductor snapping in two phases
iii |  | Conductor snapping in three phases
6 |  | Failure of Earth wire
7 |  | Insulator failure with conductor snapping
8 |  | Any other combination of failures
B |  | Elements of sub-station for each KV class seperately
1 |  | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
|  | Other major failures in ICTs | Single phase Unit |  | Three phase Unit
| ICT2 RAJGARH 400/220KV | (i) Replacement of faulty bushings | Less than 1 day
| ICT1 GWALIOR 400/220kV |  | Less than 1 day
|  | (ii) Replacement of failed/blasted bushings | NIL
(iii) Replacement of faulty tap changers
2 |  | Failures of Reactors
Restoration of failed Reactors

## Supporting Annex V
Supporting Annex V
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF JUNE -2014 | [17 empty] | O
S
|  | WRTS-II | MONTH: | 2014-06-14 |  |  |  |  | ATTRIBUTED TO ( IN HRS:MIN) | [5 empty] | UNIT OUT DUE TO TRIPPING OF LINE |  |  | D | Outage in Days |  |  |  | REMARKS
SN | EVENT NO. | NAME OF LINE/ICT | OWNERSHIP | Cumulative Tripping till last months | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | LICENCEE | OTHERS | SYSTEM CONSTR. | DEEMED AVAILABLE | OUTAGE CATEGORY | OUTAGE CATEGORY |  | REASON | Tripping Code | Charging Code | Flashover | Snapping | Collapes of Tower | Bushing Replacement
76 | 906071 | KAKRAPAR-VAPI II 220kV | WRTS-II | 1 | 2014-06-14 | 04:21 | 2014-06-14 | 04:53 | 0.022222 | 0 | 0 | 0 | L | LHWT | N | Line A/T on R ph to E/F, F/L 15.16km from Vapi, due to failure of R phase insulator string at location no. 335. |  | LD 06/1401 | 0.022222
80 | 906075 | KAKRAPAR-VAPI II 220kV | WRTS-II | 1 | 2014-06-14 | 13:59 | 2014-06-14 | 22:04 | 0.33681 | 0 | 0 | 0 | L | OSPT | N | Line H/T to avail S/D for replacement of flashed over insulator of R phase at Location no 335. | LD 06/1451 | LD 06/1495 | 0.33681
91 | 906086 | KAKRAPAR-HALDARWA I 220kV | WRTS-II | 1 | 2014-06-15 | 05:53 | 2014-06-15 | 22:10 | 0.67847 | 0 | 0 | 0 | L | LHWT | N | Line A/T on R-ph to E/F, F/L - 6.5kms from Haldarwa due to failure of insulator string at Location no. 204. |  | LD 06/1599 | 0.67847
92 | 906087 | ICT2 RAJGARH 400/220KV | WRTS-II | 1 | 2014-06-15 | 07:08 | 2014-06-15 | 16:35 | 0.39375 | 0 | 0 | 0 | L | OSPT | N | S/D availed for replacement of 220kV side B-ph Bushing due to high Tan delta value. | LD 06/1529 | LD 06/1570 |  |  |  | 0.39375
93 | 906088 | SATNA-BINA I 400kV | WRTS-II | 1 | 2014-06-15 | 09:50 | 2014-06-15 | 13:28 | 0.15139 | 0 | 0 | 0 | L | OSPT | N | S/D availed for rectification of failed inner V string at location no. 483. | LD 06/1541 | LD 06/1557 | 0.15139
138 | 906133 | ICT1 GWALIOR 400/220kV | WRTS-II | 1 | 2014-06-21 | 13:44 | 2014-06-21 | 18:45 | 0.20903 | 0 | 0 | 0 | L | OSPT | N | ICT H/T to avail S/D for replacement of 220kV side Y phase bushing. | LD 06/2221 | LD 06/2266 |  |  |  | 0.20903
168 | 906163 | VAPI-NAVASARI(GIS) II 400kV | WRTS-II | 1 | 2014-06-25 | 09:23 | 2014-06-25 | 19:14 | 0.41042 | 0 | 0 | 0 | L | OSPT | N | H/T to avail S/D by PG for attending insulator flashover at Location no. -14. | LD 06/2680 | LD 06/2727 | 0.41042
190 | 906185 | KHANDWA-DHULE I 400kV | WRTS-II | 1 | 2014-06-27 | 15:24 | 2014-06-27 | 21:33 | 0.25625 | 0 | 0 | 0 | L | OSPT | N | S/D availed by WR-I for replacement of failed insulator inner V string at location no:854. | LD 06/2973 | LD 06/3017 | 0.25625
198 | 906193 | KHANDWA-DHULE I 400kV | WRTS-II | 1 | 2014-06-28 | 17:39 | 2014-06-29 | 01:01 | 0.30694 | 0 | 0 | 0 | L | OSPT | N | S/D availed by WR-I for replacement of failed insulator inner V string at location no:854. | LD 06/3099 | LD 06/3130 | 0.30694
[9 empty] | 1900-01-01 18:22 | 0 | 0 | 0
Note on C4: Enter company name here
Note on E4: Enter Month for which data is sent in date format