## Tripping AC SYSTEM (hidden)
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR MARCH- 2011
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032
5 | 400kV Indore-Asoj # 2 | 8 | 38 |  |  | 8.6333 | 0 | 744 | 273 | 2 | 4713.8 | 546 | 406224
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
8 | 400 KV Jabalpur - Itarsi # 1 | 4 | 54 |  |  | 4.9 | 0 | 744 | 232 | 2 | 2273.6 | 464 | 345216
9 | 400 KV Jabalpur - Itarsi # 2 | 6 | 25 |  |  | 6.4167 | 0 | 744 | 232 | 2 | 2977.3333 | 464 | 345216
10 | 400kV Jhanor-Dehgam#1 | 0 | 0 |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616
11 | 400kV Jhanor-Dehgam#2 | 12 | 59 |  |  | 12.9833 | 0 | 744 | 157 | 2 | 4076.7667 | 314 | 233616
12 | 400 KV V'chal - Jabalpur # 3 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
13 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
14 | 400 KV Jabalpur - Itarsi # 3 | 4 | 45 |  |  | 4.75 | 0 | 744 | 234 | 2 | 2223 | 468 | 348192
15 | 400 KV Jabalpur - Itarsi # 4 | 5 | 52 |  |  | 5.8667 | 0 | 744 | 234 | 2 | 2745.6 | 468 | 348192
16 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
17 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
18 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
19 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
20 | 400 KV Jhanor - Sugen(PGCIL portion) | 13 | 31 | 0 | 51 | 13.5167 | 0.85 | 743.15 | 57 | 2 | 1540.9 | 114 | 84719.1
21 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 9 | 3 | 0 | 9.05 | 734.95 | 110 | 2 | 0 | 220 | 161689
22 | 400 KV Jhanor - Jhanor(GPEC) |  |  | 1 | 88 | 0 | 2.4667 | 741.5333 | 13 | 2 | 0 | 26 | 19279.8667
23 | 220kV Jhanor-Haldarwa ckI # 1 | 0 | 15 | 3 | 42 | 0.25 | 3.7 | 740.3 | 13 | 1 | 3.25 | 13 | 9623.9
24 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  | 71 | 0 | 1.1833 | 742.8167 | 13 | 1 | 0 | 13 | 9656.6167
25 | 220kV Kawas-Navsari ckt # 1 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 49 | 1 | 17.9667 | 49 | 36456
26 | 220kV Kawas-Navsari ckt # 2 | 0 | 13 | 0 | 52 | 0.21667 | 0.86667 | 743.1333 | 49 | 1 | 10.6167 | 49 | 36413.5333
27 | 220kV Kawas-Ichchapur |  |  |  |  | 0 | 0 | 744 | 3 | 1 | 0 | 3 | 2232
28 | 220kV Kawas-Vav |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528
29 | 220kV Kawas - Haldarwa # 1 | 0 | 80 | 8 | 25 | 1.3333 | 8.4167 | 735.5833 | 81 | 1 | 108 | 81 | 59582.25
30 | 220kV Kawas-Haldarwa # 2 |  |  | 0 | 33 | 0 | 0.55 | 743.45 | 81 | 1 | 0 | 81 | 60219.45
31 | 220 kV Kakrapar - Haldarwa # 1 | 5 | 20 |  | 74 | 5.3333 | 1.2333 | 742.7667 | 74 | 1 | 394.6667 | 74 | 54964.7333
32 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 74 | 1 | 0 | 74 | 55012.8333
33 | 220 KV Kakrapar - Vav # 1 |  |  | 1 | 18 | 0 | 1.3 | 742.7 | 43 | 1 | 0 | 43 | 31936.1
35 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992
35 | 220kV Kakrapar-Vapi ckt # 1 | 0 | 26 |  |  | 0.43333 | 0 | 744 | 117 | 1 | 50.7 | 117 | 87048
36 | 220kV Kakrapar-Vapi ckt # 2 | 0 | 53 | 7 | 82 | 0.88333 | 8.3667 | 735.6333 | 117 | 1 | 103.35 | 117 | 86069.1
37 | 220kV Ichchapur-Vav |  |  |  |  | 0 | 0 | 744 | 34 | 1 | 0 | 34 | 25296
38 | 400kV V'chal - Satna # 1 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 267 | 2 | 0 | 534 | 397171.4
39 | 400kV V'chal - Satna # 2 | 0 | 50 | 0 | 18 | 0.83333 | 0.3 | 743.7 | 267 | 2 | 445 | 534 | 397135.8
40 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
41 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
42 | 400kV Satna - Bina # 1 | 0 | 24 |  |  | 0.4 | 0 | 744 | 276 | 2 | 220.8 | 552 | 410688
43 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688
44 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  | 1 | 49 | 0 | 1.8167 | 742.1833 | 0.742 | 2 | 0 | 1.484 | 1101.4001
45 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  | 1 | 50 | 0 | 1.8333 | 742.1667 | 0.742 | 2 | 0 | 1.484 | 1101.3753
46 | 400 kV Gwalior-Bina # 1 | 5 | 38 |  |  | 5.6333 | 0 | 744 | 234.931 | 4 | 5293.7785 | 939.724 | 699154.656
47 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
48 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
49 | 400KV Bina - Nagda # 1 | 0 | 18 |  |  | 0.3 | 0 | 744 | 330.155 | 2 | 198.093 | 660.31 | 491270.64
50 | 400KV Bina - Nagda # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 330.155 | 2 | 0 | 660.31 | 491160.5883
51 | 400KV Nagda - Dehgam # 2 |  |  | 3 | 58 | 0 | 3.9667 | 740.0333 | 331.442 | 2 | 0 | 662.884 | 490556.2561
52 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696
53 | 400KV Seoni - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
54 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
55 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
56 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
57 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
58 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
59 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
60 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
61 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
62 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
63 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
64 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
65 | 400 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352
66 | 400 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2
67 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848
68 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4
69 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
70 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
71 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
72 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
73 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
74 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
| Total Sr.No. 1 to 74 | 73 | 705 | 34 | 773 | 73.05 |  |  | 12271.634 |  | 27397.2215 |  | 19691267.3032
|  |  | 84.75 |  | 46.8833 |  |  |  |  | NAFM | 0.0013913
| Availability of 74 ( Sl no 1 to 74) transmission lines during MARCH-2011 = | [8 empty] | TAFM | 99.8609
Sr.No. 71,72,73 & 74 lines are declared for commercial operation w.e.f. 01.03.11
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
0.63333
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0.83333
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
10 | 400/220kV ICT # 2 / Vapi | 11 | 51 |  |  | 11.85 | 0 | 744 | 315 | 2.5 | 9331.875 | 787.5 | 585900
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
14 | 400/220kV ICT # 1 / Itarsi | 2 | 48 |  |  | 2.8 | 0 | 744 | 315 | 2.5 | 2205 | 787.5 | 585900
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
| Total Sr.No. 1 to 19 | 13 | 99 | 0 | 0 | 14.65 |  |  | 5040 | 47.5 | 11536.875 |  | 11132100
|  | 14.65 |  | 0 | [5 empty] | NAFM | 0.0010364
[10 empty] | TAFM | 99.8964
Availability of 19 ( Sl no 1 to 19) ICTs in MARCH-2011 =
ICT # 1 at Pirana was declared for commercial operation w.e.f. 01.03.11
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
| Total of sl no 1 to 14 | 0 | 0 | 0 | 0 |  |  |  | 882 | 56 | 0 |  | 2624832
0
[8 empty] | NAFM | 0
| Availability of 14( Sl no 1 to 14) Bus Reactors in MARCH-2011 = | [6 empty] | TAFM | 100
[11 empty] | 38934.0965 |  | 33448199.3032
[8 empty] | NAFM = | 0.001164
| % System Availability for MARCH 2011 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.8836
3
Note on B43: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B45: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B47: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B49: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B187: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B189: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## INDEX
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR DECEMBER - 2012
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length |  |  |  |  | Element_wise_%availability | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 100 | 90%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 100 | 90%
3 | 400kV Itarsi-Indore # 2 |  |  | 0 | 16 | 0 | 0.26667 | 743.7333 | 214 | 2 | 0 | 428 | 318317.8667 | 100 | 90%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 100 | 90%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 100 | 90%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 100 | 90%
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 100 | 90%
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 100 | 90%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 100 | 90%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 100 | 90%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 100 | 90%
12 | 400 KV Jabalpur-Sasan |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 376 | 2 | 0 | 752 | 559049.3333 | 100 | 90%
13 | 400kV Sasan-Vindhyachal |  |  | 1 | 15 | 0 | 1.25 | 742.75 | 21 | 2 | 0 | 42 | 31195.5 | 100 | 90%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 100 | 90%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 100 | 90%
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 100 | 90%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 100 | 90%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 100 | 90%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 100 | 90%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 100 | 90%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 100 | 90%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 2 | 16 | 0 | 2.2667 | 741.7333 | 110 | 2 | 0 | 220 | 163181.3333 | 100 | 90%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 100 | 90%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 100 | 90%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 100 | 90%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 100 | 90%
27 | 220kV Kawas-Navsari (GIS)#2 | 0 | 27 |  |  | 0.45 | 0 | 744 | 58.149 | 1 | 26.167 | 58.149 | 43262.856 | 99.9395 | 90%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 0 | 17 | 11 | 9 | 0.28333 | 11.15 | 732.85 | 31.334 | 1 | 8.878 | 31.334 | 22963.1219 | 99.9613 | 90%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 31.334 | 1 | 11.4891 | 31.334 | 23312.496 | 99.9507 | 90%
30 | 220kV Kawas-Vav#1 |  |  | 0 | 26 | 0 | 0.43333 | 743.5667 | 37 | 1 | 0 | 37 | 27511.9667 | 100 | 90%
31 | 220kV Kawas-Vav#2 | 0 | 10 | 5 | 34 | 0.16667 | 5.5667 | 738.4333 | 37 | 1 | 6.1667 | 37 | 27322.0333 | 99.9774 | 90%
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 100 | 90%
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 100 | 90%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 100 | 90%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 100 | 90%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 100 | 90%
37 | 220 KV Kakrapar - Vav # 2 |  |  | 2 | 34 | 0 | 2.5667 | 741.4333 | 43 | 1 | 0 | 43 | 31881.6333 | 100 | 90%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 100 | 90%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 100 | 90%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 100 | 90%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 100 | 90%
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 100 | 90%
43 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 100 | 90%
44 | 400kV Satna - Bina # 1 | 21 | 3 |  |  | 21.05 | 0 | 744 | 276 | 2 | 11619.6 | 552 | 410688 | 97.1707 | 90%
45 | 400kV Satna - Bina # 2 | 9 | 20 |  |  | 9.3333 | 0 | 744 | 276 | 2 | 5152 | 552 | 410688 | 98.7455 | 90%
46 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 100 | 90%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 100 | 90%
48 | 765 kV Gwalior-Bina # 1 * | 7 | 37 |  |  | 7.6167 | 0 | 744 | 234.931 | 4 | 7157.5645 | 939.724 | 699154.656 | 98.9763 | 90%
49 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 100 | 90%
50 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 100 | 90%
51 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 100 | 90%
52 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 100 | 90%
53 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 100 | 90%
54 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 100 | 90%
55 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 100 | 90%
56 | 400KV Nagda - Dehgam # 1 |  |  | 1 | 12 | 0 | 1.2 | 742.8 | 331.442 | 2 | 0 | 662.884 | 492390.2352 | 100 | 90%
57 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 100 | 90%
58 | 400KV Seoni - Khandwa # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 100 | 90%
59 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 100 | 90%
60 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 114 | 8 | 0 | 114.1333 | 629.8667 | 4.01 | 2 | 0 | 8.02 | 5051.5307 | 100 | 90%
61 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 4.01 | 2 | 0 | 8.02 | 5965.0087 | 100 | 90%
62 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  | 1 | 6 | 0 | 1.1 | 742.9 | 4.12 | 2 | 0 | 8.24 | 6121.496 | 100 | 90%
63 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 100 | 90%
64 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 100 | 90%
65 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 100 | 90%
66 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 100 | 90%
67 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 100 | 90%
68 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 100 | 90%
69 | 765 kV Gwalior-Bina # 2 * | 6 | 56 |  |  | 6.9333 | 0 | 744 | 233.652 | 4 | 6479.9488 | 934.608 | 695348.352 | 99.0681 | 90%
70 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 100 | 90%
71 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 100 | 90%
72 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 100 | 90%
73 | 220 KV Vapi - Khadoli # 1 |  |  | 0 | 28 | 0 | 0.46667 | 743.5333 | 28.549 | 1 | 0 | 28.549 | 21227.1331 | 100 | 90%
74 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 100 | 90%
75 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 100 | 90%
76 | 400kV Damoh-Birsinghpur#2 | 0 | 7 |  |  | 0.11667 | 0 | 744 | 228.474 | 2 | 53.3106 | 456.948 | 339969.312 | 99.9843 | 90%
77 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 100 | 90%
78 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 100 | 90%
79 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 100 | 90%
80 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 100 | 90%
81 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 100 | 90%
82 | 400kV Bhachau - Ranchodpura # 2 | 3 | 5 |  |  | 3.0833 | 0 | 744 | 282.856 | 3 | 2616.418 | 848.568 | 631334.592 | 99.5856 | 90%
83 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 100 | 90%
84 | 400kV Mundra - Limbdi # 2 |  |  | 0 | 19 | 0 | 0.31667 | 743.6833 | 314.053 | 3 | 0 | 942.159 | 700667.9457 | 100 | 90%
85 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 100 | 90%
86 | 765kV Satna - Bina # 2 |  |  | 467 | 35 | 0 | 467.5833 | 276.4167 | 275.635 | 4 | 0 | 1102.54 | 304760.4317 | 100 | 90%
87 | 765kV Bina - Indore * |  |  |  |  | 0 | 0 | 744 | 311.17 | 4 | 0 | 1244.68 | 926041.92 | 100 | 90%
88 | 400kV Gandhar - Navsari # 2 |  |  | 0 | 55 | 0 | 0.91667 | 743.0833 | 102.15 | 2 | 0 | 204.3 | 151811.925 | 100 | 90%
89 | LILO of Mundra-Limbdi#1 at Jetpur (GETCO) |  |  |  |  | 0 | 0 | 744 | 313 | 3 | 0 | 939 | 698616 | 100 | 90%
90 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.15 | 2 | 0 | 204.3 | 151999.2 | 100 | 90%
| Total Sr.No. 1 to 90 | 46 | 204 | 604 | 382 | 49.4 |  |  | 15175.643 |  | 33131.5427 |  | 25989575.3626
* | Lines charged with 400kV level
|  |  | 49.4 |  | 610.3667
[10 empty] | NAFM | 0.0012748
| Availability of 90 ( Sl no 1 to 90) transmission lines during DECEMBER -2012 = | [8 empty] | TAFM | 99.8725
1 | 400 kV Gwalior -Agra # 1 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 129.435 | 4 | 0 | 517.74 | 385198.56 | 100 | 90%
1 | 400 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 100 | 90%
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  |  | Element_wise_%availability | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  | 0 | 3 | 0 | 0.05 | 743.95 | 315 | 2.5 | 0 | 787.5 | 585860.625 | 100 | 90%
2 | 400/220kV ICT # 2 /Jabalpur. |  |  | 1 | 43 | 0 | 1.7167 | 742.2833 | 315 | 2.5 | 0 | 787.5 | 584548.125 | 100 | 90%
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
6 | 400/220kV ICT # 2 / Satna | 4 | 35 |  |  | 4.5833 | 0 | 744 | 315 | 2.5 | 3609.375 | 787.5 | 585900 | 99.384 | 90%
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
10 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
14 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
20 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
21 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
22 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
23 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
24 | 400/220 KV ICT # 2 / Bhachau | 6 | 2 |  |  | 6.0333 | 0 | 744 | 315 | 2.5 | 4751.25 | 787.5 | 585900 | 99.1891 | 90%
25 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
26 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100 | 90%
27 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
28 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 90%
29 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100 | 90%
30 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100 | 90%
| Total Sr.No. 1 to 30 | 10 | 37 | 1 | 46 | 10.6167 |  |  | 11505 | 75 | 8360.625 |  | 21397908.75
Availability of 30 ( Sl no 1 to 30) ICTs in DECEMBER -2012 =
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR |  |  |  | Element_wise_%availability | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 100 | 90%
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 100 | 90%
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100 | 90%
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100 | 90%
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100 | 90%
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 100 | 90%
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100 | 90%
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100 | 90%
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100 | 90%
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100 | 90%
15 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
16 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
17 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100 | 90%
18 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100 | 90%
19 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100 | 90%
20 | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100 | 90%
21 | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100 | 90%
| Total of sl no 1 to 21 | 0 | 0 | 0 | 0 |  |  |  | 1916 | 84 | 0 |  | 5702016
0
[8 empty] | NAFM | 0
| Availability of 21( Sl no 1 to 21) Bus Reactors in DECEMBER -2012 = | [6 empty] | TAFM | 100
[11 empty] | 41492.1677 |  | 53089500.1125
[8 empty] | NAFM = | 0.00078155
| % System Availability for DECEMBER 2012 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.9218
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B30: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B123: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B124: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## DEC 12
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | CAT CODE | Details | % Availability
[8 empty] | OTHERS | SYSTEM CONSTR.
1 | 912052 | SATPURA-ITARSI 400kV | 2012-12-11 | 09:51 | 2012-12-11 | 18:11 | - | - | - | 0.34722 | OSFD | Line H/T to avail emergency S/D by MPPTCL | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.34722
2 |  | ITARSI-INDORE I 400kV |  |  |  |  | - | - | - | - |  |  | 100
3 | 912036 | ITARSI-INDORE II 400kV | 2012-12-07 | 06:11 | 2012-12-07 | 06:11 | 0 | - | - | - | LART | A/R Successfully from Itarsi end but A/T at Indore end on B-ph to E/F, F/L - 182.7kM from Itarsi | 100
| 912037 |  | 2012-12-08 | 06:11 | 2012-12-08 | 06:27 | - | 0.011111 | - | - | OMSU | A/R Successfully from Itarsi end but A/T at Indore end on B-ph to E/F, F/L - 182.7kM from Itarsi
|  | SUBTOTAL |  |  |  |  | 0 | 0.011111 | 0 | 0
4 | 912005 | INDORE-ASOJ I 400kV | 2012-12-02 | 00:05 | 2012-12-02 | 07:15 | - | - | - | 0.29861 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912086 |  | 2012-12-17 | 23:05 | 2012-12-18 | 07:45 | - | - | - | 0.36111 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.65972
5 |  | INDORE-ASOJ II 400kV |  |  |  |  | - | - | - | - |  |  | 100
6 | 912135 | VINDHYACHAL-JABALPUR I 400kV | 2012-12-25 | 09:56 | 2012-12-25 | 22:36 | - | - | - | 0.52778 | LCSD | Line H/T for stringing of 765kV sasan satna line | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.52778
7 | 912136 | VINDHYACHAL-JABALPUR II 400kV | 2012-12-25 | 10:24 | 2012-12-25 | 22:43 | - | - | - | 0.51319 | LCSD | Line H/T for stringing of 765kV sasan satna line | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.51319
8 | 912098 | JABALPUR-ITARSI I 400kV | 2012-12-19 | 03:18 | 2012-12-19 | 06:31 | - | - | - | 0.13403 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912105 |  | 2012-12-20 | 03:09 | 2012-12-20 | 08:03 | - | - | - | 0.20417 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.33819
9 |  | JABALPUR-ITARSI # 2 400KV |  |  |  |  | - | - | - | - |  |  | 100
10 |  | GANDHAR-DEHGAM I 400kV |  |  |  |  | - | - | - | - |  |  | 100
11 |  | GANDHAR-DEHGAM II 400kV |  |  |  |  | - | - | - | - |  |  | 100
12 | 911102 | SASAN (RELIANCE) - JABALPUR 400kV | 2012-11-27 | 14:54 | 2012-12-06 | 09:58 | - | - | - | 1900-01-04 09:58 | LCSD | Line H/T for shifting of loopin circuit at sasan | 100
| 912163 |  | 2012-12-30 | 17:35 | 2012-12-30 | 18:10 | - | - | 0.024306 | - | GOVC | A/T on D/T received from SASAN due to operation of O/V Protection at SASAN.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.024306 | 1900-01-04 09:58
13 | 912162 | VINDHYACHAL (NTPC) -SASAN (RELIANCE) 400kV | 2012-12-30 | 17:20 | 2012-12-30 | 18:10 | - | 0.034722 | - | - | OMSU | H/T to facilitate firdt time charging of 400/765kV ICT at SASAN Reliance. | 100
| 912169 |  | 2012-12-31 | 15:38 | 2012-12-31 | 16:03 | - | 0.017361 | - | - | OMSU | H/T to facilitate firdt time charging of 400/765kV ICT at SASAN Reliance.
|  | SUBTOTAL |  |  |  |  | 0 | 0.052083 | 0 | 0
14 |  | VINDHYACHAL-JABALPUR IV 400kV |  |  |  |  | - | - | - | - |  |  | 100
15 |  | JABALPUR-ITARSI III 400kV |  |  |  |  | - | - | - | - |  |  | 100
16 |  | JABALPUR-ITARSI IV 400kV |  |  |  |  | - | - | - | - |  |  | 100
17 | 911112 | ITARSI-KHANDWA I 400kV | 2012-11-30 | 23:45 | 2012-12-01 | 07:39 | - | - | - | 0.31875 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912019 |  | 2012-12-04 | 23:04 | 2012-12-05 | 07:17 | - | - | - | 0.34236 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912040 |  | 2012-12-07 | 23:08 | 2012-12-08 | 06:02 | - | - | - | 0.2875 | LVRD | Line H/T on voltage regulation as WRLDC instruction
| 912068 |  | 2012-12-13 | 21:32 | 2012-12-14 | 07:04 | - | - | - | 0.39722 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912110 |  | 2012-12-21 | 01:49 | 2012-12-21 | 06:50 | - | - | - | 0.20903 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912134 |  | 2012-12-25 | 02:46 | 2012-12-25 | 08:32 | - | - | - | 0.24028 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912148 |  | 2012-12-27 | 22:37 | 2012-12-28 | 16:49 | - | - | - | 0.75833 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912159 |  | 2012-12-29 | 21:26 | 2012-12-30 | 06:56 | - | - | - | 0.39583 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 22:47
18 | 912013 | ITARSI-KHANDWA II 400kV | 2012-12-03 | 23:53 | 2012-12-04 | 09:14 | - | - | - | 0.38958 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912027 |  | 2012-12-05 | 22:11 | 2012-12-06 | 07:19 | - | - | - | 0.38056 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912034 |  | 2012-12-06 | 22:54 | 2012-12-07 | 06:26 | - | - | - | 0.31389 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912063 |  | 2012-12-12 | 23:35 | 2012-12-13 | 07:25 | - | - | - | 0.32639 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912115 |  | 2012-12-21 | 23:02 | 2012-12-22 | 07:13 | - | - | - | 0.34097 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912152 |  | 2012-12-28 | 22:27 | 2012-12-29 | 06:56 | - | - | - | 0.35347 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 02:31
19 |  | KHANDWA-DHULE I 400kV |  |  |  |  | - | - | - | - |  |  | 100
20 |  | KHANDWA-DHULE II 400kV |  |  |  |  | - | - | - | - |  |  | 100
21 |  | GANDHAR-SUGEN 400kV |  |  |  |  | - | - | - | - |  |  | 100
22 | 912127 | SUGEN-VAPI 400kV | 2012-12-23 | 11:12 | 2012-12-23 | 13:28 | - | 0.094444 | - | - | OMSU | H/T for installation of PMU at Suzan as per WRLDC instructions. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0.094444 | 0 | 0
23 | 912011 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | 2012-12-03 | 09:43 | 2012-12-03 | 20:06 | - | - | - | 0.43264 | OSPD | H/T to avail S/D by GTEC for replacement of B-ph LA. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.43264
24 |  | GANDHAR-HALDARWA I 220kV |  |  |  |  | - | - | - | - |  |  | 100
25 |  | GANDHAR-HALDARWA II 220kV |  |  |  |  | - | - | - | - |  |  | 100
26 | 912112 | KAWAS-NAVSARI (PG GIS) I 220kV | 2012-12-21 | 10:00 | 2012-12-21 | 20:25 | - | - | - | 0.43403 | OSPD | Line H/T to avail S/D by NTPC for relay testing at Kawas | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.43403
27 | 912046 | KAWAS-NAVSARI (PG GIS) II 220kV | 2012-12-09 | 22:59 | 2012-12-09 | 23:26 | 0.01875 | - | - | - | LEFT | A/T on RY Ph to Ph fault from both ends,F/L - 27kM from NAV (GIS). | 99.9395
| 912113 |  | 2012-12-21 | 13:02 | 2012-12-21 | 19:21 | - | - | - | 0.26319 | OSPD | Line H/T to avail S/D by NTPC for relay testing at Kawas
|  | SUBTOTAL |  |  |  |  | 0.01875 | 0 | 0 | 0.26319
28 | 912154 | NAVSARI (PG GIS)-NAVSARI I 220kV | 2012-12-29 | 07:19 | 2012-12-29 | 07:36 | 0.011806 | - | - | - | LEFT | A/T on Y-ph to E/F from both ends,F/L - 12.93kM (NAV GIS) | 99.9613
| 912156 |  | 2012-12-29 | 07:36 | 2012-12-29 | 18:45 | - | 0.46458 | - | - | OMSU | Test charging delayed by NAV GETCO due to CB Problem.
|  | SUBTOTAL |  |  |  |  | 0.011806 | 0.46458 | 0 | 0
29 | 912155 | NAVSARI (PG GIS)-NAVSARI II 220kV | 2012-12-29 | 07:19 | 2012-12-29 | 07:41 | 0.015278 | - | - | - | OMST | Line A/T at Navsari GIS only | 99.9507
|  | SUBTOTAL |  |  |  |  | 0.015278 | 0 | 0 | 0
30 | 912055 | KAWAS-VAV I 220kV | 2012-12-11 | 14:53 | 2012-12-11 | 15:19 | - | - | 0.018056 | - | LMAC | Line A/T on B ph to E/F due to burning of sugarcane waste. F/L:8.97kM from kawas | 100
| 912119 |  | 2012-12-22 | 13:25 | 2012-12-22 | 20:00 | - | - | - | 0.27431 | OSPD | Line H/T to avail S/D by NTPC Kawas for Relay Testing at Kawas
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.018056 | 0.27431
31 | 912168 | KAWAS-VAV II 220kV | 2012-12-31 | 11:49 | 2012-12-31 | 17:33 | 0.0069444 | 0.23194 | - | - | OMSU | A/T on R-ph to E/F, F/L - 10.54kM from VAV, Test charging delayed by VAV GETCO due to persisting of CB PD alarm. | 99.9774
|  | SUBTOTAL |  |  |  |  | 0.0069444 | 0.23194 | 0 | 0
101 | 912091 | KAWAS-ICHCHAPUR#2 220kV | 2012-12-18 | 09:35 | 2012-12-18 | 17:23 | - | - | - | 0.325 | OSPD | Line H/T to avail S/D by NTPC kawas
| 912092 |  | 2012-12-18 | 20:26 | 2012-12-18 | 21:09 | - | - | - | 0.029861 | OSFD | Line H/T due to sparking at kawas end
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.35486
32 | 911106 | KAWAS-HALDARWA I 220kV | 2012-11-28 | 10:02 | 2012-12-19 | 14:14 | - | - | - | 1900-01-17 14:14 | LPRD | H/T on Power Regulation on WRLDC Instructions. | 100
| 912146 |  | 2012-12-27 | 12:02 |  |  | - | - | - | 1900-01-02 11:58 | LPRD | H/T on Power Regulation on WRLDC Instructions.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-21 02:12
33 | 912100 | KAWAS-HALDARWA II 220kV | 2012-12-19 | 15:07 | 2012-12-27 | 12:01 | - | - | - | 1900-01-06 20:54 | LPRD | H/T on Power Regulation on WRLDC Instructions. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-06 20:54
34 | 912140 | KAKRAPAR-HALDARWA I 220kV | 2012-12-26 | 8:00 | 2012-12-26 | 19:16 | - | - | - | 0.46944 | OSPD | Line H/T to avail S/D by GETCO for stringing of line | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.46944
35 | 912141 | KAKRAPAR-HALDARWA II 220kV | 2012-12-26 | 8:00 | 2012-12-26 | 19:44 | - | - | - | 0.48889 | OSPD | Line H/T to avail S/D by GETCO for stringing of line | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.48889
36 |  | KAKRAPAR-VAV I 220kV |  |  |  |  | - | - | - | - |  |  | 100
37 | 912118 | KAKRAPAR-VAV II 220kV | 2012-12-22 | 10:20 | 2012-12-22 | 12:54 | - | 0.10694 | - | - | OMSU | Line A/T at Vav(GETCO) end only due to suspected DC earth leakege at Vav end | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0.10694 | 0 | 0
38 |  | KAKRAPAR-VAPI I 220kV |  |  |  |  | - | - | - | - |  |  | 100
39 |  | KAKRAPAR-VAPI II 220kV |  |  |  |  | - | - | - | - |  |  | 100
40 |  | VINDHYACHAL-SATNA I 400kV |  |  |  |  | - | - | - | - |  |  | 100
41 |  | VINDHYACHAL-SATNA II 400kV |  |  |  |  | - | - | - | - |  |  | 100
42 |  | VINDHYACHAL-SATNA III 400kV |  |  |  |  | - | - | - | - |  |  | 100
43 |  | VINDHYACHAL-SATNA IV 400kV |  |  |  |  | - | - | - | - |  |  | 100
44 | 912014 | SATNA-BINA(PG) I 400kV | 2012-12-03 | 23:59 | 2012-12-04 | 07:45 | - | - | - | 0.32361 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 97.1707
| 912021 |  | 2012-12-05 | 04:25 | 2012-12-05 | 07:50 | - | - | - | 0.14236 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912035 |  | 2012-12-06 | 23:08 | 2012-12-07 | 06:38 | - | - | - | 0.3125 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912041 |  | 2012-12-08 | 08:16 | 2012-12-08 | 19:37 | 0.47292 | - | - | - | OMST | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912045 |  | 2012-12-09 | 08:40 | 2012-12-09 | 18:22 | 0.40417 | - | - | - | OMST | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912074 |  | 2012-12-15 | 03:40 | 2012-12-15 | 06:21 | - | - | - | 0.11181 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912103 |  | 2012-12-19 | 22:44 | 2012-12-20 | 08:22 | - | - | - | 0.40139 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912130 |  | 2012-12-24 | 03:17 | 2012-12-24 | 06:40 | - | - | - | 0.14097 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912139 |  | 2012-12-26 | 02:54 | 2012-12-26 | 08:44 | - | - | - | 0.24306 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912161 |  | 2012-12-30 | 03:07 | 2012-12-30 | 07:05 | - | - | - | 0.16528 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912166 |  | 2012-12-31 | 00:04 | 2012-12-31 | 06:06 | - | - | - | 0.25139 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912171 |  | 2012-12-31 | 21:29 |  |  | - | - | - | 0.10486 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0.87708 | 0 | 0 | 1900-01-01 04:44
45 | 912001 | SATNA-BINA(PG) II 400kV | 2012-12-01 | 00:02 | 2012-12-01 | 07:50 | - | - | - | 0.325 | LVRD | Line H/T for voltage regulation on WRLDC instruction. | 98.7455
| 912003 |  | 2012-12-01 | 07:50 | 2012-12-01 | 18:55 | - | - | - | 0.46181 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912007 |  | 2012-12-02 | 02:52 | 2012-12-02 | 08:05 | - | - | - | 0.21736 | LVRD | Line H/T for voltage regulation on WRLDC instruction.
| 912009 |  | 2012-12-02 | 08:05 | 2012-12-02 | 18:29 | - | - | - | 0.43333 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912012 |  | 2012-12-03 | 10:06 | 2012-12-03 | 18:52 | - | - | - | 0.36528 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912015 |  | 2012-12-04 | 08:30 | 2012-12-04 | 18:06 | - | - | - | 0.4 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912023 |  | 2012-12-05 | 10:14 | 2012-12-05 | 18:51 | - | - | - | 0.35903 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912030 |  | 2012-12-05 | 23:25 | 2012-12-05 | 23:58 | 0.022917 | - | - | - | LEFT | Line A/T due to B ph to E/F .F/L:148.2 kM from Bina.
| 912031 |  | 2012-12-05 | 23:58 | 2012-12-06 | 09:25 | - | - | - | 0.39375 | LVRD | Line kept out on V/R on WRLDC instruction ( Test charging not permitted by WRLDC due to prevailing system high voltgae).
| 912032 |  | 2012-12-06 | 09:25 | 2012-12-06 | 12:13 | 0.11667 | - | - | - | LHWT | S/D availed by PowerGrid for replacement of B-ph insulator string at Loc 324. | No clear as the Shutdown was planned or not ,and its maintenance work not new system excecution (OMST)
| 912048 |  | 2012-12-10 | 13:07 | 2012-12-10 | 19:06 | 0.24931 | - | - | - | OMST | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
| 912080 |  | 2012-12-16 | 03:33 | 2012-12-16 | 06:14 | - | - | - | 0.11181 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912095 |  | 2012-12-19 | 00:52 | 2012-12-19 | 08:53 | - | - | - | 0.33403 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0.38889 | 0 | 0 | 1900-01-02 09:38
46 |  | BINA(PG)-BINA(MPEB) I 400kV |  |  |  |  | - | - | - | - |  |  | 100
47 |  | BINA(PG)-BINA(MPEB) II 400kV |  |  |  |  | - | - | - | - |  |  | 100
48 | 912071 | GWALIOR-BINA I (400kV) 800kV | 2012-12-14 | 09:57 | 2012-12-14 | 17:34 | 0.31736 | - | - | - | OSPT | Line H/T to avail OCC approved S/D by Powergrid for attending various type of S/D nature defects. | 98.9763
|  | SUBTOTAL |  |  |  |  | 0.31736 | 0 | 0 | 0
49 | 912051 | SATNA-BINA(PG) IV 400kV | 2012-12-10 | 23:15 | 2012-12-11 | 09:10 | - | - | - | 0.41319 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912088 |  | 2012-12-18 | 00:10 | 2012-12-18 | 07:46 | - | - | - | 0.31667 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.31667
50 | 912044 | SATNA-BINA(PG) III 400kV | 2012-12-08 | 21:14 | 2012-12-08 | 21:57 | - | - | - | 0.029861 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912058 |  | 2012-12-12 | 03:10 | 2012-12-12 | 06:44 | - | - | - | 0.14861 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912082 |  | 2012-12-17 | 01:27 | 2012-12-17 | 07:44 | - | - | - | 0.26181 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.26181
51 | 912070 | BINA-SHUJALPUR I 400kV | 2012-12-14 | 03:31 | 2012-12-14 | 08:27 | - | - | - | 0.20556 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912099 |  | 2012-12-19 | 03:30 | 2012-12-19 | 08:33 | - | - | - | 0.21042 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912142 |  | 2012-12-27 | 03:24 | 2012-12-27 | 07:31 | - | - | - | 0.17153 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912160 |  | 2012-12-29 | 23:20 | 2012-12-30 | 07:10 | - | - | - | 0.32639 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.91389
52 | 912020 | BINA-SHUJALPUR II 400kV | 2012-12-05 | 00:05 | 2012-12-05 | 07:07 | - | - | - | 0.29306 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912028 |  | 2012-12-05 | 22:13 | 2012-12-06 | 08:28 | - | - | - | 0.42708 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912064 |  | 2012-12-13 | 01:37 | 2012-12-13 | 08:02 | - | - | - | 0.26736 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912153 |  | 2012-12-28 | 22:33 | 2012-12-29 | 07:03 | - | - | - | 0.35417 | LVRD | Line H/T for voltage regulation on WRLDC instruction. LR of same connected as BR at both ends.
| 912165 |  | 2012-12-30 | 23:40 | 2012-12-31 | 05:54 | - | - | - | 0.25972 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 14:26
53 |  | SHUJALPUR-NAGDA I 400kV |  |  |  |  | - | - | - | - |  |  | 100
54 |  | SHUJALPUR-NAGDA II 400kV |  |  |  |  | - | - | - | - |  |  | 100
55 | 912006 | NAGDA-DEHGAM II 400kV | 2012-12-02 | 02:10 | 2012-12-02 | 06:39 | - | - | - | 0.18681 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912083 |  | 2012-12-17 | 01:33 | 2012-12-17 | 06:42 | - | - | - | 0.21458 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912123 |  | 2012-12-23 | 03:19 | 2012-12-24 | 10:03 | - | - | - | 1899-12-31 06:44 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912149 |  | 2012-12-28 | 02:10 | 2012-12-28 | 07:10 | - | - | - | 0.20833 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 21:22
56 | 912002 | NAGDA-DEHGAM I 400KV | 2012-12-01 | 03:17 | 2012-12-01 | 07:34 | - | - | - | 0.17847 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912008 |  | 2012-12-02 | 06:06 | 2012-12-02 | 07:18 | - | - | 0.05 | - | GOVC | Line A/T due to receipt of D/T from Nagda MPPTCL end due to operation of O/V Stage - I at Nagda (MPPTCL).
| 912087 |  | 2012-12-17 | 23:53 | 2012-12-18 | 07:01 | - | - | - | 0.29722 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912094 |  | 2012-12-19 | 00:02 | 2012-12-19 | 08:36 | - | - | - | 0.35694 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912106 |  | 2012-12-20 | 03:11 | 2012-12-20 | 08:34 | - | - | - | 0.22431 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912143 |  | 2012-12-27 | 03:21 | 2012-12-27 | 09:05 | - | - | - | 0.23889 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912164 |  | 2012-12-30 | 23:33 | 2012-12-31 | 06:50 | - | - | - | 0.30347 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.05 | 1899-12-31 14:23
57 | 912079 | SEONI-KHANDWA I 400kV | 2012-12-16 | 02:25 | 2012-12-16 | 05:54 | - | - | - | 0.14514 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912084 |  | 2012-12-17 | 01:43 | 2012-12-17 | 05:31 | - | - | 0.0069444 | 0.15139 | GOVC | A/T on D/T received from Seoni due to operation of O/V Protection,'Line kept out for voltage regulation on WRLDC instruction.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.056944 | 1900-01-02 00:28
58 | 912050 | SEONI-KHANDWA II 400kV | 2012-12-10 | 21:02 | 2012-12-10 | 21:12 | - | - | 0.0069444 | - | GOVC | A/T on operation of O/V Protection at Khandwa during H/T of 400kV Khandwa - Rajgarh # 1 | 100
| 912073 |  | 2012-12-15 | 03:03 | 2012-12-15 | 06:29 | - | - | - | 0.14306 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912096 |  | 2012-12-19 | 02:58 | 2012-12-19 | 08:59 | - | - | - | 0.25069 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912124 |  | 2012-12-23 | 03:47 | 2012-12-23 | 06:33 | - | - | - | 0.11528 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912129 |  | 2012-12-23 | 22:49 | 2012-12-24 | 08:28 | - | - | - | 0.40208 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.0069444 | 0.91111
59 | 912010 | KHANDWA-RAJGARH II 400kV | 2012-12-02 | 22:33 | 2012-12-04 | 10:48 | - | - | - | 1899-12-31 12:15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912039 |  | 2012-12-07 | 23:02 | 2012-12-08 | 09:04 | - | - | - | 0.41806 | LVRD | Line H/T on voltage regulation as WRLDC instruction
| 912056 |  | 2012-12-11 | 21:07 | 2012-12-15 | 07:58 | - | - | - | 1900-01-02 10:51 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912078 |  | 2012-12-15 | 22:01 | 2012-12-16 | 08:52 | - | - | - | 0.45208 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912085 |  | 2012-12-17 | 22:58 | 2012-12-18 | 07:05 | - | - | - | 0.33819 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912102 |  | 2012-12-19 | 19:28 | 2012-12-20 | 08:14 | - | - | - | 0.53194 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912122 |  | 2012-12-22 | 22:50 | 2012-12-23 | 07:44 | - | - | - | 0.37083 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912133 |  | 2012-12-24 | 23:10 | 2012-12-25 | 08:38 | - | - | - | 0.39444 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912151 |  | 2012-12-28 | 21:07 | 2012-12-31 | 06:51 | - | - | - | 1900-01-01 09:44 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912172 |  | 2012-12-31 | 22:12 |  |  | - | - | - | 0.075 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-08 22:46
60 | 911058 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2012-11-17 | 18:41 | 2012-12-05 | 18:08 | - | 1900-01-03 18:08 | - | - | OMSU | Line A/T on SOTF, CS, Z-1, 3 Ph trip, F/L 74kM from Rajgarh (under MPPTCL jurisdiction). | 100
| 912024 |  | 2012-12-05 | 18:09 | 2012-12-05 | 18:09 | - | 0 | - | - | OMSU | Line A/R on Y ph to E/F.75 km from rajgarh
| 912026 |  | 2012-12-05 | 19:02 |  |  | - | - | - | 1900-01-25 04:58 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 1900-01-03 18:08 | 0 | 1900-02-08 06:31
61 | 912077 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2012-12-15 | 17:05 | 2012-12-15 | 17:19 | - | - | 0.0097222 | - | GOVC | Line A/T due to operation of O/V protection at SSP and receipt of DT at Rajgarh | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.0097222 | 0
62 | 911084 | RAJGARH-NAGDA I 400kV (LILO) | 2012-11-24 | 03:04 | 2012-12-05 | 17:08 | - | - | - | 1900-01-03 17:08 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912075 |  | 2012-12-15 | 05:32 | 2012-12-15 | 06:38 | - | 0.045833 | - | - | SBBU | Line A/T only at Nagda end due to operation of Bus bar protection at Nagda (MPPTCL).
| 912120 |  | 2012-12-22 | 16:33 |  |  | - | - | - | 1900-01-08 07:27 | OSPD | Line H/T to avail S/D by MPPTCL for checking of isolators at Nagda (MPPTCL).
|  | SUBTOTAL |  |  |  |  | 0 | 0.045833 | 0 | 1900-01-13 00:35
63 | 912025 | RAJGARH-NAGDA II 400kV (LILO) | 2012-12-05 | 18:15 | 2012-12-22 | 16:06 | - | - | - | 1900-01-15 21:51 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-15 21:51
64 | 911095 | KHANDWA-RAJGARH I 400kV | 2012-11-25 | 17:07 | 2012-12-01 | 07:49 | - | - | - | 0.32569 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912004 |  | 2012-12-01 | 22:02 | 2012-12-02 | 07:07 | - | - | - | 0.37847 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912018 |  | 2012-12-04 | 22:37 | 2012-12-05 | 08:35 | - | - | - | 0.41528 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912029 |  | 2012-12-05 | 22:16 | 2012-12-07 | 18:57 | - | - | - | 1899-12-31 20:41 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912049 |  | 2012-12-10 | 21:02 | 2012-12-11 | 15:41 | - | - | - | 0.77708 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912072 |  | 2012-12-14 | 23:07 | 2012-12-15 | 10:39 | - | - | - | 0.48056 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912081 |  | 2012-12-17 | 01:04 | 2012-12-17 | 06:51 | - | - | - | 0.24097 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912093 |  | 2012-12-18 | 23:51 | 2012-12-19 | 09:06 | - | - | - | 0.38542 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912109 |  | 2012-12-20 | 23:01 | 2012-12-22 | 07:38 | - | - | - | 1899-12-31 08:37 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912128 |  | 2012-12-23 | 22:05 | 2012-12-24 | 10:15 | - | - | - | 0.50694 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912138 |  | 2012-12-25 | 23:45 | 2012-12-26 | 08:29 | - | - | - | 0.36389 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912150 |  | 2012-12-28 | 03:11 | 2012-12-28 | 10:21 | - | - | - | 0.29861 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912167 |  | 2012-12-31 | 00:09 | 2012-12-31 | 11:09 | - | - | - | 0.45833 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912170 |  | 2012-12-31 | 21:29 |  |  | - | - | - | 0.10486 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-06 22:58
65 |  | VAPI-MAGARWADA I 220kV |  |  |  |  | - | - | - | - |  |  | 100
66 |  | VAPI-MAGARWADA II 220kV |  |  |  |  | - | - | - | - |  |  | 100
67 | 912125 | VAPI-KHARADPARA I 220kV | 2012-12-23 | 07:42 | 2012-12-23 | 19:53 | - | - | - | 0.50764 | LCSD | H/T to avail OCC Approved S/D to facilitate stringing work of new 400kV NAV-VAPI-Boisar Line. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.50764
68 | 912126 | VAPI-KHARADPARA II 220kV | 2012-12-23 | 07:43 | 2012-12-24 | 13:02 | - | - | - | 1899-12-31 05:19 | LCSD | H/T to avail OCC Approved S/D to facilitate stringing work of new 400kV NAV-VAPI-Boisar Line. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 05:19
69 | 912076 | GWALIOR-BINA II (400kV) 800kV | 2012-12-15 | 10:03 | 2012-12-15 | 16:59 | 0.28889 | - | - | - | OSPT | Line H/T to avail OCC approved S/D by Powergrid for attending various type of S/D nature defects. | 99.0681
|  | SUBTOTAL |  |  |  |  | 0.28889 | 0 | 0 | 0
70 | 912065 | SEONI-BINA I 765kV | 2012-12-13 | 01:45 | 2012-12-13 | 07:31 | - | - | - | 0.24028 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
| 912069 |  | 2012-12-13 | 22:02 | 2012-12-14 | 07:38 | - | - | - | 0.4 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912111 |  | 2012-12-21 | 01:53 | 2012-12-21 | 07:13 | - | - | - | 0.22222 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912116 |  | 2012-12-21 | 23:03 | 2012-12-22 | 07:36 | - | - | - | 0.35625 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 05:15
71 | 912059 | DAMOH-BHOPAL I 400KV | 2012-12-12 | 09:49 | 2012-12-12 | 10:29 | - | - | - | 0.027778 | LPRD | H/T on Power Regulation on WRLDC Instructions. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.027778
72 |  | DAMOH-BHOPAL II 400KV |  |  |  |  | - | - | - | - |  |  | 100
73 | 912137 | VAPI-KHADOLI I 220kV | 2012-12-25 | 11:45 | 2012-12-25 | 12:13 | - | 0.019444 | - | - | OMSU | Line A/T due to problem at khadoli end.DT received at vapi end | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0.019444 | 0 | 0
74 |  | VAPI-KHADOLI II 220kV |  |  |  |  | - | - | - | - |  |  | 100
75 |  | DAMOH-BIRSINGHPUR I 400kV |  |  |  |  | - | - | - | - |  |  | 100
76 | 912060 | DAMOH-BIRSINGHPUR II 400kV | 2012-12-12 | 10:09 | 2012-12-12 | 10:16 | 0.0048611 | - | - | - | OSFT | Line H/T to check Buchholz alarm in L/R at damoh end | 99.9843
|  | SUBTOTAL |  |  |  |  | 0.0048611 | 0 | 0 | 0
77 |  | DEHGAM PIRANA I 400kV |  |  |  |  | - | - | - | - |  |  | 100
78 |  | DEHGAM PIRANA II 400kV |  |  |  |  | - | - | - | - |  |  | 100
79 | 912066 | MUNDRA-BHACHAU I 400kV | 2012-12-13 | 04:42 | 2012-12-13 | 04:52 | 0 | 0.0069444 | - | - | LART | Line A/R from Bhachau end only on Y ph to E/F ,F/L:71.2 km from Bhachau and subsequently line tripped on receipt of DT from Mundra (CGPL) end. | 100
| 912117 |  | 2012-12-22 | 04:00 | 2012-12-22 | 08:03 | - | - | - | 0.16875 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912121 |  | 2012-12-22 | 17:18 | 2012-12-23 | 17:51 | - | - | - | 1899-12-31 00:33 | LVRD | Line H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0.0069444 | 0 | 1899-12-31 04:36
80 | 912089 | MUNDRA-BHACHAU II 400kV | 2012-12-18 | 15:09 | 2012-12-19 | 02:38 | - | - | - | 0.47847 | OSFD | Line H/T from Bachau due to fire in wave trap at Mundra end | 100
| 912144 |  | 2012-12-27 | 11:20 | 2012-12-27 | 17:55 | - | - | - | 0.27431 | OSFD | H/T to attend Hot Spot at CGPL end. S/D availed by CGPL.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.75278
81 | 912090 | BHACHAU-RANCHODPURA I 400kV | 2012-12-18 | 16:46 | 2012-12-19 | 02:25 | - | - | - | 0.40208 | LPRD | H/T on Power Regulation on WRLDC Instructions. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 10:18
82 | 912054 | BHACHAU-RANCHODPURA II 400kV | 2012-12-11 | 13:07 | 2012-12-11 | 13:45 | 0.026389 | - | - | - | LHWT | Line A/T on R-B ph to ph fault.F/L:182kM from Bhachau. During patrolling Jumper found opened at Loc no. 480 | 99.5856
| 912057 |  | 2012-12-11 | 22:40 | 2012-12-11 | 23:04 | 0.016667 | - | - | - | LHWT | Line A/T on R-B ph to ph fault.F/L:182kM from Bhachau. During patrolling Jumper found opened at Loc no. 480
| 912062 |  | 2012-12-12 | 15:23 | 2012-12-12 | 17:26 | 0.085417 | - | - | - | OMST | Line H/T to avail outage for jumper tightening work at loc.no. 480
|  | SUBTOTAL |  |  |  |  | 0.12847 | 0 | 0 | 0
83 |  | MUNDRA-LIMBDI I 400kV |  |  |  |  | - | - | - | - |  |  | 100
84 | 912158 | MUNDRA-LIMBDI II 400kV | 2012-12-29 | 11:24 | 2012-12-29 | 11:43 | - | 0.013194 | - | - | OMSU | A/T at Mundra end | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0.013194 | 0 | 0
85 | 911074 | SATNA-BINA(PG) I 765kV | 2012-11-22 | 15:29 | 2012-12-12 | 16:50 | - | - | - | 1900-01-10 16:50 | LVRD | Line H/T for voltage regulation on WRLDC instruction | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-10 16:50
86 | 912061 | SATNA-BINA(PG) II 765kV | 2012-12-12 | 12:25 |  |  | - | 1900-01-18 11:35 | - | - | OMSU | Line H/T for interchanging #1 &2 | 100
|  | SUBTOTAL |  |  |  |  | 0 | 1900-01-18 11:35 | 0 | 0
87 |  | BINA (PG) -INDORE (MPPTCL) I 765kV (400kV) |  |  |  |  | - | - | - | - |  |  | 100
88 | 912017 | GANDHAR-NAVSARI (PG GIS) II 400kV | 2012-12-04 | 14:50 | 2012-12-04 | 15:45 | - | 0.038194 | - | - | OMSU | Line A/T due to DT received at Navsari end during SCADA implementation by NTPC at Gandhar. | 100
| 912033 |  | 2012-12-06 | 10:35 | 2012-12-06 | 18:15 | - | - | - | 0.31944 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar.
| 912038 |  | 2012-12-07 | 11:08 | 2012-12-07 | 18:51 | - | - | - | 0.32153 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar.
89 |  | LILO of Mundra-Limbdi#1 at Jetpur (GETCO)
| 911047 | JETPUR (GETCO) - LIMDI (GETCO) 400kV | 2012-11-13 | 16:37 | 2012-12-12 | 13:25 | - | - | - | 1900-01-10 13:25 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912097 |  | 2012-12-19 | 03:17 | 2012-12-19 | 15:07 | - | - | - | 0.49306 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912104 |  | 2012-12-20 | 00:05 | 2012-12-21 | 09:54 | - | - | - | 1899-12-31 09:49 | LVRD | Line H/T for voltage regulation on WRLDC instruction
| 912114 |  | 2012-12-21 | 22:20 | 2012-12-31 | 22:34 | - | - | - | 1900-01-09 00:14 | LPRD | Line H/T for pwer regulation as per WRLDC instruction (Line Brought back as 400kV Mundra - Limdi # 1)
| 912101 | MUNDRA (CGPL) - JETPUR (GETCO) 400kV | 2012-12-19 | 15:37 | 2012-12-19 | 19:08 | - | - | - | 0.14653 | OSFD | H/T to avail S/D by Mundra to attend hot spot.
| 912157 | MUNDRA (CGPL) - JETPUR (GETCO) 400kV | 2012-12-29 | 09:23 | 2012-12-31 | 17:37 | - | - | - | 1900-01-01 08:14 | LCSD | H/T for removing LILO at Jetpur (Line Brought back as 400kV Mundra - Limdi # 1)
90 | 912016 | GANDHAR-NAVSARI (PG) I 400kV | 2012-12-04 | 10:18 | 2012-12-04 | 19:51 | - | - | - | 0.39792 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar. | 100
| 912022 |  | 2012-12-05 | 9:18 | 2012-12-05 | 18:43 | - | - | - | 0.39236 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.79028
91 |  | 400 kV Gwalior -Agra # 1 |  |  |  |  | - | - | - | - |  |  | 100
92 |  | 400 kV Gwalior -Agra # 2 |  |  |  |  | - | - | - | - |  |  | 100
[12 empty] | TRANSMISSION LINE AVAILABILITY | 99.8725
1 | 912042 | ICT1 JABALPUR 400/220kV | 2012-12-08 | 10:54 | 2012-12-08 | 10:57 | - | 0.0020833 | - | - | OMSU | H/T to change Tap position from 9b-11 | 100
| 912047 |  | 2012-12-10 | 12:27 | 2012-12-10 | 14:34 | - | - | - | 0.088194 | LPRD | H/T on Power Regulation on WRLDC Instructions from 220kV side only.
| 912132 |  | 2012-12-24 | 10:32 | 2012-12-24 | 12:20 | - | - | - | 0.075 | SPRD | H/T on Power Regulation on WRLDC Instructions.
|  | SUBTOTAL |  |  |  |  | 0 | 0.0020833 | 0 | 0.16319
2 | 912043 | ICT2 JABALPUR 400/220kV | 2012-12-08 | 10:57 | 2012-12-08 | 12:40 | - | 0.071528 | - | - | OMSU | H/T to change Tap position from 9b-12 | 100
| 912053 |  | 2012-12-11 | 10:31 | 2012-12-11 | 12:10 | - | - | - | 0.06875 | LPRD | ICT H/T from 220kV side on P/R
|  | SUBTOTAL |  |  |  |  | 0 | 0.071528 | 0 | 0.06875
3 |  | ICT1 DEHGAM 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
4 |  | ICT2 DEHGAM 400/220kV | [10 empty] | 100
5 | 912107 | ICT1 SATNA 400/220KV | 2012-12-20 | 10:20 | 2012-12-20 | 13:17 | - | - | - | 0.12292 | SPRD | Line H/T for voltage regulation on WRLDC instruction | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.12292
6 | 912108 | ICT2 SATNA 400/220KV | 2012-12-20 | 10:20 | 2012-12-20 | 13:36 | - | - | - | 0.13611 | SPRD | Line H/T for voltage regulation on WRLDC instruction | 99.384
| 912131 |  | 2012-12-24 | 06:35 | 2012-12-24 | 11:10 | 0.19097 | - | - | - | SEFT | A/T on operation Diff protection due B-ph isolator support insulator of ICT incomer isolator.
|  | SUBTOTAL |  |  |  |  | 0.19097 | 0 | 0 | 0.13611
7 |  | ICT1 KHANDWA 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
8 |  | ICT2 KHANDWA 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
9 |  | ICT1 VAPI 400/220KV |  |  |  |  | - | - | - | - |  |  | 100
10 |  | ICT2 VAPI 400/220KV |  |  |  |  | - | - | - | - |  |  | 100
11 |  | ICT1 GWALIOR 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
12 |  | ICT1 RAJGARH 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
13 |  | ICT2 GWALIOR 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
14 |  | ICT ITARSI 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
15 |  | ICT1 DAMOH 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
16 |  | ICT2 DAMOH 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
17 |  | ICT2 RAJGARH 400/220kV |  |  |  |  | - | - | - | - |  |  | 100
18 |  | ICT1 BINA 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
19 |  | ICT1 PIRANA 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
20 |  | ICT2 PIRANA 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
21 |  | ICT3 GWALIOR 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
22 |  | ICT1 SHUJALPUR 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
23 |  | ICT1 BHACHAU 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
24 | 912067 | ICT2 BHACHAU 400/220/33kV | 2012-12-13 | 11:23 | 2012-12-13 | 17:25 | 0.25139 | - | - | - | OMST | OCC approved S/D availed by Powergrid replacement of faulty (tan-delta violation) 220kV Y- ph bushing of ICT#2. | 99.1891
|  | SUBTOTAL |  |  |  |  | 0.25139 | 0 | 0 | 0
25 |  | ICT2 SHUJALPUR 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
26 |  | ICT1 SATNA 765/400KV |  |  |  |  | - | - | - | - |  |  | 100
27 |  | ICT2 NAVSARI 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
28 |  | ICT1 NAVSARI 400/220/33kV |  |  |  |  | - | - | - | - |  |  | 100
29 | 912145 | ICT2 SATNA 765/400kV | 2012-12-27 | 11:35 | 2012-12-27 | 16:31 | - | - | - | 0.20556 | SCSD | H/T for Jumpering of Earth Wire. | 100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.20556
30 |  | ICT1 BINA 765/400KV |  |  |  |  | - | - | - | - |  |  | 100
[12 empty] | ICT AVAILABILITY | 99.9609
1 |  | BUS REACTOR DEHGAM I 400kV |  |  |  |  | - | - | - | - |  |  | 100
2 |  | BUS REACTOR JABALPUR I 33kV |  |  |  |  | - | - | - | - |  |  | 100
3 |  | BUS REACTOR JABALPUR II 33kV |  |  |  |  | - | - | - | - |  |  | 100
4 |  | BUS REACTOR ITARSI I 400kV |  |  |  |  | - | - | - | - |  |  | 100
5 |  | BUS REACTOR ITARSI II 400kV |  |  |  |  | - | - | - | - |  |  | 100
6 |  | BUS REACTOR ITARSI III 400kV |  |  |  |  | - | - | - | - |  |  | 100
7 |  | BUS REACTOR JABALPUR III 400kV |  |  |  |  | - | - | - | - |  |  | 100
8 |  | BUS REACTOR DHULE 400kV |  |  |  |  | - | - | - | - |  |  | 100
9 |  | BUS REACTOR SATNA 400kV |  |  |  |  | - | - | - | - |  |  | 100
10 |  | Bus Reactor # 1 / Bina |  |  |  |  | - | - | - | - |  |  | 100
11 |  | Bus Reactor / Damoh |  |  |  |  | - | - | - | - |  |  | 100
12 |  | Bus Reactor / Gwalior |  |  |  |  | - | - | - | - |  |  | 100
13 |  | Bus Reactor / Khandwa |  |  |  |  | - | - | - | - |  |  | 100
14 |  | Bus Reactor / Dehgam |  |  |  |  | - | - | - | - |  |  | 100
15 |  | Bus Reactor / Bhachau |  |  |  |  | - | - | - | - |  |  | 100
16 |  | Bus Reactor / Shujalpur |  |  |  |  | - | - | - | - |  |  | 100
17 |  | Bus Reactor/ Rajgarh |  |  |  |  | - | - | - | - |  |  | 100
18 | 911001 | BUS REACTOR SATNA 765kV | 2012-11-01 | 00:00 | 2012-12-27 | 18:15 | - | - | - | 1900-01-25 18:15 | SVRD | Bus Reactor kept out for voltage regulation | 100
| 912147 |  | 2012-12-27 | 18:34 | 2012-12-27 | 23:08 | - | - | - | 0.19028 | SVRD | H/T for voltage regulation on WRLDC instruction
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-25 22:49
19 |  | Bus Reactor / Navsari |  |  |  |  | - | - | - | - |  |  | 100
20 |  | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | - | - | - | - |  |  | 100
21 |  | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | - | - | - | - |  |  | 100
[12 empty] | BUS REACTOR AVAILABILITY | 100
[12 empty] | SYSTEM AVAILABILITY | 99.9218
Formulas:
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT CODE],1)="D"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE DEEMED AVAILABLE = SUM([OUTAGE DEEMED AVAILABLE, row above])
ATTRIBUTED TO PGCIL = SUM([ATTRIBUTED TO PGCIL, row above])
ATTRIBUTED TO PGCIL = IF((RIGHT([CAT CODE],1)="T"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE HOURS ATTRIBUTED TO = SUM([OUTAGE HOURS ATTRIBUTED TO, row above])
OUTAGE HOURS ATTRIBUTED TO = IF((RIGHT([CAT CODE],1)="U"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")

## Tripping AC SYSTEM Revised
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR DECEMBER - 2012
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length |  |  |  |  | Element_wise_%availability
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 100
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 100
3 | 400kV Itarsi-Indore # 2 |  |  | 0 | 16 | 0 | 0.26667 | 743.7333 | 214 | 2 | 0 | 428 | 318317.8667 | 100
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 100
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 100
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 100
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 100
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 100
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 100
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 100
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 100
12 | 400 KV Jabalpur-Sasan |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 376 | 2 | 0 | 752 | 559049.3333 | 100
13 | 400kV Sasan-Vindhyachal |  |  | 1 | 15 | 0 | 1.25 | 742.75 | 21 | 2 | 0 | 42 | 31195.5 | 100
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 100
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 100
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 100
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 100
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 100
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 100
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 100
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 100
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 2 | 16 | 0 | 2.2667 | 741.7333 | 110 | 2 | 0 | 220 | 163181.3333 | 100
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 100
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 100
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 100
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 100
27 | 220kV Kawas-Navsari (GIS)#2 | 0 | 27 |  |  | 0.45 | 0 | 744 | 58.149 | 1 | 26.167 | 58.149 | 43262.856 | 99.9395
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 0 | 17 | 11 | 9 | 0.28333 | 11.15 | 732.85 | 31.334 | 1 | 8.878 | 31.334 | 22963.1219 | 99.9613
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 31.334 | 1 | 11.4891 | 31.334 | 23312.496 | 99.9507
30 | 220kV Kawas-Vav#1 |  |  | 0 | 26 | 0 | 0.43333 | 743.5667 | 37 | 1 | 0 | 37 | 27511.9667 | 100
31 | 220kV Kawas-Vav#2 | 0 | 10 | 5 | 34 | 0.16667 | 5.5667 | 738.4333 | 37 | 1 | 6.1667 | 37 | 27322.0333 | 99.9774
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 100
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 100
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 100
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 100
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 100
37 | 220 KV Kakrapar - Vav # 2 |  |  | 2 | 34 | 0 | 2.5667 | 741.4333 | 43 | 1 | 0 | 43 | 31881.6333 | 100
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 100
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 100
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 100
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 100
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 100
43 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 100
44 | 400kV Satna - Bina # 1 | 21 | 3 |  |  | 21.05 | 0 | 744 | 276 | 2 | 11619.6 | 552 | 410688 | 97.1707
45 | 400kV Satna - Bina # 2 | 9 | 20 |  |  | 9.3333 | 0 | 744 | 276 | 2 | 5152 | 552 | 410688 | 98.7455
46 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 100
47 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 100
48 | 765 kV Gwalior-Bina # 1 * | 7 | 37 |  |  | 7.6167 | 0 | 744 | 234.931 | 4 | 7157.5645 | 939.724 | 699154.656 | 98.9763
49 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 100
50 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 100
51 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 100
52 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 100
53 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 100
54 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 100
55 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 100
56 | 400KV Nagda - Dehgam # 1 |  |  | 1 | 12 | 0 | 1.2 | 742.8 | 331.442 | 2 | 0 | 662.884 | 492390.2352 | 100
57 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 100
58 | 400KV Seoni - Khandwa # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 100
59 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 100
60 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 114 | 8 | 0 | 114.1333 | 629.8667 | 4.01 | 2 | 0 | 8.02 | 5051.5307 | 100
61 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 4.01 | 2 | 0 | 8.02 | 5965.0087 | 100
62 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  | 1 | 6 | 0 | 1.1 | 742.9 | 4.12 | 2 | 0 | 8.24 | 6121.496 | 100
63 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 100
64 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 100
65 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 100
66 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 100
67 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 100
68 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 100
69 | 765 kV Gwalior-Bina # 2 * | 6 | 56 |  |  | 6.9333 | 0 | 744 | 233.652 | 4 | 6479.9488 | 934.608 | 695348.352 | 99.0681
70 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 100
71 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 100
72 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 100
73 | 220 KV Vapi - Khadoli # 1 |  |  | 0 | 28 | 0 | 0.46667 | 743.5333 | 28.549 | 1 | 0 | 28.549 | 21227.1331 | 100
74 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 100
75 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 100
76 | 400kV Damoh-Birsinghpur#2 | 0 | 7 |  |  | 0.11667 | 0 | 744 | 228.474 | 2 | 53.3106 | 456.948 | 339969.312 | 99.9843
77 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 100
78 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 100
79 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 100
80 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 100
81 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 100
82 | 400kV Bhachau - Ranchodpura # 2 | 3 | 5 |  |  | 3.0833 | 0 | 744 | 282.856 | 3 | 2616.418 | 848.568 | 631334.592 | 99.5856
83 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 100
84 | 400kV Mundra - Limbdi # 2 |  |  | 0 | 19 | 0 | 0.31667 | 743.6833 | 314.053 | 3 | 0 | 942.159 | 700667.9457 | 100
85 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 100
86 | 765kV Satna - Bina # 2 |  |  | 467 | 35 | 0 | 467.5833 | 276.4167 | 275.635 | 4 | 0 | 1102.54 | 304760.4317 | 100
87 | 765kV Bina - Indore * |  |  |  |  | 0 | 0 | 744 | 311.17 | 4 | 0 | 1244.68 | 926041.92 | 100
88 | 400kV Gandhar - Navsari # 2 |  |  | 0 | 55 | 0 | 0.91667 | 743.0833 | 102.15 | 2 | 0 | 204.3 | 151811.925 | 100
89 | LILO of Mundra-Limbdi#1 at Jetpur (GETCO) |  |  |  |  | 0 | 0 | 744 | 313 | 3 | 0 | 939 | 698616 | 100
90 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.15 | 2 | 0 | 204.3 | 151999.2 | 100
| Total Sr.No. 1 to 90 | 46 | 204 | 604 | 382 | 49.4 |  |  | 15175.643 |  | 33131.5427 |  | 25989575.3626
* | Lines charged with 400kV level
|  |  | 49.4 |  | 610.3667
[10 empty] | NAFM | 0.0012748
| Availability of 90 ( Sl no 1 to 90) transmission lines during DECEMBER -2012 = | [8 empty] | TAFM | 99.8725
1 | 400 kV Gwalior -Agra # 1 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 129.435 | 4 | 0 | 517.74 | 385198.56 | 100
1 | 400 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 100
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  |  | Element_wise_%availability
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  | 0 | 3 | 0 | 0.05 | 743.95 | 315 | 2.5 | 0 | 787.5 | 585860.625 | 100
2 | 400/220kV ICT # 2 /Jabalpur. |  |  | 1 | 43 | 0 | 1.7167 | 742.2833 | 315 | 2.5 | 0 | 787.5 | 584548.125 | 100
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 0.83333
6 | 400/220kV ICT # 2 / Satna | 4 | 35 |  |  | 4.5833 | 0 | 744 | 315 | 2.5 | 3609.375 | 787.5 | 585900 | 99.384
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
10 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
14 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
20 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
21 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
22 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
23 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
24 | 400/220 KV ICT # 2 / Bhachau | 6 | 2 |  |  | 6.0333 | 0 | 744 | 315 | 2.5 | 4751.25 | 787.5 | 585900 | 99.1891
25 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
26 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100
27 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
28 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
29 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100
30 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100
| Total Sr.No. 1 to 30 | 10 | 37 | 1 | 46 | 10.6167 |  |  | 11505 | 75 | 8360.625 |  | 21397908.75
|  | 10.6167 |  | 1.7667 | [5 empty] | NAFM | 0.00039072
[10 empty] | TAFM | 99.9609
Availability of 30 ( Sl no 1 to 30) ICTs in DECEMBER -2012 =
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR |  |  |  | Element_wise_%availability
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 100
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 100
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 100
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100
15 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
16 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
17 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100
18 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
19 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
20 | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
21 | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
| Total of sl no 1 to 21 | 0 | 0 | 0 | 0 |  |  |  | 1916 | 84 | 0 |  | 5702016
0
[8 empty] | NAFM | 0
| Availability of 21( Sl no 1 to 21) Bus Reactors in DECEMBER -2012 = | [6 empty] | TAFM | 100
[11 empty] | 41492.1677 |  | 53089500.1125
[8 empty] | NAFM = | 0.00078155
| % System Availability for DECEMBER 2012 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.9218
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B30: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B123: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B124: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## IR lines - As per new tariff (hidden)
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR DECEMBER 2012
A | 400 kV Gwalior -Agra # 1
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
|  | Powergrid | Powergrid |  |  | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400 kV Gwalior -Agra # 1 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 129.435 | 4 | 0 | 517.74 | 385198.56 | 100
| Total | 0 | 0 | 0 | 0 | 0 |  |  | 129.435 |  | 0 |  | 385198.56
[10 empty] | NAFM | 0
| Availability of transmission lines during DECEMBER -2012 = | [8 empty] | TAFM | 100
12.5667
B | 400 kV Gwalior - Agra Ckt.2, Zerda-Kankroli, Zerda -Bhinmal, Bhinmal - Kankroli
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
|  | Powergrid | Powergrid |  |  | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 100
2 | 400 kV Zerda -Kankroli | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 233.707 | 2 | 0 | 467.414 | 347756.016
3 | 400 kV Zerda - Bhinmal (excl. of LILO portion) | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 146.2 | 2 | 0 | 292.4 | 217545.6
4 | 400 kV Bhinmal - Kankroli ( excl. LILO portion) | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 87.507 | 2 | 0 | 175.014 | 130210.416
| Total Sr.No. 1 to 4 | 0 | 0 | 0 | 0 | 0 |  |  | 595.348 |  | 0 |  | 1076243.616
[10 empty] | NAFM | 0
| Availability of transmission lines during DECEMBER 2012 = | [8 empty] | TAFM | 100
720

## CC Format_Dec'12 (hidden)
TRIPPING DETAILS OF WR-II FOR THE MONTH OF DEC' 2012
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | CAT CODE | Details | WRLDC CODE FOR
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING
765 kV TRANSMISSION LINES
80 | 912071 | GWALIOR-BINA I (400kV) 800kV | 2012-12-14 | 09:57 | 2012-12-14 | 17:34 | 0.31736 | - | - | - | OSPT | Line H/T to avail OCC approved S/D by Powergrid for attending various type of S/D nature defects. | LD 12/1240 & 12/100 | LD 12/1282
|  | SUBTOTAL |  |  |  |  | 0.31736 | 0 | 0 | 0
86 | 912076 | GWALIOR-BINA II (400kV) 800kV | 2012-12-15 | 10:03 | 2012-12-15 | 16:59 | 0.28889 | - | - | - | OSPT | Line H/T to avail OCC approved S/D by Powergrid for attending various type of S/D nature defects. | LD 12/1345 | LD 12/1359
|  | SUBTOTAL |  |  |  |  | 0.28889 | 0 | 0 | 0
5 | 911074 | SATNA-BINA(PG) I 765kV | 2012-11-22 | 15:29 | 2012-12-12 | 16:50 | - | - | - | 1900-01-10 16:50 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 11/1902 | LD12/1033
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-10 16:50
70 | 912061 | SATNA-BINA(PG) II 765kV | 2012-12-12 | 12:25 |  |  | - | 1900-01-18 11:35 | - | - | OMSU | Line H/T for interchanging #1 &2 | LD12/1039
|  | SUBTOTAL |  |  |  |  | 0 | 1900-01-18 11:35 | 0 | 0
74 | 912065 | SEONI-BINA I 765kV | 2012-12-13 | 01:45 | 2012-12-13 | 07:31 | - | - | - | 0.24028 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1098 | LD12/1105
78 | 912069 | SEONI-BINA I 765kV | 2012-12-13 | 22:02 | 2012-12-14 | 07:38 | - | - | - | 0.4 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1197 12/97 NLDC | LD 12/99 LD 12/1223
121 | 912111 | SEONI-BINA I 765kV | 2012-12-21 | 01:53 | 2012-12-21 | 07:13 | - | - | - | 0.22222 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1951 | LD 12/1959
126 | 912116 | SEONI-BINA I 765kV | 2012-12-21 | 23:03 | 2012-12-22 | 07:36 | - | - | - | 0.35625 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2059 | LD 12/2072 LD 12/150
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 05:15
400 kV TRANSMISSION LINES
100 | 912090 | BHACHAU-RANCHODPURA I 400kV | 2012-12-18 | 16:46 | 2012-12-19 | 02:25 | - | - | - | 0.40208 | LPRD | H/T on Power Regulation on WRLDC Instructions. | LD12/1619 | LD12/1667
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.40208
63 | 912054 | BHACHAU-RANCHODPURA II 400kV | 2012-12-11 | 13:07 | 2012-12-11 | 13:45 | 0.026389 | - | - | - | LHWT | Line A/T on R-B ph to ph fault.F/L:182kM from Bhachau. During patrolling Jumper found opened at Loc no. 480 |  | LD12/943 | No 63 and 66 are same .Not clearly mentioned also in no 71 outage was availed for jumper tightening
66 | 912057 | BHACHAU-RANCHODPURA II 400kV | 2012-12-11 | 22:40 | 2012-12-11 | 23:04 | 0.016667 | - | - | - | LHWT | Line A/T on R-B ph to ph fault.F/L:182kM from Bhachau. During patrolling Jumper found opened at Loc no. 480 |  | LD12/995
71 | 912062 | BHACHAU-RANCHODPURA II 400kV | 2012-12-12 | 15:23 | 2012-12-12 | 17:26 | 0.085417 | - | - | - | OMST | Line H/T to avail outage for jumper tightening work at loc.no. 480 | LD12/1051 | LD12/1062
|  | SUBTOTAL |  |  |  |  | 0.12847 | 0 | 0 | 0
79 | 912070 | BINA-SHUJALPUR I 400kV | 2012-12-14 | 03:31 | 2012-12-14 | 08:27 | - | - | - | 0.20556 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1211 | LD 12/1229
109 | 912099 | BINA-SHUJALPUR I 400kV | 2012-12-19 | 03:30 | 2012-12-19 | 08:33 | - | - | - | 0.21042 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1672 | LD 12/1680
152 | 912142 | BINA-SHUJALPUR I 400kV | 2012-12-27 | 03:24 | 2012-12-27 | 07:31 | - | - | - | 0.17153 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2492 | LD 12/2495
169 | 912160 | BINA-SHUJALPUR I 400kV | 2012-12-29 | 23:20 | 2012-12-30 | 07:10 | - | - | - | 0.32639 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2761 | LD 12/2778
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.91389
29 | 912020 | BINA-SHUJALPUR II 400kV | 2012-12-05 | 00:05 | 2012-12-05 | 07:07 | - | - | - | 0.29306 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/380 | LD 12/387
37 | 912028 | BINA-SHUJALPUR II 400kV | 2012-12-05 | 22:13 | 2012-12-06 | 08:28 | - | - | - | 0.42708 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/462 | LD12/487
73 | 912064 | BINA-SHUJALPUR II 400kV | 2012-12-13 | 01:37 | 2012-12-13 | 08:02 | - | - | - | 0.26736 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1097 | LD12/1109
162 | 912153 | BINA-SHUJALPUR II 400kV | 2012-12-28 | 22:33 | 2012-12-29 | 07:03 | - | - | - | 0.35417 | LVRD | Line H/T for voltage regulation on WRLDC instruction. LR of same connected as BR at both ends. | LD 12/2660 | LD 12/2687
174 | 912165 | BINA-SHUJALPUR II 400kV | 2012-12-30 | 23:40 | 2012-12-31 | 05:54 | - | - | - | 0.25972 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2837 | LD 12/2844
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 14:26
68 | 912059 | DAMOH-BHOPAL I 400KV | 2012-12-12 | 09:49 | 2012-12-12 | 10:29 | - | - | - | 0.027778 | LPRD | H/T on Power Regulation on WRLDC Instructions. | LD12/1023 | LD12/1032
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.027778
69 | 912060 | DAMOH-BIRSINGHPUR II 400kV | 2012-12-12 | 10:09 | 2012-12-12 | 10:16 | 0.0048611 | - | - | - | OSFT | Line H/T to check Buchholz alarm in L/R at damoh end | LD12/1021 | LD12/1024
|  | SUBTOTAL |  |  |  |  | 0.0048611 | 0 | 0 | 0
20 | 912011 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | 2012-12-03 | 09:43 | 2012-12-03 | 20:06 | - | - | - | 0.43264 | OSPD | H/T to avail S/D by GTEC for replacement of B-ph LA.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.43264
25 | 912016 | GANDHAR-NAVSARI (PG) I 400kV | 2012-12-04 | 10:18 | 2012-12-04 | 19:51 | - | - | - | 0.39792 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar. | LD12/314 | LD12/363
31 | 912022 | GANDHAR-NAVSARI (PG) I 400kV | 2012-12-05 | 9:18 | 2012-12-05 | 18:43 | - | - | - | 0.39236 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar. | LD12/399 | LD12/442
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.79028
26 | 912017 | GANDHAR-NAVSARI (PG GIS) II 400kV | 2012-12-04 | 14:50 | 2012-12-04 | 15:45 | - | 0.038194 | - | - | OMSU | Line A/T due to DT received at Navsari end during SCADA implementation by NTPC at Gandhar. |  | LD12/337
42 | 912033 | GANDHAR-NAVSARI (PG GIS) II 400kV | 2012-12-06 | 10:35 | 2012-12-06 | 18:15 | - | - | - | 0.31944 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar. | LD 12//501 | LD 12/531
47 | 912038 | GANDHAR-NAVSARI (PG GIS) II 400kV | 2012-12-07 | 11:08 | 2012-12-07 | 18:51 | - | - | - | 0.32153 | OSPD | Line H/T to avail S/D for SCADA implementation work by NTPC Gandhar. | LD 12/584 | LD 12/609
|  | SUBTOTAL |  |  |  |  | 0 | 0.038194 | 0 | 0.64097
14 | 912005 | INDORE-ASOJ I 400kV | 2012-12-02 | 00:05 | 2012-12-02 | 07:15 | - | - | - | 0.29861 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/92
96 | 912086 | INDORE-ASOJ I 400kV | 2012-12-17 | 23:05 | 2012-12-18 | 07:45 | - | - | - | 0.36111 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1544 | LD 12/1561
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.65972
45 | 912036 | ITARSI-INDORE II 400kV | 2012-12-07 | 06:11 | 2012-12-07 | 06:11 | 0 | - | - | - | LART | A/R Successfully from Itarsi end but A/T at Indore end on B-ph to E/F, F/L - 182.7kM from Itarsi
46 | 912037 | ITARSI-INDORE II 400kV | 2012-12-08 | 06:11 | 2012-12-08 | 06:27 | - | 0.011111 | - | - | OMSU | A/R Successfully from Itarsi end but A/T at Indore end on B-ph to E/F, F/L - 182.7kM from Itarsi |  | LD 12/568
|  | SUBTOTAL |  |  |  |  | 0 | 0.011111 | 0 | 0
9 | 911112 | ITARSI-KHANDWA I 400kV | 2012-11-30 | 23:45 | 2012-12-01 | 07:39 | - | - | - | 0.31875 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 11/2741 | LD 12/12
28 | 912019 | ITARSI-KHANDWA I 400kV | 2012-12-04 | 23:04 | 2012-12-05 | 07:17 | - | - | - | 0.34236 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/375 | LD 12/388
49 | 912040 | ITARSI-KHANDWA I 400kV | 2012-12-07 | 23:08 | 2012-12-08 | 06:02 | - | - | - | 0.2875 | LVRD | Line H/T on voltage regulation as WRLDC instruction | LD 12/622 | LD 12/629
77 | 912068 | ITARSI-KHANDWA I 400kV | 2012-12-13 | 21:32 | 2012-12-14 | 07:04 | - | - | - | 0.39722 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1195 | LD 12/1224
120 | 912110 | ITARSI-KHANDWA I 400kV | 2012-12-21 | 01:49 | 2012-12-21 | 06:50 | - | - | - | 0.20903 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1950 | LD 12/1960
144 | 912134 | ITARSI-KHANDWA I 400kV | 2012-12-25 | 02:46 | 2012-12-25 | 08:32 | - | - | - | 0.24028 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2328 | LD12/2336
157 | 912148 | ITARSI-KHANDWA I 400kV | 2012-12-27 | 22:37 | 2012-12-28 | 16:49 | - | - | - | 0.75833 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2574 | LD 12/2638
168 | 912159 | ITARSI-KHANDWA I 400kV | 2012-12-29 | 21:26 | 2012-12-30 | 06:56 | - | - | - | 0.39583 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2749 | LD 12/2777
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 22:47
22 | 912013 | ITARSI-KHANDWA II 400kV | 2012-12-03 | 23:53 | 2012-12-04 | 09:14 | - | - | - | 0.38958 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/284 | LD12/307
36 | 912027 | ITARSI-KHANDWA II 400kV | 2012-12-05 | 22:11 | 2012-12-06 | 07:19 | - | - | - | 0.38056 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/461 | LD12/482
43 | 912034 | ITARSI-KHANDWA II 400kV | 2012-12-06 | 22:54 | 2012-12-07 | 06:26 | - | - | - | 0.31389 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/551 | ld 12/564
72 | 912063 | ITARSI-KHANDWA II 400kV | 2012-12-12 | 23:35 | 2012-12-13 | 07:25 | - | - | - | 0.32639 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1090 | LD12/1106
125 | 912115 | ITARSI-KHANDWA II 400kV | 2012-12-21 | 23:02 | 2012-12-22 | 07:13 | - | - | - | 0.34097 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2060 | LD 12/2075
161 | 912152 | ITARSI-KHANDWA II 400kV | 2012-12-28 | 22:27 | 2012-12-29 | 06:56 | - | - | - | 0.35347 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2659 | LD 12/2686
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 02:31
108 | 912098 | JABALPUR-ITARSI I 400kV | 2012-12-19 | 03:18 | 2012-12-19 | 06:31 | - | - | - | 0.13403 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1671 | LD12/1676
115 | 912105 | JABALPUR-ITARSI I 400kV | 2012-12-20 | 03:09 | 2012-12-20 | 08:03 | - | - | - | 0.20417 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1808 | LD 12/1823
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.33819
2 | 911047 | JETPUR (GETCO) - LIMDI (GETCO) 400kV | 2012-11-13 | 16:37 | 2012-12-12 | 13:25 | - | - | - | 1900-01-10 13:25 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 11/1168 | LD12/1044
107 | 912097 | JETPUR (GETCO) - LIMDI (GETCO) 400kV | 2012-12-19 | 03:17 | 2012-12-19 | 15:07 | - | - | - | 0.49306 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1670
114 | 912104 | JETPUR (GETCO) - LIMDI (GETCO) 400kV | 2012-12-20 | 00:05 | 2012-12-21 | 09:54 | - | - | - | 1899-12-31 09:49 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1800
124 | 912114 | JETPUR (GETCO) - LIMDI (GETCO) 400kV | 2012-12-21 | 22:20 | 2012-12-31 | 22:34 | - | - | - | 1900-01-09 00:14 | LPRD | Line H/T for pwer regulation as per WRLDC instruction (Line Brought back as 400kV Mundra - Limdi # 1) | LD 12/2055 | LD 12/2899
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-22 11:18
7 | 911095 | KHANDWA-RAJGARH I 400kV | 2012-11-25 | 17:07 | 2012-12-01 | 07:49 | - | - | - | 0.32569 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 11/2205 | LD 12/13
13 | 912004 | KHANDWA-RAJGARH I 400kV | 2012-12-01 | 22:02 | 2012-12-02 | 07:07 | - | - | - | 0.37847 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/84 | LD 12/112
27 | 912018 | KHANDWA-RAJGARH I 400kV | 2012-12-04 | 22:37 | 2012-12-05 | 08:35 | - | - | - | 0.41528 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/374 | LD 12/394
38 | 912029 | KHANDWA-RAJGARH I 400kV | 2012-12-05 | 22:16 | 2012-12-07 | 18:57 | - | - | - | 1899-12-31 20:41 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/460 | LD 12/611
58 | 912049 | KHANDWA-RAJGARH I 400kV | 2012-12-10 | 21:02 | 2012-12-11 | 15:41 | - | - | - | 0.77708 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/881 | LD12/952
81 | 912072 | KHANDWA-RAJGARH I 400kV | 2012-12-14 | 23:07 | 2012-12-15 | 10:39 | - | - | - | 0.48056 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1306 | LD 12/1346
91 | 912081 | KHANDWA-RAJGARH I 400kV | 2012-12-17 | 01:04 | 2012-12-17 | 06:51 | - | - | - | 0.24097 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1458 | LD 12/1473
103 | 912093 | KHANDWA-RAJGARH I 400kV | 2012-12-18 | 23:51 | 2012-12-19 | 09:06 | - | - | - | 0.38542 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1656 | LD 121686
119 | 912109 | KHANDWA-RAJGARH I 400kV | 2012-12-20 | 23:01 | 2012-12-22 | 07:38 | - | - | - | 1899-12-31 08:37 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1943 | LD 12/2078
138 | 912128 | KHANDWA-RAJGARH I 400kV | 2012-12-23 | 22:05 | 2012-12-24 | 10:15 | - | - | - | 0.50694 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2208
148 | 912138 | KHANDWA-RAJGARH I 400kV | 2012-12-25 | 23:45 | 2012-12-26 | 08:29 | - | - | - | 0.36389 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2396 | LD 12/2411
159 | 912150 | KHANDWA-RAJGARH I 400kV | 2012-12-28 | 03:11 | 2012-12-28 | 10:21 | - | - | - | 0.29861 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2584 | LD 12/2609
176 | 912167 | KHANDWA-RAJGARH I 400kV | 2012-12-31 | 00:09 | 2012-12-31 | 11:09 | - | - | - | 0.45833 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2839 | LD 12/2866
180 | 912170 | KHANDWA-RAJGARH I 400kV | 2012-12-31 | 21:29 |  |  | - | - | - | 0.10486 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2909
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-06 22:58
19 | 912010 | KHANDWA-RAJGARH II 400kV | 2012-12-02 | 22:33 | 2012-12-04 | 10:48 | - | - | - | 1899-12-31 12:15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/151 | LD 12/318
48 | 912039 | KHANDWA-RAJGARH II 400kV | 2012-12-07 | 23:02 | 2012-12-08 | 09:04 | - | - | - | 0.41806 | LVRD | Line H/T on voltage regulation as WRLDC instruction | LD 12/618 | LD 12/642
65 | 912056 | KHANDWA-RAJGARH II 400kV | 2012-12-11 | 21:07 | 2012-12-15 | 07:58 | - | - | - | 1900-01-02 10:51 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/991 | LD 12/1330
88 | 912078 | KHANDWA-RAJGARH II 400kV | 2012-12-15 | 22:01 | 2012-12-16 | 08:52 | - | - | - | 0.45208 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1389 | LD 12/1418
95 | 912085 | KHANDWA-RAJGARH II 400kV | 2012-12-17 | 22:58 | 2012-12-18 | 07:05 | - | - | - | 0.33819 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1543 | LD 12/1555
112 | 912102 | KHANDWA-RAJGARH II 400kV | 2012-12-19 | 19:28 | 2012-12-20 | 08:14 | - | - | - | 0.53194 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1770 | LD 12/1825
133 | 912122 | KHANDWA-RAJGARH II 400kV | 2012-12-22 | 22:50 | 2012-12-23 | 07:44 | - | - | - | 0.37083 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2151 | LD 12/2172
143 | 912133 | KHANDWA-RAJGARH II 400kV | 2012-12-24 | 23:10 | 2012-12-25 | 08:38 | - | - | - | 0.39444 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2320 | LD12/2335
160 | 912151 | KHANDWA-RAJGARH II 400kV | 2012-12-28 | 21:07 | 2012-12-31 | 06:51 | - | - | - | 1900-01-01 09:44 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2653 | LD 12/2846
182 | 912172 | KHANDWA-RAJGARH II 400kV | 2012-12-31 | 22:12 |  |  | - | - | - | 0.075 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2914
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-08 22:46
111 | 912101 | MUNDRA (CGPL) - JETPUR (GETCO) 400kV | 2012-12-19 | 15:37 | 2012-12-19 | 19:08 | - | - | - | 0.14653 | OSFD | H/T to avail S/D by Mundra to attend hot spot. | LD 12/1737 | LD 12/1768
166 | 912157 | MUNDRA (CGPL) - JETPUR (GETCO) 400kV | 2012-12-29 | 09:23 | 2012-12-31 | 17:37 | - | - | - | 1900-01-01 08:14 | LCSD | H/T for removing LILO at Jetpur (Line Brought back as 400kV Mundra - Limdi # 1) | LD 12/2696 | LD 12/2899
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 11:45
75 | 912066 | MUNDRA-BHACHAU I 400kV | 2012-12-13 | 04:42 | 2012-12-13 | 04:52 | 0 | 0.0069444 | - | - | LART | Line A/R from Bhachau end only on Y ph to E/F ,F/L:71.2 km from Bhachau and subsequently line tripped on receipt of DT from Mundra (CGPL) end. |  | LD12/1102
127 | 912117 | MUNDRA-BHACHAU I 400kV | 2012-12-22 | 04:00 | 2012-12-22 | 08:03 | - | - | - | 0.16875 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2070
131 | 912121 | MUNDRA-BHACHAU I 400kV | 2012-12-22 | 17:18 | 2012-12-23 | 17:51 | - | - | - | 1899-12-31 00:33 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2131
|  | SUBTOTAL |  |  |  |  | 0 | 0.0069444 | 0 | 1899-12-31 04:36
99 | 912089 | MUNDRA-BHACHAU II 400kV | 2012-12-18 | 15:09 | 2012-12-19 | 02:38 | - | - | - | 0.47847 | OSFD | Line H/T from Bachau due to fire in wave trap at Mundra end |  | LD 12/1666
154 | 912144 | MUNDRA-BHACHAU II 400kV | 2012-12-27 | 11:20 | 2012-12-27 | 17:55 | - | - | - | 0.27431 | OSFD | H/T to attend Hot Spot at CGPL end. S/D availed by CGPL. | LD12/2521
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.75278
167 | 912158 | MUNDRA-LIMBDI II 400kV | 2012-12-29 | 11:24 | 2012-12-29 | 11:43 | - | 0.013194 | - | - | OMSU | A/T at Mundra end |  | LD 12/2711
|  | SUBTOTAL |  |  |  |  | 0 | 0.013194 | 0 | 0
11 | 912002 | NAGDA-DEHGAM I 400KV | 2012-12-01 | 03:17 | 2012-12-01 | 07:34 | - | - | - | 0.17847 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/05 | LD 12/11
17 | 912008 | NAGDA-DEHGAM I 400kV | 2012-12-02 | 06:06 | 2012-12-02 | 07:18 | - | - | 0.05 | - | GOVC | Line A/T due to receipt of D/T from Nagda MPPTCL end due to operation of O/V Stage - I at Nagda (MPPTCL). |  | LD 12/111
97 | 912087 | NAGDA-DEHGAM I 400KV | 2012-12-17 | 23:53 | 2012-12-18 | 07:01 | - | - | - | 0.29722 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1548 | LD 12/1554
104 | 912094 | NAGDA-DEHGAM I 400KV | 2012-12-19 | 00:02 | 2012-12-19 | 08:36 | - | - | - | 0.35694 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1658 | LD 12/1681
116 | 912106 | NAGDA-DEHGAM I 400KV | 2012-12-20 | 03:11 | 2012-12-20 | 08:34 | - | - | - | 0.22431 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1807 | LD 12/1824
153 | 912143 | NAGDA-DEHGAM I 400KV | 2012-12-27 | 03:21 | 2012-12-27 | 09:05 | - | - | - | 0.23889 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2491 | LD12/2500
173 | 912164 | NAGDA-DEHGAM I 400KV | 2012-12-30 | 23:33 | 2012-12-31 | 06:50 | - | - | - | 0.30347 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2835 | LD 12/2848
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.05 | 1899-12-31 14:23
15 | 912006 | NAGDA-DEHGAM II 400kV | 2012-12-02 | 02:10 | 2012-12-02 | 06:39 | - | - | - | 0.18681 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/96
93 | 912083 | NAGDA-DEHGAM II 400kV | 2012-12-17 | 01:33 | 2012-12-17 | 06:42 | - | - | - | 0.21458 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1461 | LD 12/1472
133 | 912123 | NAGDA-DEHGAM II 400kV | 2012-12-23 | 03:19 | 2012-12-24 | 10:03 | - | - | - | 1899-12-31 06:44 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2161 | LD 12/2239
158 | 912149 | NAGDA-DEHGAM II 400kV | 2012-12-28 | 02:10 | 2012-12-28 | 07:10 | - | - | - | 0.20833 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2582 | LD12/2590
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 21:22
6 | 911084 | RAJGARH-NAGDA I 400kV (LILO) | 2012-11-24 | 03:04 | 2012-12-05 | 17:08 | - | - | - | 1900-01-03 17:08 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 11/2030 | LD12/427
85 | 912075 | RAJGARH-NAGDA I 400kV (LILO) | 2012-12-15 | 05:32 | 2012-12-15 | 06:38 | - | 0.045833 | - | - | SBBU | Line A/T only at Nagda end due to operation of Bus bar protection at Nagda (MPPTCL). |  | LD 12/1326
130 | 912120 | RAJGARH-NAGDA I 400kV (LILO) | 2012-12-22 | 16:33 |  |  | - | - | - | 1900-01-08 07:27 | OSPD | Line H/T to avail S/D by MPPTCL for checking of isolators at Nagda (MPPTCL). | LD 12/2123
|  | SUBTOTAL |  |  |  |  | 0 | 0.045833 | 0 | 1900-01-13 00:35
34 | 912025 | RAJGARH-NAGDA II 400kV (LILO) | 2012-12-05 | 18:15 | 2012-12-22 | 16:06 | - | - | - | 1900-01-15 21:51 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/439 | LD 12/2118
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-15 21:51
4 | 911058 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2012-11-17 | 18:41 | 2012-12-05 | 18:08 | - | 1900-01-03 18:08 | - | - | OMSU | Line A/T on SOTF, CS, Z-1, 3 Ph trip, F/L 74kM from Rajgarh (under MPPTCL jurisdiction). | - | LD12/428
33 | 912024 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2012-12-05 | 18:09 | 2012-12-05 | 18:09 | - | 0 | - | - | OMSU | Line A/R on Y ph to E/F.75 km from rajgarh
35 | 912026 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2012-12-05 | 19:02 |  |  | - | - | - | 1900-01-25 04:58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/444
|  | SUBTOTAL |  |  |  |  | 0 | 1900-01-03 18:08 | 0 | 1900-01-25 04:58
87 | 912077 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2012-12-15 | 17:05 | 2012-12-15 | 17:19 | - | - | 0.0097222 | - | GOVC | Line A/T due to operation of O/V protection at SSP and receipt of DT at Rajgarh |  | LD/12/1366
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.0097222 | 0
8 | 911102 | SASAN (RELIANCE) - JABALPUR 400kV | 2012-11-27 | 14:54 | 2012-12-06 | 09:58 | - | - | - | 1900-01-04 09:58 | LCSD | Line H/T for shifting of loopin circuit at sasan | LD 11/2397 | LD 12/486
172 | 912163 | SASAN (RELIANCE) - JABALPUR 400kV | 2012-12-30 | 17:35 | 2012-12-30 | 18:10 | - | - | 0.024306 | - | GOVC | A/T on D/T received from SASAN due to operation of O/V Protection at SASAN. |  | LD 12/2818
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.024306 | 1900-01-04 09:58
23 | 912014 | SATNA-BINA(PG) I 400kV | 2012-12-03 | 23:59 | 2012-12-04 | 07:45 | - | - | - | 0.32361 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/283 | LD 12/298
30 | 912021 | SATNA-BINA(PG) I 400kV | 2012-12-05 | 04:25 | 2012-12-05 | 07:50 | - | - | - | 0.14236 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/384 | LD 12/391
44 | 912035 | SATNA-BINA(PG) I 400kV | 2012-12-06 | 23:08 | 2012-12-07 | 06:38 | - | - | - | 0.3125 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/553 | ld 12/565
50 | 912041 | SATNA-BINA(PG) I 400kV | 2012-12-08 | 08:16 | 2012-12-08 | 19:37 | 0.47292 | - | - | - | OMST | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD 12/634 | LD 12/702
54 | 912045 | SATNA-BINA(PG) I 400kV | 2012-12-09 | 08:40 | 2012-12-09 | 18:22 | 0.40417 | - | - | - | OMST | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD 12/720 | LD 12/760 | No clear as the Shutdown was planned or not ,and its maintenance work not new system excecution (OMST)
84 | 912074 | SATNA-BINA(PG) I 400kV | 2012-12-15 | 03:40 | 2012-12-15 | 06:21 | - | - | - | 0.11181 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1321 | LD 12/1324
113 | 912103 | SATNA-BINA(PG) I 400kV | 2012-12-19 | 22:44 | 2012-12-20 | 08:22 | - | - | - | 0.40139 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1791 | LD 12/1822
140 | 912130 | SATNA-BINA(PG) I 400kV | 2012-12-24 | 03:17 | 2012-12-24 | 06:40 | - | - | - | 0.14097 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2223 | LD 12/2228
149 | 912139 | SATNA-BINA(PG) I 400kV | 2012-12-26 | 02:54 | 2012-12-26 | 08:44 | - | - | - | 0.24306 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/2403 | LD 12/2410
170 | 912161 | SATNA-BINA(PG) I 400kV | 2012-12-30 | 03:07 | 2012-12-30 | 07:05 | - | - | - | 0.16528 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2770 | LD 12/2776
175 | 912166 | SATNA-BINA(PG) I 400kV | 2012-12-31 | 00:04 | 2012-12-31 | 06:06 | - | - | - | 0.25139 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2838 | LD 12/2845
181 | 912171 | SATNA-BINA(PG) I 400kV | 2012-12-31 | 21:29 |  |  | - | - | - | 0.10486 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2910
|  | SUBTOTAL |  |  |  |  | 0.87708 | 0 | 0 | 1900-01-01 04:44
10 | 912001 | SATNA-BINA(PG) II 400kV | 2012-12-01 | 00:02 | 2012-12-01 | 07:50 | - | - | - | 0.325 | LVRD | Line H/T for voltage regulation on WRLDC instruction. | LD 11/2742 | LD 12/75
12 | 912003 | SATNA-BINA(PG) II 400kV | 2012-12-01 | 07:50 | 2012-12-01 | 18:55 | - | - | - | 0.46181 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis.
16 | 912007 | SATNA-BINA(PG) II 400kV | 2012-12-02 | 02:52 | 2012-12-02 | 08:05 | - | - | - | 0.21736 | LVRD | Line H/T for voltage regulation on WRLDC instruction. | LD 12/101 | LD 12/115
18 | 912009 | SATNA-BINA(PG) II 400kV | 2012-12-02 | 08:05 | 2012-12-02 | 18:29 | - | - | - | 0.43333 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD 12/115
21 | 912012 | SATNA-BINA(PG) II 400kV | 2012-12-03 | 10:06 | 2012-12-03 | 18:52 | - | - | - | 0.36528 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD 12/189 | LD 12/259
24 | 912015 | SATNA-BINA(PG) II 400kV | 2012-12-04 | 08:30 | 2012-12-04 | 18:06 | - | - | - | 0.4 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD12/303 | LD 12/348
32 | 912023 | SATNA-BINA(PG) II 400kV | 2012-12-05 | 10:14 | 2012-12-05 | 18:51 | - | - | - | 0.35903 | LCSD | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD12/405 | LD12/438
39 | 912030 | SATNA-BINA(PG) II 400kV | 2012-12-05 | 23:25 | 2012-12-05 | 23:58 | 0.022917 | - | - | - | LEFT | Line A/T due to B ph to E/F .F/L:148.2 kM from Bina.
40 | 912031 | SATNA-BINA(PG) II 400kV | 2012-12-05 | 23:58 | 2012-12-06 | 09:25 | - | - | - | 0.39375 | LVRD | Line kept out on V/R on WRLDC instruction ( Test charging not permitted by WRLDC due to prevailing system high voltgae). | LD 12/473
41 | 912032 | SATNA-BINA(PG) II 400kV | 2012-12-06 | 09:25 | 2012-12-06 | 12:13 | 0.11667 | - | - | - | LHWT | S/D availed by PowerGrid for replacement of B-ph insulator string at Loc 324. | LD 12//490 | LD 12/514
57 | 912048 | SATNA-BINA(PG) II 400kV | 2012-12-10 | 13:07 | 2012-12-10 | 19:06 | 0.24931 | - | - | - | OMST | S/D availed by Powergrid for Insulator replacement work based on PID analysis. | LD 12/836 | LD 12/877 | No clear as the Shutdown was planned or not ,and its maintenance work not new system excecution (OMST)
90 | 912080 | SATNA-BINA(PG) II 400kV | 2012-12-16 | 03:33 | 2012-12-16 | 06:14 | - | - | - | 0.11181 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1407 | LD 12/1410
105 | 912095 | SATNA-BINA(PG) II 400kV | 2012-12-19 | 00:52 | 2012-12-19 | 08:53 | - | - | - | 0.33403 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1660 | LD 12/1679
|  | SUBTOTAL |  |  |  |  | 0.38889 | 0 | 0 | 1900-01-02 09:38
53 | 912044 | SATNA-BINA(PG) III 400kV | 2012-12-08 | 21:14 | 2012-12-08 | 21:57 | - | - | - | 0.029861 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/707 | LD12/708
67 | 912058 | SATNA-BINA(PG) III 400kV | 2012-12-12 | 03:10 | 2012-12-12 | 06:44 | - | - | - | 0.14861 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1003 | LD12/1010
92 | 912082 | SATNA-BINA(PG) III 400kV | 2012-12-17 | 01:27 | 2012-12-17 | 07:44 | - | - | - | 0.26181 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1460 | LD 12/1479
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.44028
60 | 912051 | SATNA-BINA(PG) IV 400kV | 2012-12-10 | 23:15 | 2012-12-11 | 09:10 | - | - | - | 0.41319 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/889 | LD 12/899
98 | 912088 | SATNA-BINA(PG) IV 400kV | 2012-12-18 | 00:10 | 2012-12-18 | 07:46 | - | - | - | 0.31667 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1550 | LD 12/1560
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.72986
61 | 912052 | SATPURA-ITARSI 400kV | 2012-12-11 | 09:51 | 2012-12-11 | 18:11 | - | - | - | 0.34722 | OSFD | Line H/T to avail emergency S/D by MPPTCL | LD 12/914 | LD12/976
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.34722
89 | 912079 | SEONI-KHANDWA I 400kV | 2012-12-16 | 02:25 | 2012-12-16 | 05:54 | - | - | - | 0.14514 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1411
94 | 912084 | SEONI-KHANDWA I 400kV | 2012-12-17 | 01:43 | 2012-12-17 | 05:31 | - | - | 0.0069444 | 0.15139 | GOVC | A/T on D/T received from Seoni due to operation of O/V Protection,'Line kept out for voltage regulation on WRLDC instruction. |  | LD 12/1467
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.0069444 | 0.29653
59 | 912050 | SEONI-KHANDWA II 400kV | 2012-12-10 | 21:02 | 2012-12-10 | 21:12 | - | - | 0.0069444 | - | GOVC | A/T on operation of O/V Protection at Khandwa during H/T of 400kV Khandwa - Rajgarh # 1 |  | LD 12/884
82 | 912073 | SEONI-KHANDWA II 400kV | 2012-12-15 | 03:03 | 2012-12-15 | 06:29 | - | - | - | 0.14306 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1317 | LD 12/1325
106 | 912096 | SEONI-KHANDWA II 400kV | 2012-12-19 | 02:58 | 2012-12-19 | 08:59 | - | - | - | 0.25069 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD12/1669 | LD 12/1684
134 | 912124 | SEONI-KHANDWA II 400kV | 2012-12-23 | 03:47 | 2012-12-23 | 06:33 | - | - | - | 0.11528 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2163 | LD 12/2166
139 | 912129 | SEONI-KHANDWA II 400kV | 2012-12-23 | 22:49 | 2012-12-24 | 08:28 | - | - | - | 0.40208 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/2212
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.0069444 | 0.91111
137 | 912127 | SUGEN-VAPI 400kV | 2012-12-23 | 11:12 | 2012-12-23 | 13:28 | - | 0.094444 | - | - | OMSU | H/T for installation of PMU at Suzan as per WRLDC instructions. | LD 12/2187 | LD 12/2193
|  | SUBTOTAL |  |  |  |  | 0 | 0.094444 | 0 | 0
171 | 912162 | VINDHYACHAL (NTPC) -SASAN (RELIANCE) 400kV | 2012-12-30 | 17:20 | 2012-12-30 | 18:10 | - | 0.034722 | - | - | OMSU | H/T to facilitate firdt time charging of 400/765kV ICT at SASAN Reliance. | LD 12/2511 | LD 12/2817
179 | 912169 | VINDHYACHAL (NTPC) -SASAN (RELIANCE) 400kV | 2012-12-31 | 15:38 | 2012-12-31 | 16:03 | - | 0.017361 | - | - | OMSU | H/T to facilitate firdt time charging of 400/765kV ICT at SASAN Reliance. | LD 12/2880 | LD 12/2888
|  | SUBTOTAL |  |  |  |  | 0 | 0.052083 | 0 | 0
145 | 912135 | VINDHYACHAL-JABALPUR I 400kV | 2012-12-25 | 09:56 | 2012-12-25 | 22:36 | - | - | - | 0.52778 | LCSD | Line H/T for stringing of 765kV sasan satna line | LD12/2344 | LD12/2389
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.52778
146 | 912136 | VINDHYACHAL-JABALPUR II 400kV | 2012-12-25 | 10:24 | 2012-12-25 | 22:43 | - | - | - | 0.51319 | LCSD | Line H/T for stringing of 765kV sasan satna line | LD12/2351 | LD12/2392
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.51319
83 |  | VAPI - BOISAR 400kV | 2012-12-15 | 03:20 | 2012-12-15 | 03:26 | - | - | - | 0.0041667 | LCSD | H/T to facilitate shifting / movement of new ICT # 3 at Vapi S/Y. | LD 12/1319 | LD 12/1320
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.0041667
220 kV TRANSMISSION LINES
150 | 912140 | KAKRAPAR-HALDARWA I 220kV | 2012-12-26 | 8:00 | 2012-12-26 | 19:16 | - | - | - | 0.46944 | OSPD | Line H/T to avail S/D by GETCO for stringing of line | LD12/2409 | LD12/2465
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.46944
151 | 912141 | KAKRAPAR-HALDARWA II 220kV | 2012-12-26 | 8:00 | 2012-12-26 | 19:44 | - | - | - | 0.48889 | OSPD | Line H/T to avail S/D by GETCO for stringing of line | LD12/2409 | LD12/2468
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.48889
128 | 912118 | KAKRAPAR-VAV II 220kV | 2012-12-22 | 10:20 | 2012-12-22 | 12:54 | - | 0.10694 | - | - | OMSU | Line A/T at Vav(GETCO) end only due to suspected DC earth leakege at Vav end |  | LD 12/2107
|  | SUBTOTAL |  |  |  |  | 0 | 0.10694 | 0 | 0
3 | 911106 | KAWAS-HALDARWA I 220kV | 2012-11-28 | 10:02 | 2012-12-19 | 14:14 | - | - | - | 1900-01-17 14:14 | LPRD | H/T on Power Regulation on WRLDC Instructions. | - | LD 12/1724
156 | 912146 | KAWAS-HALDARWA I 220kV | 2012-12-27 | 12:02 |  |  | - | - | - | 1900-01-02 11:58 | LPRD | H/T on Power Regulation on WRLDC Instructions.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-21 02:12
110 | 912100 | KAWAS-HALDARWA II 220kV | 2012-12-19 | 15:07 | 2012-12-27 | 12:01 | - | - | - | 1900-01-06 20:54 | LPRD | H/T on Power Regulation on WRLDC Instructions. | LD 12/1725
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-06 20:54
101 | 912091 | KAWAS-ICHCHAPUR#2 220kV | 2012-12-18 | 09:35 | 2012-12-18 | 17:23 | - | - | - | 0.325 | OSPD | Line H/T to avail S/D by NTPC kawas |  | LD12/1624
102 | 912092 | KAWAS-ICHCHAPUR#2 220kV | 2012-12-18 | 20:26 | 2012-12-18 | 21:09 | - | - | - | 0.029861 | OSFD | Line H/T due to sparking at kawas end | LD12/1643 | LD12/1644
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.35486
122 | 912112 | KAWAS-NAVSARI (PG GIS) I 220kV | 2012-12-21 | 10:00 | 2012-12-21 | 20:25 | - | - | - | 0.43403 | OSPD | Line H/T to avail S/D by NTPC for relay testing at Kawas | LD 12/1983 | LD 12/2039
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.43403
55 | 912046 | KAWAS-NAVSARI (PG GIS) II 220kV | 2012-12-09 | 22:59 | 2012-12-09 | 23:26 | 0.01875 | - | - | - | LEFT | A/T on RY Ph to Ph fault from both ends,F/L - 27kM from NAV (GIS). |  | LD 12/776
123 | 912113 | KAWAS-NAVSARI (PG GIS) II 220kV | 2012-12-21 | 13:02 | 2012-12-21 | 19:21 | - | - | - | 0.26319 | OSPD | Line H/T to avail S/D by NTPC for relay testing at Kawas | LD 12/2006 | LD 12/2037
|  | SUBTOTAL |  |  |  |  | 0.01875 | 0 | 0 | 0.26319
64 | 912055 | KAWAS-VAV I 220kV | 2012-12-11 | 14:53 | 2012-12-11 | 15:19 | - | - | 0.018056 | - | LMAC | Line A/T on B ph to E/F due to burning of sugarcane waste. F/L:8.97kM from kawas |  | LD12/950
129 | 912119 | KAWAS-VAV I 220kV | 2012-12-22 | 13:25 | 2012-12-22 | 20:00 | - | - | - | 0.27431 | OSPD | Line H/T to avail S/D by NTPC Kawas for Relay Testing at Kawas | LD 12/2104 | LD 12/2142
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0.018056 | 0.27431
178 | 912168 | KAWAS-VAV II 220kV | 2012-12-31 | 11:49 | 2012-12-31 | 17:33 | 0.0069444 | 0.23194 | - | - | OMSU | A/T on R-ph to E/F, F/L - 10.54kM from VAV, Test charging delayed by VAV GETCO due to persisting of CB PD alarm. |  | LD 12/2896
|  | SUBTOTAL |  |  |  |  | 0.0069444 | 0.23194 | 0 | 0
163 | 912154 | NAVSARI (PG GIS)-NAVSARI I 220kV | 2012-12-29 | 07:19 | 2012-12-29 | 07:36 | 0.011806 | - | - | - | LEFT | A/T on Y-ph to E/F from both ends,F/L - 12.93kM (NAV GIS)
165 | 912156 | NAVSARI (PG GIS)-NAVSARI I 220kV | 2012-12-29 | 07:36 | 2012-12-29 | 18:45 | - | 0.46458 | - | - | OMSU | Test charging delayed by NAV GETCO due to CB Problem. |  | LD 12/2735
|  | SUBTOTAL |  |  |  |  | 0.011806 | 0.46458 | 0 | 0
164 | 912155 | NAVSARI (PG GIS)-NAVSARI II 220kV | 2012-12-29 | 07:19 | 2012-12-29 | 07:41 | 0.015278 | - | - | - | OMST | Line A/T at Navsari GIS only |  | LD 12/2690
|  | SUBTOTAL |  |  |  |  | 0.015278 | 0 | 0 | 0
147 | 912137 | VAPI-KHADOLI I 220kV | 2012-12-25 | 11:45 | 2012-12-25 | 12:13 | - | 0.019444 | - | - | OMSU | Line A/T due to problem at khadoli end.DT received at vapi end |  | LD12/2362
|  | SUBTOTAL |  |  |  |  | 0 | 0.019444 | 0 | 0
135 | 912125 | VAPI-KHARADPARA I 220kV | 2012-12-23 | 07:42 | 2012-12-23 | 19:53 | - | - | - | 0.50764 | LCSD | H/T to avail OCC Approved S/D to facilitate stringing work of new 400kV NAV-VAPI-Boisar Line. | LD 12/2174 | LD 12/2207
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.50764
136 | 912126 | VAPI-KHARADPARA II 220kV | 2012-12-23 | 07:43 | 2012-12-24 | 13:02 | - | - | - | 1899-12-31 05:19 | LCSD | H/T to avail OCC Approved S/D to facilitate stringing work of new 400kV NAV-VAPI-Boisar Line. | LD 12/2175
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1899-12-31 05:19
ICTs
51 | 912042 | ICT1 JABALPUR 400/220kV | 2012-12-08 | 10:54 | 2012-12-08 | 10:57 | - | 0.0020833 | - | - | OMSU | H/T to change Tap position from 9b-11 | LD 12/652
56 | 912047 | ICT1 JABALPUR 400/220kV | 2012-12-10 | 12:27 | 2012-12-10 | 14:34 | - | - | - | 0.088194 | LPRD | H/T on Power Regulation on WRLDC Instructions from 220kV side only. | LD 12/830 | LD 12/844
142 | 912132 | ICT1 JABALPUR 400/220kV | 2012-12-24 | 10:32 | 2012-12-24 | 12:20 | - | - | - | 0.075 | SPRD | H/T on Power Regulation on WRLDC Instructions. | LD 12/2253 | LD 12/2268
|  | SUBTOTAL |  |  |  |  | 0 | 0.0020833 | 0 | 0.16319
52 | 912043 | ICT2 JABALPUR 400/220kV | 2012-12-08 | 10:57 | 2012-12-08 | 12:40 | - | 0.071528 | - | - | OMSU | H/T to change Tap position from 9b-12 | LD 12/653
62 | 912053 | ICT2 JABALPUR 400/220kV | 2012-12-11 | 10:31 | 2012-12-11 | 12:10 | - | - | - | 0.06875 | LPRD | ICT H/T from 220kV side on P/R | LD12/924 | LD12/938
|  | SUBTOTAL |  |  |  |  | 0 | 0.071528 | 0 | 0.06875
117 | 912107 | ICT1 SATNA 400/220KV | 2012-12-20 | 10:20 | 2012-12-20 | 13:17 | - | - | - | 0.12292 | SPRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1857 | LD 12/1880
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.12292
118 | 912108 | ICT2 SATNA 400/220KV | 2012-12-20 | 10:20 | 2012-12-20 | 13:36 | - | - | - | 0.13611 | SPRD | Line H/T for voltage regulation on WRLDC instruction | LD 12/1857 | LD 12/1880
141 | 912131 | ICT2 SATNA 400/220kV | 2012-12-24 | 06:35 | 2012-12-24 | 11:10 | 0.19097 | - | - | - | SEFT | A/T on operation Diff protection due B-ph isolator support insulator of ICT incomer isolator.
|  | SUBTOTAL |  |  |  |  | 0.19097 | 0 | 0 | 0.13611
155 | 912145 | ICT2 SATNA 765/400kV | 2012-12-27 | 11:35 | 2012-12-27 | 16:31 | - | - | - | 0.20556 | SCSD | H/T for Jumpering of Earth Wire. | LD12/2518 | LD12/2533
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.20556
76 | 912067 | ICT2 BHACHAU 400/220/33kV | 2012-12-13 | 11:23 | 2012-12-13 | 17:25 | 0.25139 | - | - | - | OMST | OCC approved S/D availed by Powergrid replacement of faulty (tan-delta violation) 220kV Y- ph bushing of ICT#2. | LD 12/1128 | LD 12/1167
|  | SUBTOTAL |  |  |  |  | 0.25139 | 0 | 0 | 0
Bus Reactors
1 | 911001 | BUS REACTOR SATNA 765kV | 2012-11-01 | 00:00 | 2012-12-27 | 18:15 | - | - | - | 1900-01-25 18:15 | SVRD | Bus Reactor kept out for voltage regulation | LD 10/2848
156 | 912147 | BUS REACTOR SATNA 765kV | 2012-12-27 | 18:34 | 2012-12-27 | 23:08 | - | - | - | 0.19028 | SVRD | H/T for voltage regulation on WRLDC instruction | LD12/2544 | LD12/2576
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-25 22:49
Remarks:- The trippings are yet to be certified by WRLDC. Hence the exact time attrituable to POWERGRID WRTS - 2 will be reflected in trippings only after final certification of trippings by WRLDC.
Formulas:
ATTRIBUTED TO PGCIL = IF((RIGHT([CAT CODE],1)="T"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
ATTRIBUTED TO PGCIL = SUM([ATTRIBUTED TO PGCIL, row above])
OUTAGE HOURS ATTRIBUTED TO = SUM([OUTAGE HOURS ATTRIBUTED TO, row above])
OUTAGE HOURS ATTRIBUTED TO = SUM(I14:[OUTAGE HOURS ATTRIBUTED TO, row above])
SYSTEM CONSTR. = SUM([SYSTEM CONSTR., row above])
SYSTEM CONSTR. = SUM(J14:[SYSTEM CONSTR., row above])
OUTAGE DEEMED AVAILABLE = SUM([OUTAGE DEEMED AVAILABLE, row above])
OUTAGE DEEMED AVAILABLE = SUM(K14:[OUTAGE DEEMED AVAILABLE, row above])

## ANX-II
MONTH : DEC-2012
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : DEC-2012
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
December 2012
Sl. No. | Name of Element | Type of failures | Restoration Time (Days) |  |  | Remarks
A |  | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 |  | Insualtor Failure | Terrain Type
|  |  | Plain | River bed | Hilly
i | SATNA-BINA(PG) II 400kV | Insualtor Failure in single phase | Less than 1 day
ii |  | Insualtor Failure in two phases | NIL
ii |  | Insualtor Failure in three phases
2 |  | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 |  | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 |  | Tower Damage ( not collapse)
i |  | One arm damage
ii |  | Two arm damage
5 |  | Snapping of phase conductor
i |  | Conductor snapping in single phase | NIL
ii |  | Conductor snapping in two phases
iii |  | Conductor snapping in three phases
6 |  | Failure of Earth wire
7 |  | Insulator failure with conductor snapping
8 |  | Any other combination of failures
B |  | Elements of sub-station for each KV class seperately
1 |  | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
|  | Other major failures in ICTs | Single phase Unit |  | Three phase Unit
|  | (i) Replacement of faulty bushings | NIL
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 |  | Failures of Reactors
Restoration of failed Reactors

## Supporting Annex V
TRIPPING DETAILS OF WR-II FOR THE MONTH OF DECEMBER 2012
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | CAT CODE | Details | Restoration (Days) |  |  | REMARKS
[8 empty] | OTHERS | SYSTEM CONSTR |  |  |  | Flashover | Snapping | Collapes of Tower
1 | 912030 | SATNA-BINA(PG) II 400kV | 2012-12-05 | 23:25 | 2012-12-05 | 23:58 | 0.022917 | - | - | - | LHWT | Line A/T due to B ph to E/F .F/L:148.2 kM from Bina. During patrolling Insulator string found flashover at Loc. No. 324. | 0.022917
Formulas:
ATTRIBUTED TO PGCIL = IF((RIGHT([CAT CODE],1)="T"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")

## for prints
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR DECEMBER - 2012
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line |  | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | Element_wise_% availability
No. | [5 empty] | attr. to | attr. to | Individual | length
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC]
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 100
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 100
3 | 400kV Itarsi-Indore # 2 |  |  | 0 | 16 | 0 | 0.26667 | 743.7333 | 214 | 2 | 0 | 428 | 318317.8667 | 100
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 100
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 100
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 100
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 100
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 100
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 100
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 100
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 100
12 | 400 KV Jabalpur-Sasan |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 376 | 2 | 0 | 752 | 559049.3333 | 100
13 | 400kV Sasan-Vindhyachal |  |  | 1 | 15 | 0 | 1.25 | 742.75 | 21 | 2 | 0 | 42 | 31195.5 | 100
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 100
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 100
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 100
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 100
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 100
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 100
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 100
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 100
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 2 | 16 | 0 | 2.2667 | 741.7333 | 110 | 2 | 0 | 220 | 163181.3333 | 100
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 100
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 100
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 100
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 100
27 | 220kV Kawas-Navsari (GIS)#2 | 0 | 27 |  |  | 0.45 | 0 | 744 | 58.149 | 1 | 26.167 | 58.149 | 43262.856 | 99.9395
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 0 | 17 | 11 | 9 | 0.28333 | 11.15 | 732.85 | 31.334 | 1 | 8.878 | 31.334 | 22963.1219 | 99.9613
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 31.334 | 1 | 11.4891 | 31.334 | 23312.496 | 99.9507
30 | 220kV Kawas-Vav#1 |  |  | 0 | 26 | 0 | 0.43333 | 743.5667 | 37 | 1 | 0 | 37 | 27511.9667 | 100
31 | 220kV Kawas-Vav#2 | 0 | 10 | 5 | 34 | 0.16667 | 5.5667 | 738.4333 | 37 | 1 | 6.1667 | 37 | 27322.0333 | 99.9774
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 100
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 100
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 100
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 100
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 100
37 | 220 KV Kakrapar - Vav # 2 |  |  | 2 | 34 | 0 | 2.5667 | 741.4333 | 43 | 1 | 0 | 43 | 31881.6333 | 100
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 100
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 100
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 100
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 100
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 100
43 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 100
44 | 400kV Satna - Bina # 1 | 21 | 3 |  |  | 21.05 | 0 | 744 | 276 | 2 | 11619.6 | 552 | 410688 | 97.1707
45 | 400kV Satna - Bina # 2 | 9 | 20 |  |  | 9.3333 | 0 | 744 | 276 | 2 | 5152 | 552 | 410688 | 98.7455
46 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 100
47 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 100
48 | 765 kV Gwalior-Bina # 1 * | 7 | 37 |  |  | 7.6167 | 0 | 744 | 234.931 | 4 | 7157.5645 | 939.724 | 699154.656 | 98.9763
49 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 100
50 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 100
51 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 100
52 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 100
53 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 100
54 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 100
55 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 100
56 | 400KV Nagda - Dehgam # 1 |  |  | 1 | 12 | 0 | 1.2 | 742.8 | 331.442 | 2 | 0 | 662.884 | 492390.2352 | 100
57 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 100
58 | 400KV Seoni - Khandwa # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 100
59 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 100
60 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 114 | 8 | 0 | 114.1333 | 629.8667 | 4.01 | 2 | 0 | 8.02 | 5051.5307 | 100
61 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 4.01 | 2 | 0 | 8.02 | 5965.0087 | 100
62 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  | 1 | 6 | 0 | 1.1 | 742.9 | 4.12 | 2 | 0 | 8.24 | 6121.496 | 100
63 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 100
64 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 100
65 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 100
66 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 100
67 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 100
68 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 100
69 | 765 kV Gwalior-Bina # 2 * | 6 | 56 |  |  | 6.9333 | 0 | 744 | 233.652 | 4 | 6479.9488 | 934.608 | 695348.352 | 99.0681
70 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 100
71 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 100
72 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 100
73 | 220 KV Vapi - Khadoli # 1 |  |  | 0 | 28 | 0 | 0.46667 | 743.5333 | 28.549 | 1 | 0 | 28.549 | 21227.1331 | 100
74 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 100
75 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 100
76 | 400kV Damoh-Birsinghpur#2 | 0 | 7 |  |  | 0.11667 | 0 | 744 | 228.474 | 2 | 53.3106 | 456.948 | 339969.312 | 99.9843
77 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 100
78 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 100
79 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 100
80 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 100
81 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 100
82 | 400kV Bhachau - Ranchodpura # 2 | 3 | 5 |  |  | 3.0833 | 0 | 744 | 282.856 | 3 | 2616.418 | 848.568 | 631334.592 | 99.5856
83 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 100
84 | 400kV Mundra - Limbdi # 2 |  |  | 0 | 19 | 0 | 0.31667 | 743.6833 | 314.053 | 3 | 0 | 942.159 | 700667.9457 | 100
85 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 100
86 | 765kV Satna - Bina # 2 |  |  | 467 | 35 | 0 | 467.5833 | 276.4167 | 275.635 | 4 | 0 | 1102.54 | 304760.4317 | 100
87 | 765kV Bina - Indore * |  |  |  |  | 0 | 0 | 744 | 311.17 | 4 | 0 | 1244.68 | 926041.92 | 100
88 | 400kV Gandhar - Navsari # 2 |  |  | 0 | 55 | 0 | 0.91667 | 743.0833 | 102.15 | 2 | 0 | 204.3 | 151811.925 | 100
89 | LILO of Mundra-Limbdi#1 at Jetpur (GETCO) |  |  |  |  | 0 | 0 | 744 | 313 | 3 | 0 | 939 | 698616 | 100
90 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.15 | 2 | 0 | 204.3 | 151999.2 | 100
91 | 400 kV Gwalior -Agra # 1 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 129.435 | 4 | 0 | 517.74 | 385198.56 | 100
92 | 400 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 100
93 | 400/220kV ICT # 1 / Jabalpur. |  |  | 0 | 3 | 0 | 0.05 | 743.95 | 315 | 2.5 | 0 | 787.5 | 585860.625 | 100
94 | 400/220kV ICT # 2 /Jabalpur. |  |  | 1 | 43 | 0 | 1.7167 | 742.2833 | 315 | 2.5 | 0 | 787.5 | 584548.125 | 100
95 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
96 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
97 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100 | 0.83333
98 | 400/220kV ICT # 2 / Satna | 4 | 35 |  |  | 4.5833 | 0 | 744 | 315 | 2.5 | 3609.375 | 787.5 | 585900 | 99.384
99 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
100 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
101 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
102 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
103 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
104 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
105 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
106 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
107 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
108 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
109 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
110 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
111 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
112 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
113 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
114 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
115 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
116 | 400/220 KV ICT # 2 / Bhachau | 6 | 2 |  |  | 6.0333 | 0 | 744 | 315 | 2.5 | 4751.25 | 787.5 | 585900 | 99.1891
117 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
118 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100
119 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
120 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 100
121 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100
122 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 100
123 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
124 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 100
125 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 100
126 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
127 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
128 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
129 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
130 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 100
131 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
132 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
133 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
134 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 100
135 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100
136 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100
137 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
138 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
139 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 100
140 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
141 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 100
142 | Switchable Bina-I LR/ Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
143 | Switchable Bina-II LR/ Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 100
Note on B25: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B107: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B108: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004