## Tripping AC SYSTEM (hidden)
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR MARCH- 2011
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032
5 | 400kV Indore-Asoj # 2 | 8 | 38 |  |  | 8.6333 | 0 | 744 | 273 | 2 | 4713.8 | 546 | 406224
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
8 | 400 KV Jabalpur - Itarsi # 1 | 4 | 54 |  |  | 4.9 | 0 | 744 | 232 | 2 | 2273.6 | 464 | 345216
9 | 400 KV Jabalpur - Itarsi # 2 | 6 | 25 |  |  | 6.4167 | 0 | 744 | 232 | 2 | 2977.3333 | 464 | 345216
10 | 400kV Jhanor-Dehgam#1 | 0 | 0 |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616
11 | 400kV Jhanor-Dehgam#2 | 12 | 59 |  |  | 12.9833 | 0 | 744 | 157 | 2 | 4076.7667 | 314 | 233616
12 | 400 KV V'chal - Jabalpur # 3 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
13 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
14 | 400 KV Jabalpur - Itarsi # 3 | 4 | 45 |  |  | 4.75 | 0 | 744 | 234 | 2 | 2223 | 468 | 348192
15 | 400 KV Jabalpur - Itarsi # 4 | 5 | 52 |  |  | 5.8667 | 0 | 744 | 234 | 2 | 2745.6 | 468 | 348192
16 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
17 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
18 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
19 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
20 | 400 KV Jhanor - Sugen(PGCIL portion) | 13 | 31 | 0 | 51 | 13.5167 | 0.85 | 743.15 | 57 | 2 | 1540.9 | 114 | 84719.1
21 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 9 | 3 | 0 | 9.05 | 734.95 | 110 | 2 | 0 | 220 | 161689
22 | 400 KV Jhanor - Jhanor(GPEC) |  |  | 1 | 88 | 0 | 2.4667 | 741.5333 | 13 | 2 | 0 | 26 | 19279.8667
23 | 220kV Jhanor-Haldarwa ckI # 1 | 0 | 15 | 3 | 42 | 0.25 | 3.7 | 740.3 | 13 | 1 | 3.25 | 13 | 9623.9
24 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  | 71 | 0 | 1.1833 | 742.8167 | 13 | 1 | 0 | 13 | 9656.6167
25 | 220kV Kawas-Navsari ckt # 1 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 49 | 1 | 17.9667 | 49 | 36456
26 | 220kV Kawas-Navsari ckt # 2 | 0 | 13 | 0 | 52 | 0.21667 | 0.86667 | 743.1333 | 49 | 1 | 10.6167 | 49 | 36413.5333
27 | 220kV Kawas-Ichchapur |  |  |  |  | 0 | 0 | 744 | 3 | 1 | 0 | 3 | 2232
28 | 220kV Kawas-Vav |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528
29 | 220kV Kawas - Haldarwa # 1 | 0 | 80 | 8 | 25 | 1.3333 | 8.4167 | 735.5833 | 81 | 1 | 108 | 81 | 59582.25
30 | 220kV Kawas-Haldarwa # 2 |  |  | 0 | 33 | 0 | 0.55 | 743.45 | 81 | 1 | 0 | 81 | 60219.45
31 | 220 kV Kakrapar - Haldarwa # 1 | 5 | 20 |  | 74 | 5.3333 | 1.2333 | 742.7667 | 74 | 1 | 394.6667 | 74 | 54964.7333
32 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 74 | 1 | 0 | 74 | 55012.8333
33 | 220 KV Kakrapar - Vav # 1 |  |  | 1 | 18 | 0 | 1.3 | 742.7 | 43 | 1 | 0 | 43 | 31936.1
35 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992
35 | 220kV Kakrapar-Vapi ckt # 1 | 0 | 26 |  |  | 0.43333 | 0 | 744 | 117 | 1 | 50.7 | 117 | 87048
36 | 220kV Kakrapar-Vapi ckt # 2 | 0 | 53 | 7 | 82 | 0.88333 | 8.3667 | 735.6333 | 117 | 1 | 103.35 | 117 | 86069.1
37 | 220kV Ichchapur-Vav |  |  |  |  | 0 | 0 | 744 | 34 | 1 | 0 | 34 | 25296
38 | 400kV V'chal - Satna # 1 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 267 | 2 | 0 | 534 | 397171.4
39 | 400kV V'chal - Satna # 2 | 0 | 50 | 0 | 18 | 0.83333 | 0.3 | 743.7 | 267 | 2 | 445 | 534 | 397135.8
40 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
41 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
42 | 400kV Satna - Bina # 1 | 0 | 24 |  |  | 0.4 | 0 | 744 | 276 | 2 | 220.8 | 552 | 410688
43 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688
44 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  | 1 | 49 | 0 | 1.8167 | 742.1833 | 0.742 | 2 | 0 | 1.484 | 1101.4001
45 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  | 1 | 50 | 0 | 1.8333 | 742.1667 | 0.742 | 2 | 0 | 1.484 | 1101.3753
46 | 400 kV Gwalior-Bina # 1 | 5 | 38 |  |  | 5.6333 | 0 | 744 | 234.931 | 4 | 5293.7785 | 939.724 | 699154.656
47 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
48 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
49 | 400KV Bina - Nagda # 1 | 0 | 18 |  |  | 0.3 | 0 | 744 | 330.155 | 2 | 198.093 | 660.31 | 491270.64
50 | 400KV Bina - Nagda # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 330.155 | 2 | 0 | 660.31 | 491160.5883
51 | 400KV Nagda - Dehgam # 2 |  |  | 3 | 58 | 0 | 3.9667 | 740.0333 | 331.442 | 2 | 0 | 662.884 | 490556.2561
52 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696
53 | 400KV Seoni - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
54 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
55 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
56 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
57 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
58 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
59 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
60 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
61 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
62 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
63 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
64 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
65 | 400 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352
66 | 400 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2
67 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848
68 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4
69 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
70 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
71 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
72 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
73 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
74 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
| Total Sr.No. 1 to 74 | 73 | 705 | 34 | 773 | 73.05 |  |  | 12271.634 |  | 27397.2215 |  | 19691267.3032
|  |  | 84.75 |  | 46.8833 |  |  |  |  | NAFM | 0.0013913
| Availability of 74 ( Sl no 1 to 74) transmission lines during MARCH-2011 = | [8 empty] | TAFM | 99.8609
Sr.No. 71,72,73 & 74 lines are declared for commercial operation w.e.f. 01.03.11
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
0.63333
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0.83333
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
10 | 400/220kV ICT # 2 / Vapi | 11 | 51 |  |  | 11.85 | 0 | 744 | 315 | 2.5 | 9331.875 | 787.5 | 585900
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
14 | 400/220kV ICT # 1 / Itarsi | 2 | 48 |  |  | 2.8 | 0 | 744 | 315 | 2.5 | 2205 | 787.5 | 585900
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
| Total Sr.No. 1 to 19 | 13 | 99 | 0 | 0 | 14.65 |  |  | 5040 | 47.5 | 11536.875 |  | 11132100
|  | 14.65 |  | 0 | [5 empty] | NAFM | 0.0010364
[10 empty] | TAFM | 99.8964
Availability of 19 ( Sl no 1 to 19) ICTs in MARCH-2011 =
ICT # 1 at Pirana was declared for commercial operation w.e.f. 01.03.11
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
| Total of sl no 1 to 14 | 0 | 0 | 0 | 0 |  |  |  | 882 | 56 | 0 |  | 2624832
0
[8 empty] | NAFM | 0
| Availability of 14( Sl no 1 to 14) Bus Reactors in MARCH-2011 = | [6 empty] | TAFM | 100
[11 empty] | 38934.0965 |  | 33448199.3032
[8 empty] | NAFM = | 0.001164
| % System Availability for MARCH 2011 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.8836
3
Note on B43: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B45: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B47: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B49: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B187: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B189: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-II) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-II) Transmission System in Western Region for the month of JULY- 2013 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 400kV Satpura-Itarsi | 100% | 37 | 220 KV Kakrapar - Vav # 2 | 100%
2 | 400kV Itarsi-Indore # 1 | 100% | 38 | 220kV Kakrapar-Vapi ckt # 1 | 100%
3 | 400kV Itarsi-Indore # 2 | 99.55% | 39 | 220kV Kakrapar-Vapi ckt # 2 | 100%
4 | 400kV Indore-Asoj # 1 | 100% | 40 | 400kV V'chal - Satna # 1 | 100%
5 | 400kV Indore-Asoj # 2 | 100% | 41 | 400kV V'chal - Satna # 2 | 100%
6 | 400 KV V'chal - Jabalpur # 1 | 100% | 42 | 400kV V'chal - Satna # 3 | 100%
7 | 400 KV V'chal - Jabalpur # 2 | 100% | 43 | 400kV V'chal -Nigrie | 100%
8 | 400 KV Jabalpur - Itarsi # 1 | 100% | 44 | 400kV Nigrie-Satna | 100%
9 | 400 KV Jabalpur - Itarsi # 2 | 100% | 45 | 400kV Satna - Bina # 1 | 100%
10 | 400kV Jhanor-Dehgam#1 | 100% | 46 | 400kV Satna - Bina # 2 | 100%
11 | 400kV Jhanor-Dehgam#2 | 100% | 47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 | 100%
12 | 400 KV Jabalpur-Sasan | 100% | 48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 | 100%
13 | 400kV Sasan-Vindhyachal | 100% | 49 | 765 kV Gwalior-Bina # 1 | 100%
14 | 400 KV V'chal - Jabalpur # 4 | 100% | 50 | 400KV Satna-Bina # 4 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 | 100% | 51 | 400KV Satna-Bina # 3 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 | 100% | 52 | 400KV Bina - Sujalpur # 1 | 100%
17 | 400 KV Itarsi - Khandwa # 1 | 100% | 53 | 400KV Bina - Sujalpur # 2 | 100%
18 | 400 KV Itarsi - Khandwa # 2 | 100% | 54 | 400KV Sujalpur - Nagda # 1 | 100%
19 | 400 KV Khandwa - Dhule # 1 | 100% | 55 | 400KV Sujalpur - Nagda # 2 | 100%
20 | 400 KV Khandwa - Dhule # 2 | 100% | 56 | 400KV Nagda - Dehgam # 2 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) | 100% | 57 | 400KV Nagda - Dehgam # 1 | 99.07%
22 | 400 KV Sugen - Vapi (PGCIL portion) | 100% | 58 | 400KV Seoni - Khandwa # 1 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) | 100% | 59 | 400KV Seoni - Khandwa # 2 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 | 100% | 60 | 400KV Khandwa - Rajgarh # 2 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 | 100% | 61 | 400KV Rajgarh - SSP (LILO portion) # 1 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 | 100% | 62 | 400KV Rajgarh - SSP (LILO portion) # 2 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 | 100% | 63 | 400KV Rajgarh - Nagda (LILO portion) # 1 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 100% | 64 | 400KV Rajgarh - Nagda (LILO portion) # 2 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 100% | 65 | 400KV Khandwa - Rajgarh # 1 | 100%
30 | 220kV Kawas-Vav#1 | 100% | 66 | 220 KV Vapi - Magarwada # 1 | 100%
31 | 220kV Kawas-Vav#2 | 100% | 67 | 220 KV Vapi - Magarwada # 2 | 100%
32 | 220kV Kawas - Haldarwa # 1 | 100% | 68 | 220 KV Vapi - Karadpada # 1 | 99.45%
33 | 220kV Kawas-Haldarwa # 2 | 99.36% | 69 | 220 KV Vapi - Karadpada # 2 | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 | 100% | 70 | 765 kV Gwalior-Bina # 2 | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 | 100% | 71 | 765 kV Seoni - Bina | 100%
36 | 220 KV Kakrapar - Vav # 1 | 100% | 72 | 400kV Damoh - Bhopal # 1 | 100%
73 | 400kV Damoh - Bhopal # 2 | 100% | 121 | 400/220kV ICT # 1 / Damoh | 100%
74 | 220 KV Vapi - Khadoli # 1 | 100% | 122 | 400/220kV ICT # 2 / Damoh | 100%
75 | 220 KV Vapi - Khadoli # 2 | 100% | 123 | 400/220 KV ICT # 2 / Rajgarh | 100%
76 | 400kV Damoh-Birsinghpur#1 | 100% | 124 | 400/220 KV ICT / Bina | 100%
77 | 400kV Damoh-Birsinghpur#2 | 100% | 125 | 400/220 KV ICT # 1 / Pirana | 100%
78 | 400kV Dehgam-Pirana#1 | 100% | 126 | 400/220 KV ICT # 2 / Pirana | 100%
79 | 400kV Dehgam-Pirana#2 | 100% | 127 | 400/220 KV ICT # 3 / Gwalior | 100%
80 | 400kV Mundra - Bhachau # 1 | 100% | 128 | 400/220 KV ICT # 1 / Shujalpur | 100%
81 | 400kV Mundra - Bhachau # 2 | 100% | 129 | 400/220 KV ICT # 1 / Bhachau | 100%
82 | 400kV Bhachau - Ranchodpura # 1 | 100% | 130 | 400/220 KV ICT # 2 / Bhachau | 100%
83 | 400kV Bhachau - Ranchodpura # 2 | 100% | 131 | 400/220 KV ICT # 2 / Shujalpur | 100%
84 | 400kV Mundra - Limbdi # 1 | 100% | 132 | 765/400KV ICT# 1 / Satna | 100%
85 | 400kV Mundra - Limbdi # 2 | 99.97% | 133 | 400/220 KV ICT # 2 / Navsari | 99.55%
86 | 765kV Satna - Bina # 1 | 100% | 134 | 400/220 KV ICT # 1 / Navsari | 99.03%
87 | 765kV Satna - Bina # 2 | 100% | 135 | 765/400KV ICT# 2 / Satna | 100%
88 | 765kV Bina - Indore | 100% | 136 | 765/400KV ICT# 1 / Bina | 100%
89 | 400kV Gandhar - Navsari # 2 | 100% | 137 | 400kV ICT#3/Vapi | 100%
90 | 400kV Gandhar - Navsari # 1 | 100% | 138 | 765/400KV ICT# 2 / Bina | 100%
91 | 400kV Mundra-Jetpur#1 | 97.43% | 139 | 765/400KV ICT# 1 / Gwalior | 100%
92 | 400kV Mundra-Jetpur#2 | 100% | 140 | 765/400KV ICT# 2 / Gwalior | 100%
93 | 400kV V'chal (NTPC) - V'chal (PG) #1 | 100% | 141 | 765/400KV ICT# 2 / INDORE | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #2 | 100% | 142 | Bus reactor / Dehgam | 100%
95 | 400kV V'chal (Pooling) - Sasan #1 | 100% | 143 | 25 MVAR reactor # 1 / Jabalpur | 100%
96 | 400k V'chal (Pooling) - Sasan # 2 | 100% | 144 | 25 MVAR reactor # 2 / Jabalpur | 100%
97 | 765kV Sasan - Satna # 1 | 100% | 145 | Bus reactor # 1 / Itarsi | 100%
98 | 400kV Bina (PG)-Bina (MPPTCL)#3 | 100% | 146 | Bus reactor # 2 / Itarsi | 100%
99 | 400kV Vapi-Navsari#1 | 100% | 147 | Bus Reactor # 3 / Itarsi | 100%
100 | 400kV Vapi-Navsari#2 | 100% | 148 | Bus Reactor # 3 / Jabalpur | 100%
101 | 765kV Sasan - Satna # 2 | 100% | 149 | Bus Reactor / Dhule | 100%
102 | 400kV Bina (PG)-Bina (MPPTCL)#4 | 100% | 150 | Bus Reactor-I (50 MVAR) / Satna | 100%
103 | 400kV Indore (MP)-Indore (PG)#1 | 100% | 151 | Bus Reactor # 1 / Bina | 100%
104 | 400kV Indore (MP)-Indore (PG)#2 | 100% | 152 | Bus Reactor / Damoh | 100%
105 | 765 kV Gwalior -Agra # 1 | 100% | 153 | Bus Reactor / Gwalior | 100%
106 | 765 kV Gwalior -Agra # 2 | 100% | 154 | Bus Reactor / Khandwa | 100%
107 | 400/220kV ICT # 1 / Jabalpur. | 100% | 155 | Bus Reactor / Dehgam | 100%
108 | 400/220kV ICT # 2 /Jabalpur. | 100% | 156 | Bus Reactor / Bhachau | 100%
109 | 400/220 KV ICT # 1 / Dehgam | 100% | 157 | Bus Reactor / Shujalpur | 100%
110 | 400/220 KV ICT # 2/ Dehgam | 100% | 158 | Bus Reactor/ Rajgarh | 100%
111 | 400/220kV ICT # 1 / Satna | 100% | 159 | Bus Reactor / Satna 765KV | 100%
112 | 400/220kV ICT # 2 / Satna | 100% | 160 | Bus Reactor / Navsari | 100%
113 | 400/220kV ICT # 1 / Khandwa | 100% | 161 | Switchable Bina-I Line Reactor / Satna 765KV | 100%
114 | 400/220kV ICT # 2 / Khandwa | 99.92% | 162 | Switchable Bina-II Line Reactor / Satna 765KV | 100%
115 | 400/220kV ICT # 1 / Vapi | 100% | 163 | Bus Reactor-II (63 MVAR)/Satna | 100%
116 | 400/220kV ICT # 2 / Vapi | 100% | 164 | Switchable Bina-I Line Reactor / Gwalior 765KV | 100%
117 | 400/220kV ICT # 1 / Gwalior | 100% | 165 | Switchable Bina-II Line Reactor / Gwalior 765KV | 100%
118 | 400/220 KV ICT # 1 / Rajgarh | 100% | 166 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV | 100%
119 | 400/220kV ICT # 2 / Gwalior | 100% | 167 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV | 100%
120 | 400/220kV ICT # 1 / Itarsi | 100%
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
Availability Bus Reactors =
System Availability :-
Note on B23: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B24: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B25: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B83: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B84: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## INDEX
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR JULY-2013
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 0 | 100 | 100% | 90%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 0 | 100 | 100% | 90%
3 | 400kV Itarsi-Indore # 2 | 3 | 19 |  |  | 3.3167 | 0 | 744 | 214 | 2 | 1419.5333 | 428 | 318432 | 0.0044579 | 99.5542 | 99.55% | 90%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 0 | 100 | 100% | 90%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 0 | 100 | 100% | 90%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 0 | 100 | 100% | 90%
7 | 400 KV V'chal - Jabalpur # 2 |  |  | 0 | 43 | 0 | 0.71667 | 743.2833 | 360 | 2 | 0 | 720 | 535164 | 0 | 100 | 100% | 90%
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100% | 90%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100% | 90%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100% | 90%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100% | 90%
12 | 400 KV Jabalpur-Sasan |  |  |  |  | 0 | 0 | 744 | 376 | 2 | 0 | 752 | 559488 | 0 | 100 | 100% | 90%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 744 | 21 | 2 | 0 | 42 | 31248 | 0 | 100 | 100% | 90%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 0 | 100 | 100% | 90%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 0 | 100 | 100% | 90%
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 0 | 100 | 100% | 90%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100% | 90%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100% | 90%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100% | 90%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100% | 90%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 0 | 100 | 100% | 90%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 110 | 2 | 0 | 220 | 163680 | 0 | 100 | 100% | 90%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 0 | 100 | 100% | 90%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100% | 90%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100% | 90%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 0 | 100 | 100% | 90%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  | 1 | 0 | 0 | 1 | 743 | 58.149 | 1 | 0 | 58.149 | 43204.707 | 0 | 100 | 100% | 90%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 744 | 31.334 | 1 | 0 | 31.334 | 23312.496 | 0 | 100 | 100% | 90%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 |  |  |  |  | 0 | 0 | 744 | 31.334 | 1 | 0 | 31.334 | 23312.496 | 0 | 100 | 100% | 90%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100% | 90%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100% | 90%
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 0 | 100 | 100% | 90%
33 | 220kV Kawas-Haldarwa # 2 | 4 | 45 |  |  | 4.75 | 0 | 744 | 81 | 1 | 384.75 | 81 | 60264 | 0.0063844 | 99.3616 | 99.36% | 90%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 0 | 100 | 100% | 90%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 0 | 100 | 100% | 90%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100% | 90%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100% | 90%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100% | 90%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100% | 90%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100% | 90%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100% | 90%
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 0 | 100 | 100% | 90%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 744 | 100.32 | 2 | 0 | 200.64 | 149276.16 | 0 | 100 | 100% | 90%
44 | 400kV Nigrie-Satna |  |  |  |  | 0 | 0 | 744 | 161.11 | 2 | 0 | 322.22 | 239731.68 | 0 | 100 | 100% | 90%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100% | 90%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100% | 90%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100% | 90%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100% | 90%
49 | 765 kV Gwalior-Bina # 1 |  |  |  |  | 0 | 0 | 744 | 234.931 | 4 | 0 | 939.724 | 699154.656 | 0 | 100 | 100% | 90%
50 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 0 | 100 | 100% | 90%
51 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 0 | 100 | 100% | 90%
52 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100% | 90%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100% | 90%
54 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100% | 90%
55 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100% | 90%
56 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 0 | 100 | 100% | 90%
57 | 400KV Nagda - Dehgam # 1 | 6 | 54 |  |  | 6.9 | 0 | 744 | 331.442 | 2 | 4573.8996 | 662.884 | 493185.696 | 0.0092742 | 99.0726 | 99.07% | 90%
58 | 400KV Seoni - Khandwa # 1 |  |  | 11 | 21 | 0 | 11.35 | 732.65 | 351.729 | 4 | 0 | 1406.916 | 1030777.0074 | 0 | 100 | 100% | 90%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504 | 0 | 100 | 100% | 90%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100% | 90%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88 | 0 | 100 | 100% | 90%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88 | 0 | 100 | 100% | 90%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100% | 90%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100% | 90%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100% | 90%
66 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100% | 90%
67 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100% | 90%
68 | 220 KV Vapi - Karadpada # 1 | 4 | 6 |  |  | 4.1 | 0 | 744 | 29.66 | 1 | 121.606 | 29.66 | 22067.04 | 0.0055108 | 99.4489 | 99.45% | 90%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 0 | 100 | 100% | 90%
70 | 765 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352 | 0 | 100 | 100% | 90%
71 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 0 | 100 | 100% | 90%
72 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 0 | 100 | 100% | 90%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 0 | 100 | 100% | 90%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 0 | 100 | 100% | 90%
75 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 0 | 100 | 100% | 90%
76 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100% | 90%
77 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100% | 90%
78 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 0 | 100 | 100% | 90%
79 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 0 | 100 | 100% | 90%
80 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100% | 90%
81 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100% | 90%
82 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100% | 90%
83 | 400kV Bhachau - Ranchodpura # 2 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100% | 90%
84 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 0 | 100 | 100% | 90%
85 | 400kV Mundra - Limbdi # 2 | 0 | 15 | 0 | 35 | 0.25 | 0.58333 | 743.4167 | 314.053 | 3 | 235.5397 | 942.159 | 700416.7033 | 0.00033629 | 99.9664 | 99.97% | 90%
86 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 0 | 100 | 100% | 90%
87 | 765kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 275.635 | 4 | 0 | 1102.54 | 820289.76 | 0 | 100 | 100% | 90%
88 | 765kV Bina - Indore |  |  | 22 | 41 | 0 | 22.6833 | 721.3167 | 311 | 4 | 0 | 1244 | 897317.9333 | 0 | 100 | 100% | 90%
89 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100% | 90%
90 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100% | 90%
91 | 400kV Mundra-Jetpur#1 | 18 | 50 | 11 | 58 | 18.8333 | 11.9667 | 732.0333 | 337 | 3 | 19040.5 | 1011 | 740085.7 | 0.025727 | 97.4273 | 97.43% | 90%
92 | 400kV Mundra-Jetpur#2 |  |  | 13 | 32 | 0 | 13.5333 | 730.4667 | 337 | 3 | 0 | 1011 | 738501.8 | 0 | 100 | 100% | 90%
93 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100% | 90%
94 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100% | 90%
95 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100% | 90%
96 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100% | 90%
97 | 765kV Sasan - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 245.7 | 4 | 0 | 982.8 | 731203.2 | 0 | 100 | 100% | 90%
98 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100% | 90%
99 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 744 | 116.85 | 2 | 0 | 233.7 | 173872.8 | 0 | 100 | 100% | 90%
100 | 400kV Vapi-Navsari#2 |  |  |  |  | 0 | 0 | 744 | 116.85 | 2 | 0 | 233.7 | 173872.8 | 0 | 100 | 100% | 90%
101 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 245.7 | 4 | 0 | 982.8 | 731203.2 | 0 | 100 | 100% | 90%
102 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100% | 90%
103 | 400kV Indore (MP)-Indore (PG)#1 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100% | 90%
104 | 400kV Indore (MP)-Indore (PG)#2 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100% | 90%
| Total Sr.No. 1 to 104 | 35 | 189 | 58 | 230 |  |  |  | 16433.683 |  | 25775.8287 |  | 29542859.019
* | Lines charged with 400kV level
|  | 38.15 |  | 61.8333
[10 empty] | NAFM | 0.00087249
Availability of ( Sl no 1 to 104) transmission lines during JULY-2013 = | [9 empty] | TAFM | 99.9128
105 | 765 kV Gwalior -Agra # 1 |  |  | 0 | 0 | 0 | 0 | 744 | 129.435 | 4 | 0 | 517.74 | 385198.56 | 0 | 100 | 100% | 90%
106 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 0 | 100 | 100% | 90%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
107 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
108 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
109 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
110 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
111 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
112 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
113 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
114 | 400/220kV ICT # 2 / Khandwa | 0 | 34 |  |  | 0.56667 | 0 | 744 | 315 | 2.5 | 446.25 | 787.5 | 585900 | 0.00076165 | 99.9238 | 99.92% | 90%
115 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
116 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
117 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
118 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
119 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
120 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
121 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
122 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
123 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
124 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
125 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
126 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
127 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
128 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
129 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
130 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
131 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
132 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
133 | 400/220 KV ICT # 2 / Navsari | 3 | 23 |  |  | 3.3833 | 0 | 744 | 315 | 2.5 | 2664.375 | 787.5 | 585900 | 0.0045475 | 99.5453 | 99.55% | 90%
134 | 400/220 KV ICT # 1 / Navsari | 7 | 13 |  |  | 7.2167 | 0 | 744 | 315 | 2.5 | 5683.125 | 787.5 | 585900 | 0.0096998 | 99.03 | 99.03% | 90%
135 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
136 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
137 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
138 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
139 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
140 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
141 | 765/400KV ICT# 2 / INDORE |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
| Total Sr.No. 1 to 35 | 10 | 70 | 0 | 0 |  |  |  | 17320 |  | 8793.75 |  | 32215200
|  | 11.1667 |  | 0 | [5 empty] | NAFM | 0.00027297
Availability of 35 ( Sl no 1 to 35) ICTs in JULY-2013 = | [9 empty] | TAFM | 99.9727
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
142 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
143 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100% | 90%
144 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100% | 90%
145 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
146 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
147 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
148 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
149 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 0 | 100 | 100% | 90%
150 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
151 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
152 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
153 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
154 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
155 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
156 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
157 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
158 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
159 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
160 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
161 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
162 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
163 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
164 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
165 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
166 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
167 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
| Total of sl no 1 to 26 | 0 | 0 | 0 | 0 |  |  |  | 2585 |  | 0 |  | 7692960
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 26 ( Sl no 1 to 26) Bus Reactors in JULY-2013 = | [7 empty] | TAFM | 100
[11 empty] | 34569.5787 |  | 69451019.019
[8 empty] | NAFM = | 0.00049775
% System Availability for JULY-2013 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9502
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B135: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B136: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## July'13 Trippind details
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF JULY'2013
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | OUTAGE HOURS ATTRIBUTED TO | [11 empty] | Outage Category | Details | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM E | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
[7 empty] | ATTRIBUTED TO PGCIL |  |  | OTHERS |  |  | SYSTEM CONSTR. |  |  | OUTAGE DEEMED AVAILABLE |  |  |  |  | TRIPPING | CHARGING
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  |  |  |  | A | B | C | D=A*B*C | 744 | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 |  | SATPURA-ITARSI 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 79 | 2 | 0 | 0 | 744 | 158 | 117552 | 0 | 100%
2 |  | ITARSI-INDORE I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 207 | 2 | 0 | 0 | 744 | 414 | 308016 | 0 | 100%
3 | 907129 | ITARSI-INDORE II 400kV | 2013-07-26 | 14:16 | 2013-07-26 | 17:35 | 0.13819 | 3 | 18 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail S/D by POWERGRID for retrofitting of Auto reclose relay at Indore(MPPTCL) end. PTW returned by POWERGRID by 17:35hrs. | LD 07/1857
| 907130 | ITARSI-INDORE II 400kV | 2013-07-26 | 17:35 | 2013-07-26 | 18:25 | - |  |  | - |  |  | - |  |  | 0.034722 | 0 | 49 | LVRD | After Returning of PTW by POWERGRID by 17:35hrs, line charging was delayed by MPPTCL due to persisting high voltage at Indore end. |  | LD 07/1876
|  | SUBTOTAL |  |  |  |  | 0.13819 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034722 | 0 | 49
|  | Element Availability= | [6 empty] | 3.3 |  |  | 0 |  |  | 0 |  |  | 0.81667 |  |  |  |  | 214 | 2 | 3.3 | 1412.4 | 744 | 428 | 318432 | 0.0044355 | 99.56%
4 | 907027 | INDORE-ASOJ I 400kV | 2013-07-06 | 00:37 | 2013-07-06 | 17:42 | - |  |  | - |  |  | - |  |  | 0.71181 | 17 | 5 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/348 | LD 07/397
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71181 | 17 | 5
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 17.0833 |  |  |  |  | 289 | 2 | 0 | 0 | 744 | 578 | 430032 | 0 | 100%
5 | 907027 | INDORE-ASOJ II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 273 | 2 | 0 | 0 | 744 | 546 | 406224 | 0 | 100%
6 | 907106 | VINDHYACHAL-JABALPUR I 400kV | 2013-07-22 | 09:58 | 2013-07-22 | 09:58 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on R-ph to E/F during Heavy rain & Lighting in that area. F/L - 269.3kms from JBP & 146.1km form V'chal .
|  | SUBTOTAL |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 360 | 2 | 0 | 0 | 744 | 720 | 535680 | 0 | 100%
7 | 907091 | VINDHYACHAL-JABALPUR II 400kV | 2013-07-19 | 18:21 | 2013-07-19 | 19:04 | 0 |  |  | 0.029861 | 0 | 43 | - |  |  | - |  |  | LART | Line tripped on R phase to E/F. Three phase tripping took place due to receipt of DT from V'chal end during dead time. As such outage is not aatributable to POWERGRID (LF 207 Km from Jabalpur) |  | LD 07/1362
| 907107 | VINDHYACHAL-JABALPUR II 400kV | 2013-07-22 | 09:58 | 2013-07-22 | 09:58 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on R-ph to E/F during Heavy rain & Lighting in that area. F/L - 238.3kms from JBP & 145.1km form V'chal .
| 907131 | VINDHYACHAL-JABALPUR II 400kV | 2013-07-26 | 18:43 | 2013-07-26 | 18:43 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully on B-ph to E/F during Heavy rains and thunder strome in that area. F/L-147.4 Km from JBP and 218.9 Km from V'chal.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.029861 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.71667 |  |  | 0 |  |  | 0 |  |  |  |  | 360 | 2 | 0 | 0 | 743.2833 | 720 | 535164 | 0 | 100%
8 | 907028 | JABALPUR-ITARSI I 400kV | 2013-07-06 | 01:02 | 2013-07-09 | 08:58 | - |  |  | - |  |  | - |  |  | 1900-01-02 07:56 | 79 | 56 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/350 | LD 07/537
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-02 07:56 | 79 | 56
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 79.9333 |  |  |  |  | 232 | 2 | 0 | 0 | 744 | 464 | 345216 | 0 | 100%
9 | 907053 | JABALPUR-ITARSI II 400kV | 2013-07-12 | 04:02 | 2013-07-24 | 20:48 | - |  |  | - |  |  | - |  |  | 1900-01-11 16:46 | 304 | 45 | LVRD | Line A/T on operation of O/V stage I at JBP and kept out on voltage regulation . | LD 07/766 | LD 07/1704
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-11 16:46 | 304 | 45
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 304.75 |  |  |  |  | 232 | 2 | 0 | 0 | 744 | 464 | 345216 | 0 | 100%
10 |  | GANDHAR-DEHGAM I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 744 | 314 | 233616 | 0 | 100%
11 |  | GANDHAR-DEHGAM II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 744 | 314 | 233616 | 0 | 100%
12 |  | 'SASAN (RELIANCE) - JABALPUR 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 376 | 2 | 0 | 0 | 744 | 752 | 559488 | 0 | 100%
13 | 906079 | 400kV Sasan-Vindhyachal |  |  |  |  | - |  |  | - |  |  | - |  |  | - | [5 empty] | LD 06/1129
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21 | 2 | 0 | 0 | 744 | 42 | 31248 | 0 | 100%
14 | 907104 | VINDHYACHAL-JABALPUR IV 400kV | 2013-07-22 | 00:43 | 2013-07-22 | 00:43 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on B-ph to E/F during Heavy rain & Lighting in that area. F/L - 328.9kms from JBP & 51.5km form V'chal.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 389 | 2 | 0 | 0 | 744 | 778 | 578832 | 0 | 100%
15 | 907041 | JABALPUR-ITARSI III 400kV | 2013-07-09 | 09:35 | 2013-07-11 | 18:49 | - |  |  | - |  |  | - |  |  | 1900-01-01 09:14 | 57 | 14 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/542 | LD 07/746
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 09:14 | 57 | 14
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 57.2333 |  |  |  |  | 234 | 2 | 0 | 0 | 744 | 468 | 348192 | 0 | 100%
16 | 906132 | JABALPUR-ITARSI IV 400kV | 2013-06-22 | 21:40 | 2013-07-02 | 10:16 | - |  |  | - |  |  | - |  |  | 1899-12-31 10:16 | 34 | 16 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 06/1905 | LD 07/87
| 907115 | JABALPUR-ITARSI IV 400kV | 2013-07-24 | 22:24 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-06 01:36 | 169 | 36 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1711
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-07 11:52 | 203 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 203.8667 |  |  |  |  | 234 | 2 | 0 | 0 | 744 | 468 | 348192 | 0 | 100%
17 | 907010 | ITARSI-KHANDWA I 400kV | 2013-07-03 | 13:15 | 11-07-13 | 12:21 | - |  |  | - |  |  | - |  |  | 1900-01-06 23:06 | 191 | 5 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/152 | LD 07/716
| 907121 | ITARSI-KHANDWA I 400kV | 2013-07-25 | 16:26 | 2013-07-31 | 10:56 | - |  |  | - |  |  | - |  |  | 1900-01-04 18:30 | 138 | 30 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1777 | LD 07/2189
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-12 17:36 | 329 | 35
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 329.5833 |  |  |  |  | 196.64 | 2 | 0 | 0 | 744 | 393.28 | 292600.32 | 0 | 100%
18 | 906044 | ITARSI-KHANDWA II 400kV | 2013-06-06 | 21:22 | 2013-07-01 | 10:41 | - |  |  | - |  |  | - |  |  | 0.44514 | 10 | 41 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 06/533 | LD 07/25
| 907047 | ITARSI-KHANDWA II 400kV | 2013-07-11 | 13:08 | 2013-07-25 | 10:13 | - |  |  | - |  |  | - |  |  | 1900-01-12 21:05 | 333 | 5 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/724 | LD 07/1739
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-13 07:46 | 343 | 46
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 343.7667 |  |  |  |  | 196.64 | 2 | 0 | 0 | 744 | 393.28 | 292600.32 | 0 | 100%
19 |  | KHANDWA-DHULE I 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 261.78 | 2 | 0 | 0 | 744 | 523.56 | 389528.64 | 0 | 100%
20 |  | KHANDWA-DHULE II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 261.78 | 2 | 0 | 0 | 744 | 523.56 | 389528.64 | 0 | 100%
21 |  | JHANOR - SUGEN 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 57 | 2 | 0 | 0 | 744 | 114 | 84816 | 0 | 100%
22 | 907100 | SUGEN-VAPI 400kV | 2013-07-21 | 03:32 | 2013-07-21 | 03:32 | 0 | 0 | 0 | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on B-ph to E/F, F/L - 66.4kms from Vapi & 54kms from Sugene
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 110 | 2 | 0 | 0 | 744 | 220 | 163680 | 0 | 100%
23 |  | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 2 | 0 | 0 | 744 | 26 | 19344 | 0 | 100%
24 |  | JHANOR - HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 744 | 13 | 9672 | 0 | 100%
25 |  | JHANOR - HALDARWA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 744 | 13 | 9672 | 0 | 100%
26 | 907073 | KAWAS - NAVSARI I 220KV | 2013-07-17 | 15:00 | 2013-07-17 | 18:06 | - |  |  | - |  |  | - |  |  | 0.12917 | 3 | 5 | LCSD | Line H/T for Remote operation & protection alarm checking of Navsari S/S through Vapi. | LD07/1171 | LD07/1183
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12917 | 3 | 5
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 3.0833 |  |  |  |  | 58.149 | 1 | 0 | 0 | 744 | 58.149 | 43262.856 | 0 | 100%
27 | 907125 | KAWAS-NAVSARI II 220kV | 2013-07-25 | 23:46 | 2013-07-26 | 00:46 | - |  |  | 0.041667 | 1 | 0 | - |  |  | - |  |  | SRMU | Line A/T at Kawas end only on Y-ph to E/F due to suspected relay maloperation at Kawas. F/L- 1 Km from Kawas. |  | LD 07/1821
| 907135 | KAWAS-NAVSARI II 220kV | 2013-07-27 | 10:59 | 2013-07-27 | 14:25 | - |  |  | - |  |  | - |  |  | 0.14306 | 3 | 26 | OSPD | H/T to avail S/D by NTPC Kawas for PLCC testing work. | LD 07/1919 | LD 07/1929
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.041667 | 1 | 0 | 0 | 0 | 0 | 0.14306 | 3 | 26
|  | Element Availability= | [6 empty] | 0 |  |  | 1 |  |  | 0 |  |  | 3.4333 |  |  |  |  | 58.149 | 1 | 0 | 0 | 743 | 58.149 | 43204.707 | 0 | 100%
28 |  | NAVSARI (PG GIS)-NAVSARI I 220kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 31.334 | 1 | 0 | 0 | 744 | 31.334 | 23312.496 | 0 | 100%
29 |  | NAVSARI (PG GIS)-NAVSARI II 220kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 31.334 | 1 | 0 | 0 | 744 | 31.334 | 23312.496 | 0 | 100%
30 | 906131 | KAWAS-VAV I 220kV | 2013-06-22 | 21:33 | 2013-07-06 | 18:47 | - |  |  | - |  |  | - |  |  | 1900-01-04 18:47 | 138 | 47 | LPRD | Line H/T for power regulation on WRLDC Instruction | LD 06/1906 | LD 07/401
| 907034 | KAWAS-VAV I 220kV | 2013-07-07 | 22:08 | 2013-07-13 | 18:36 | - |  |  | - |  |  | - |  |  | 1900-01-04 20:28 | 140 | 28 | LPRD | Line H/T for Power Regulation On WRLDC Instruction | LD 07/457 | LD 07/937
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-10 15:15 | 278 | 75
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 279.25 |  |  |  |  | 37 | 1 | 0 | 0 | 744 | 37 | 27528 | 0 | 100%
31 | 907048 | KAWAS-VAV II 220kV | 2013-07-11 | 14:52 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-19 09:08 | 489 | 8 | LPRD | Line H/T for power regulation ON WRLDC Instruction | LD 07/732
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-19 09:08 | 489 | 8
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 489.1333 |  |  |  |  | 37 | 1 | 0 | 0 | 744 | 37 | 27528 | 0 | 100%
32 |  | KAWAS-HALDARWA I 220kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 81 | 1 | 0 | 0 | 744 | 81 | 60264 | 0 | 100%
33 | 907113 | KAWAS-HALDARWA II 220kV | 2013-07-24 | 17:37 | 2013-07-25 | 10:45 | 0.19792 | 4 | 45 | - |  |  | - |  |  | 0.51597 | 12 | 23 | LHWT | Line A/T on R-ph to E/F due to Insulator string flashover at Loc no 118. Patrolling could not be carried out due to poor visibility during heavy rains and inaccessable location. Hence outage from 24.07.2013/17:37 hrs to 25.07.2013/06:00 Hrs may not be attributable to POWERGRID (F/L - 41.8kms from Haldarwa). |  | LD 07/1741
|  | SUBTOTAL |  |  |  |  | 0.19792 | 4 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51597 | 12 | 23
|  | Element Availability= | [6 empty] | 4.75 |  |  | 0 |  |  | 0 |  |  | 12.3833 |  |  |  |  | 81 | 1 | 4.75 | 384.75 | 744 | 81 | 60264 | 0.0063844 | 99.36%
34 |  | KAKRAPAR-HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 0 | 0 | 744 | 74 | 55056 | 0 | 100%
35 |  | KAKRAPAR-HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 0 | 0 | 744 | 74 | 55056 | 0 | 100%
36 |  | KAKRAPAR-VAV I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 43 | 1 | 0 | 0 | 744 | 43 | 31992 | 0 | 100%
37 |  | KAKRAPAR-VAV II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 43 | 1 | 0 | 0 | 744 | 43 | 31992 | 0 | 100%
38 |  | KAKRAPAR-VAPI I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 117 | 1 | 0 | 0 | 744 | 117 | 87048 | 0 | 100%
39 |  | KAKRAPAR-VAPI II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 117 | 1 | 0 | 0 | 744 | 117 | 87048 | 0 | 100%
40 |  | VINDHYACHAL-SATNA I 400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 744 | 534 | 397296 | 0 | 100%
41 | 907095 | VINDHYACHAL-SATNA II 400KV | 2013-07-20 | 16:36 | 2013-07-20 | 16:36 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R succeccfully at both ends on R-ph to E/F during Heavy rain & Lighting in that area. F/L - 51.32kms from Satna & 85% from VSTPP | - | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 744 | 534 | 397296 | 0 | 100%
42 |  | VINDHYACHAL-SATNA III 400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 258.31 | 2 | 0 | 0 | 744 | 516.62 | 384365.28 | 0 | 100%
43 |  | VINDHYACHAL-NIGRIE 400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 100.32 | 2 | 0 | 0 | 744 | 200.64 | 149276.16 | 0 | 100%
44 |  | NIGRIE-SATNA 400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 161.11 | 2 | 0 | 0 | 744 | 322.22 | 239731.68 | 0 | 100%
45 | 907033 | SATNA-BINA(PG ) I 400kV | 2013-07-07 | 15:15 | 2013-07-18 | 18:22 | - |  |  | - |  |  | - |  |  | 1900-01-10 03:07 | 267 | 7 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/442 | LD 07/1273
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-10 03:07 | 267 | 7
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 267.1167 |  |  |  |  | 276 | 2 | 0 | 0 | 744 | 552 | 410688 | 0 | 100%
46 | 906144 | SATNA-BINA(PG ) II 400kV | 2013-06-27 | 01:43 | 2013-07-02 | 12:20 | - |  |  | - |  |  | - |  |  | 1900-01-04 10:37 | 130 | 37 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 06/2151 | LD 07/92
| 907093 | SATNA-BINA(PG ) II 400kV | 2013-07-20 | 09:26 | 2013-07-23 | 12:34 | - |  |  | - |  |  | - |  |  | 1900-01-02 03:08 | 75 | 7 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1402 | LD 07/1619
| 907119 | SATNA-BINA(PG) II 400kV | 2013-07-25 | 12:34 | 2013-07-25 | 21:10 | - |  |  | - |  |  | - |  |  | 0.35833 | 8 | 36 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1757 | LD 07/1803
| 907141 | SATNA-BINA II 400kV | 2013-07-30 | 12:15 | 2013-07-31 | 09:18 | - |  |  | - |  |  | - |  |  | 0.87708 | 21 | 2 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/2128 | LD 07/2178
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 19:24 | 234 | 82
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 235.3667 |  |  |  |  | 276 | 2 | 0 | 0 | 744 | 552 | 410688 | 0 | 100%
47 |  | BINA(PG)-BINA(MPEB) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 744 | 1.484 | 1104.096 | 0 | 100%
48 |  | BINA(PG)-BINA(MPEB) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 744 | 1.484 | 1104.096 | 0 | 100%
49 |  | GWALIOR-BINA I 765KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 234.931 | 4 | 0 | 0 | 744 | 939.724 | 699154.656 | 0 | 100%
50 |  | SATNA-BINA(PG) IV 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 272.586 | 2 | 0 | 0 | 744 | 545.172 | 405607.968 | 0 | 100%
51 | 907007 | SATNA-BINA(PG) III 400kV | 2013-07-02 | 13:44 | 2013-07-04 | 10:52 | - |  |  | - |  |  | - |  |  | 1899-12-31 21:08 | 45 | 7 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/96 | LD07/218
| 907124 | SATNA-BINA(PG) III 400kV | 2013-07-25 | 23:03 | 2013-07-26 | 00:14 | - |  |  | - |  |  | - |  |  | 0.049306 | 1 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1813 | LD 07/1815
| 907128 | SATNA-BINA(PG) III 400kV | 2013-07-26 | 01:34 | 2013-07-29 | 10:05 | - |  |  | - |  |  | - |  |  | 1900-01-02 08:31 | 80 | 30 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1825 | LD 07/2056
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-04 06:50 | 126 | 48
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 126.8 |  |  |  |  | 272.586 | 2 | 0 | 0 | 744 | 545.172 | 405607.968 | 0 | 100%
52 | 907002 | BINA-SHUJALPUR I 400kV | 2013-07-01 | 01:25 | 2013-07-02 | 12:11 | - |  |  | - |  |  | - |  |  | 1899-12-31 10:46 | 34 | 45 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/02 | LD 07/89
| 907016 | BINA-SHUJALPUR I 400kV | 2013-07-04 | 17:34 | 2013-07-05 | 08:29 | - |  |  | - |  |  | - |  |  | 0.62153 | 14 | 55 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/248 | LD07/287
| 907040 | BINA-SHUJALPUR I 400kV | 2013-07-09 | 00:22 | 2013-07-09 | 10:57 | - |  |  | - |  |  | - |  |  | 0.44097 | 10 | 35 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/517 | LD 07/551
| 907065 | BINA-SHUJALPUR I 400kV | 2013-07-15 | 00:56 | 2013-07-15 | 09:32 | - |  |  | - |  |  | - |  |  | 0.35833 | 8 | 35 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1011 | LD 07/1024
| 907070 | BINA-SHUJALPUR I 400kV | 2013-07-16 | 23:29 | 2013-07-17 | 07:50 | - |  |  | - |  |  | - |  |  | 0.34792 | 8 | 20 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1128 | LD07/1142
| 907079 | BINA-SHUJALPUR I 400kV | 2013-07-17 | 22:09 | 2013-07-18 | 07:36 | - |  |  | - |  |  | - |  |  | 0.39375 | 9 | 26 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1198 | LD 07/1229
| 907085 | BINA-SHUJALPUR I 400 KV | 2013-07-19 | 01:44 | 2013-07-20 | 10:27 | - |  |  | - |  |  | - |  |  | 1899-12-31 08:43 | 32 | 42 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1300 | LD 07/1399
| 907109 | BINA-SHUJALPUR I 400kV | 2013-07-23 | 00:19 | 2013-07-23 | 06:17 | - |  |  | - |  |  | - |  |  | 0.24861 | 5 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1584 | LD07/1594
| 907117 | BINA-SHUJALPUR I 400kV | 2013-07-25 | 01:02 | 2013-07-25 | 12:42 | - |  |  | - |  |  | - |  |  | 0.48611 | 11 | 39 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1718 | LD 07/1751
| 907123 | BINA-SHUJALPUR I 400kV | 2013-07-25 | 22:09 | 2013-07-26 | 08:44 | - |  |  | - |  |  | - |  |  | 0.44097 | 10 | 34 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1809 | LD 07/1833
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-05 03:36 | 141 | 389
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 147.4833 |  |  |  |  | 199.936 | 2 | 0 | 0 | 744 | 399.872 | 297504.768 | 0 | 100%
53 | 907044 | BINA-SHUJALPUR II 400kV | 2013-07-09 | 23:05 | 2013-07-10 | 09:35 | - |  |  | - |  |  | - |  |  | 0.4375 | 10 | 30 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/603 | LD 07/636
| 907098 | BINA-SHUJALPUR II 400kV | 2013-07-21 | 00:02 | 2013-07-22 | 12:26 | - |  |  | - |  |  | - |  |  | 1899-12-31 12:24 | 36 | 24 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1452 | LD 07/1541
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 22:54 | 46 | 54
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 46.9 |  |  |  |  | 199.936 | 2 | 0 | 0 | 744 | 399.872 | 297504.768 | 0 | 100%
54 | 907019 | SHUJALPUR-NAGDA I 400kV | 2013-07-05 | 02:08 | 2013-07-05 | 15:04 | - |  |  | - |  |  | - |  |  | 0.53889 | 12 | 56 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/275 | LD07/319
| 907035 | SHUJALPUR-NAGDA I 400kV | 2013-07-08 | 00:52 | 2013-07-08 | 08:08 | - |  |  | - |  |  | - |  |  | 0.30278 | 7 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/463 | LD 07/473
| 907051 | SHUJALPUR-NAGDA I 400kV | 2013-07-12 | 02:20 | 2013-07-12 | 08:43 | - |  |  | - |  |  | - |  |  | 0.26597 | 6 | 23 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/764
| 907064 | SHUJALPUR-NAGDA I 400kV | 2013-07-15 | 00:52 | 2013-07-17 | 10:03 | - |  |  | - |  |  | - |  |  | 1900-01-01 09:11 | 57 | 10 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1010 | LD 07/1148
| 907086 | SHUJALPUR-NAGDA I 400kV | 2013-07-19 | 03:14 | 2013-07-20 | 11:14 | - |  |  | - |  |  | - |  |  | 1899-12-31 08:00 | 32 | 59 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1302 | LD 07/1414
| 907099 | SHUJALPUR-NAGDA I 400kV | 2013-07-21 | 01:42 | 2013-07-21 | 11:41 | - |  |  | - |  |  | - |  |  | 0.41597 | 9 | 59 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1458 | LD 07/1481
| 907127 | SHUJALPUR-NAGDA I 400kV | 2013-07-26 | 01:31 | 2013-07-30 | 10:20 | - |  |  | - |  |  | - |  |  | 1900-01-03 08:49 | 104 | 48 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1827 | LD 07/2119
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 14:34 | 227 | 270
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 231.5 |  |  |  |  | 152.229 | 2 | 0 | 0 | 744 | 304.458 | 226516.752 | 0 | 100%
55 | 907029 | SHUJALPUR-NAGDA II 400kV | 2013-07-06 | 01:12 | 2013-07-06 | 18:06 | - |  |  | - |  |  | - |  |  | 0.70417 | 16 | 53 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/351 | LD 07/394
| 907045 | SHUJALPUR-NAGDA II 400kV | 2013-07-09 | 02:42 | 2013-07-10 | 07:32 | - |  |  | - |  |  | - |  |  | 1899-12-31 04:50 | 28 | 49 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/619 | LD 07/626
| 907060 | SHUJALPUR-NAGDA II 400kV | 2013-07-14 | 01:46 | 2013-07-14 | 09:11 | - |  |  | - |  |  | - |  |  | 0.30903 | 7 | 25 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/958 | LD07/970
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 05:09 | 51 | 127
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 53.1167 |  |  |  |  | 152.229 | 2 | 0 | 0 | 744 | 304.458 | 226516.752 | 0 | 100%
56 | 907057 | NAGDA-DEHGAM II 400kV | 2013-07-13 | 01:52 | 2013-07-17 | 09:12 | - |  |  | - |  |  | - |  |  | 1900-01-03 07:20 | 103 | 19 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/878 | LD 07/1144
| 907137 | NAGDA-DEHGAM II 400kV | 2013-07-28 | 04:52 | 2013-07-28 | 08:32 | - |  |  | - |  |  | - |  |  | 0.15278 | 3 | 40 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1964 | LD 07/1981
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 11:00 | 106 | 59
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 106.9833 |  |  |  |  | 331.442 | 2 | 0 | 0 | 744 | 662.884 | 493185.696 | 0 | 100%
57 | 907012 | NAGDA-DEHGAM I 400KV | 2013-07-04 | 01:04 | 2013-07-05 | 13:54 | 0.2875 | 6 | 54 | - |  |  | - |  |  | 1899-12-31 05:56 | 29 | 56 | LHWT | Line A/T on Y ph to Earth fault due to Flashover of at loc 641. The patrolling could not be carried out in night hours due to poor visibility. Further, Restoration work get delayed due to Continuous heavy rain and inaccessable location. Hence outage from 01:04 Hrs/04.07.2013 to 07:00 hrs/05.07.2013 may not be attributable to POWERGRID Account(F/L 96.7KM from Dehgam) |  | LD 07/308
| 907031 | NAGDA-DEHGAM I 400KV | 2013-07-07 | 00:48 | 2013-07-09 | 10:44 | - |  |  | - |  |  | - |  |  | 1900-01-01 09:56 | 57 | 56 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/409 | LD 07/552
| 907052 | NAGDA-DEHGAM I 400KV | 2013-07-12 | 03:38 | 2013-07-12 | 08:26 | - |  |  | - |  |  | - |  |  | 0.2 | 4 | 48 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/765
| 907140 | NAGDA-DEHGAM I 400KV | 2013-07-29 | 01:35 | 2013-07-29 | 08:19 | - |  |  | - |  |  | - |  |  | 0.28056 | 6 | 44 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/2033 | LD 07/2049
|  | SUBTOTAL |  |  |  |  | 0.2875 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 03:24 | 96 | 204
|  | Element Availability= | [6 empty] | 6.9 |  |  | 0 |  |  | 0 |  |  | 99.4 |  |  |  |  | 331.442 | 2 | 6.9 | 4573.8996 | 744 | 662.884 | 493185.696 | 0.0092742 | 99.07%
58 | 907015 | SEONI-KHANDWA I 400kV | 2013-07-04 | 03:31 | 2013-07-04 | 10:49 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | 0.29722 | 7 | 8 | GOVC | Line A/T due to Operation of O/V Protection at Khandwa end & subsequently kept out for voltage Regulation on WRLDC instruction | LD 07/206 | LD 07/220
| 907056 | SEONI-KHANDWA I 400kV | 2013-07-13 | 01:02 | 2013-07-13 | 10:08 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | 0.37222 | 8 | 56 | GOVC | Line A/T ON operation of O/V stage I at Khandwa and subsequentaly kept out on Voltage Regulation . | LD 07/874 | LD 07/903
| 907082 | SEONI-KHANDWA I 400kV | 2013-07-18 | 13:00 | 2013-07-18 | 14:12 | - |  |  | - |  |  | 0.05 | 1 | 12 | - |  |  | GOVC | Line A/T on operation of O/V stage I at Khandwa S/S. |  | LD07/1259
| 907089 | SEONI-KHANDWA I 400kV | 2013-07-19 | 13:12 | 2013-07-20 | 09:24 | - |  |  | - |  |  | - |  |  | 0.84167 | 20 | 12 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1334 | LD 07/1398
| 907120 | SEONI-KHANDWA I 400kV | 2013-07-25 | 12:58 | 2013-07-25 | 15:38 | - |  |  | - |  |  | 0.11111 | 2 | 39 | - |  |  | GOVC | Line A/T on operation of O/V stage-I at Khandwa. |  | LD 07/1773
| 907126 | SEONI-KHANDWA I 400kV | 2013-07-26 | 01:05 | 2013-07-26 | 08:14 | - |  |  | - |  |  | 0.29792 | 7 | 8 | - |  |  | GOVC | Line A/T on operation of O/V stage-I at Khandwa. |  | LD 07/1834
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.47292 | 10 | 79 | 1899-12-31 12:16 | 35 | 76
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 11.3167 |  |  | 36.2667 |  |  |  |  | 351.729 | 4 | 0 | 0 | 732.6833 | 1406.916 | 1030823.9046 | 0 | 100%
59 | 907018 | SEONI-KHANDWA II 400kV | 2013-07-05 | 00:47 | 2013-07-05 | 08:35 | - |  |  | - |  |  | - |  |  | 0.325 | 7 | 48 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/270 | LD07/286
| 907030 | SEONI-KHANDWA II 400kV | 2013-07-06 | 01:18 | 2013-07-06 | 10:20 | - |  |  | - |  |  | - |  |  | 0.37639 | 9 | 1 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/352 | LD 07/366
| 907037 | SEONI-KHANDWA II 400kV | 2013-07-08 | 03:34 | 2013-07-08 | 08:17 | - |  |  | - |  |  | - |  |  | 0.19653 | 4 | 43 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/466 | LD 07/476
| 907059 | SEONI-KHANDWA II 400kV | 2013-07-13 | 23:19 | 2013-07-14 | 09:27 | - |  |  | - |  |  | - |  |  | 0.42222 | 10 | 8 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/952 | LD07/969
| 907133 | SEONI-KHANDWA II 400kV | 2013-07-27 | 00:02 | 2013-07-27 | 07:18 | - |  |  | - |  |  | - |  |  | 0.30278 | 7 | 16 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1891 | LD 07/1905
| 907136 | SEONI-KHANDWA II 400kV | 2013-07-27 | 23:53 | 2013-07-28 | 07:39 | - |  |  | - |  |  | - |  |  | 0.32361 | 7 | 45 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1960 | LD 07/1979
| 907138 | SEONI-KHANDWA II 400kV | 2013-07-28 | 15:07 | 2013-07-29 | 09:27 | - |  |  | - |  |  | - |  |  | 0.76389 | 18 | 20 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1999 | LD 07/2055
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 17:03 | 62 | 181
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 65.0167 |  |  |  |  | 351.729 | 4 | 0 | 0 | 744 | 1406.916 | 1046745.504 | 0 | 100%
60 | 906153 | KHANDWA-RAJGARH II 400kV | 2013-06-29 | 02:30 | 2013-07-03 | 06:57 | - |  |  | - |  |  | - |  |  | 1900-01-03 04:27 | 100 | 27 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 06/2287 | LD 07/131
| 907011 | KHANDWA-RAJGARH II 400kV | 2013-07-04 | 00:12 | 2013-07-07 | 09:37 | - |  |  | - |  |  | - |  |  | 1900-01-02 09:25 | 81 | 24 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/180 | LD 07/424
| 907036 | KHANDWA-RAJGARH II 400kV | 2013-07-08 | 01:01 | 2013-07-09 | 07:35 | - |  |  | - |  |  | - |  |  | 1899-12-31 06:34 | 30 | 33 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/464 | LD 07/530
| 907043 | KHANDWA-RAJGARH II 400kV | 2013-07-09 | 18:03 | 2013-07-15 | 10:10 | - |  |  | - |  |  | - |  |  | 1900-01-04 16:07 | 136 | 6 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/583 | LD 07/1031
| 907068 | KHANDWA-RAJGARH II 400kV | 2013-07-16 | 04:02 | 2013-07-16 | 07:48 | - |  |  | - |  |  | - |  |  | 0.15694 | 3 | 45 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1075 | LD 07/1084
| 907069 | KHANDWA-RAJGARH II 400kV | 2013-07-16 | 23:25 | 2013-07-17 | 07:31 | - |  |  | - |  |  | - |  |  | 0.3375 | 8 | 6 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1126 | LD07/1141
| 907075 | KHANDWA-RAJGARH II 400kV | 2013-07-17 | 17:03 | 2013-07-18 | 06:50 | - |  |  | - |  |  | - |  |  | 0.57431 | 13 | 46 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1182 | LD 07/1228
| 907083 | KHANDWA-RAJGARH II 400kV | 2013-07-18 | 14:04 | 2013-07-24 | 10:05 | - |  |  | - |  |  | - |  |  | 1900-01-04 20:01 | 140 | 1 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1257 | LD 07/1670
| 907114 | KHANDWA-RAJGARH II 400kV | 2013-07-24 | 22:19 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-06 01:41 | 169 | 41 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1709
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-27 11:54 | 680 | 229
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 683.8167 |  |  |  |  | 220.588 | 2 | 0 | 0 | 744 | 441.176 | 328234.944 | 0 | 100%
61 | 907014 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-07-04 | 03:09 | 2013-07-08 | 09:08 | - |  |  | - |  |  | - |  |  | 1900-01-03 05:59 | 101 | 59 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/190 | LD 07/477
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 05:59 | 101 | 59
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 101.9833 |  |  |  |  | 4.01 | 2 | 0 | 0 | 744 | 8.02 | 5966.88 | 0 | 100%
62 | 907038 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-07-08 | 09:32 | 2013-07-13 | 01:51 | - |  |  | - |  |  | - |  |  | 1900-01-03 16:19 | 112 | 18 | OSPD | H/T to avail S/D by MPPTCL | LD 07/479 | LD 07/877
| 907058 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-07-13 | 01:55 | 2013-07-13 | 01:55 | - |  |  | 0 | 0 | 0 | - |  |  | - |  |  | OMSU | Line A/R successfully at both ends on B-ph to E/F, F/L -42kms from Rajgarh. Fault was in MPPTCL zone.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 16:19 | 112 | 18
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 112.3 |  |  |  |  | 4.01 | 2 | 0 | 0 | 744 | 8.02 | 5966.88 | 0 | 100%
63 |  | RAJGARH-NAGDA I 400kV (LILO)
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 4.12 | 2 | 0 | 0 | 744 | 8.24 | 6130.56 | 0 | 100%
64 | 906138 | RAJGARH-NAGDA II 400kV (LILO) | 2013-06-24 | 11:31 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-30 | 744 | 0 | OSPD | Line H/T to avail shut down by MPPTCL. | LD06/2003
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-30 | 744 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 744 |  |  |  |  | 4.12 | 2 | 0 | 0 | 744 | 8.24 | 6130.56 | 0 | 100%
65 | 906143 | KHANDWA-RAJGARH I 400kV | 2013-06-26 | 01:54 | 2013-07-02 | 10:09 | - |  |  | - |  |  | - |  |  | 1900-01-05 08:15 | 152 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 06/2099 | LD 07/88
| 907009 | KHANDWA-RAJGARH I 400kV | 2013-07-02 | 22:14 | 2013-07-04 | 08:24 | - |  |  | - |  |  | - |  |  | 1899-12-31 10:10 | 34 | 9 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/118 | LD 07/209
| 907017 | KHANDWA-RAJGARH I 400kV | 2013-07-04 | 23:05 | 2013-07-08 | 07:38 | - |  |  | - |  |  | - |  |  | 1900-01-02 08:33 | 80 | 33 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/264 | LD 07/474
| 907039 | KHANDWA-RAJGARH I 400kV | 2013-07-09 | 00:15 | 2013-07-10 | 07:36 | - |  |  | - |  |  | - |  |  | 1899-12-31 07:21 | 31 | 21 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/518 | LD 07/627
| 907049 | KHANDWA-RAJGARH I 400kV | 2013-07-11 | 23:03 | 2013-07-12 | 06:12 | - |  |  | - |  |  | - |  |  | 0.29792 | 7 | 8 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/759 | LD 07/771
| 907055 | KHANDWA-RAJGARH I 400kV | 2013-07-12 | 22:48 | 2013-07-17 | 09:49 | - |  |  | - |  |  | - |  |  | 1900-01-03 11:01 | 107 | 1 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/870 | LD 07/1150
| 907078 | KHANDWA-RAJGARH I 400kV | 2013-07-17 | 22:03 | 2013-07-19 | 10:49 | - |  |  | - |  |  | - |  |  | 1899-12-31 12:46 | 36 | 46 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1199 | LD 07/1322
| 907092 | KHANDWA-RAJGARH I 400kV | 2013-07-19 | 23:39 | 2013-07-20 | 19:51 | - |  |  | - |  |  | - |  |  | 0.84167 | 20 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1377 | LD 07/1440
| 907096 | KHANDWA-RAJGARH I 400kV | 2013-07-20 | 23:21 | 2013-07-22 | 11:41 | - |  |  | - |  |  | - |  |  | 1899-12-31 12:20 | 36 | 20 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1451 | LD 07/1542
| 907108 | KHANDWA-RAJGARH I 400kV | 2013-07-22 | 12:17 | 2013-07-28 | 20:17 | - |  |  | - |  |  | - |  |  | 1900-01-05 08:00 | 152 | 59 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1548 | LD 07/2016
| 907139 | KHANDWA-RAJGARH I 400kV | 2013-07-29 | 01:23 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-01 22:37 | 70 | 37 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/2034
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-29 08:24 | 725 | 260
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 729.3333 |  |  |  |  | 220.588 | 2 | 0 | 0 | 744 | 441.176 | 328234.944 | 0 | 100%
66 |  | VAPI-MAGARWADA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 744 | 25.71 | 19128.24 | 0 | 100%
67 |  | VAPI-MAGARWADA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 744 | 25.71 | 19128.24 | 0 | 100%
68 | 907090 | VAPI-KHARADPARA I 220kV | 2013-07-19 | 16:34 | 2013-07-19 | 20:40 | 0.17083 | 4 | 5 | - |  |  | - |  |  | - |  |  | OMST | H/T to avail for rectification of snapped Jumper between Gantry and CT at Vapi S/S. | LD 07/1349 | LD 07/1369
|  | SUBTOTAL |  |  |  |  | 0.17083 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 4.0833 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 4.0833 | 121.1117 | 744 | 29.66 | 22067.04 | 0.0054884 | 99.45%
69 |  | VAPI-KHARADPARA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 744 | 29.66 | 22067.04 | 0 | 100%
70 |  | GWALIOR-BINA II 765KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 233.652 | 4 | 0 | 0 | 744 | 934.608 | 695348.352 | 0 | 100%
71 |  | SEONI-BINA 765KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 292.45 | 4 | 0 | 0 | 744 | 1169.8 | 870331.2 | 0 | 100%
72 | 906098 | DAMOH-BHOPAL I 400KV | 2013-06-15 | 13:24 | 2013-07-02 | 19:38 | - |  |  | - |  |  | - |  |  | 1900-01-16 06:14 | 414 | 14 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 06/1329 | LD 07/ 100
| 907116 | DAMOH-BHOPAL I 400KV | 2013-07-25 | 00:51 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-05 23:09 | 167 | 9 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1716
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-23 05:23 | 581 | 23
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 581.3833 |  |  |  |  | 241.471 | 2 | 0 | 0 | 744 | 482.942 | 359308.848 | 0 | 100%
73 | 907008 | DAMOH-BHOPAL II 400KV | 2013-07-02 | 20:11 | 2013-07-11 | 10:21 | - |  |  | - |  |  | - |  |  | 1900-01-07 14:10 | 206 | 10 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/112 | LD 07/708
| 907072 | DAMOH-BHOPAL II 400KV | 2013-07-17 | 14:34 | 2013-07-17 | 14:34 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on B-ph to E/F, F/L - 116 kms from Damoh & 105.44 kms from Bhopal.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-07 14:10 | 206 | 10
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 206.1667 |  |  |  |  | 213.8 | 2 | 0 | 0 | 744 | 427.6 | 318134.4 | 0 | 100%
74 | 907076 | VAPI-KHADOLI I 220kV | 2013-07-17 | 21:46 | 2013-07-18 | 00:33 | - |  |  | 0.11597 | 2 | 46 | - |  |  | - |  |  | SBBU | Line A/T due to operation Bus Bar Protection due to auto closing of faulty Earth Switch at Sayali. |  | LD07/1207
75 | 907077 | VAPI-KHADOLI I 220kV | 2013-07-17 | 21:46 | 2013-07-18 | 00:05 | - |  |  | 0.096528 | 2 | 18 | - |  |  | - |  |  | SBBU | Line A/T due to operation Bus Bar Protection due to auto closing of faulty Earth Switch At Sayali. The line charged by Sayali without taking any Charging Code from WRLDC.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.2125 | 4 | 64 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 5.0667 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 738.9333 | 25.71 | 18997.976 | 0 | 100%
76 | 907067 | VAPI-KHADOLI II 220kV | 2013-07-15 | 13:28 | 2013-07-17 | 14:39 | - |  |  | - |  |  | - |  |  | 1900-01-01 01:11 | 49 | 11 | OSPD | Line H/T to avail S/D by DNH for LILO work. After LILO at Sayali (DNH) Vapi - Sayali section charged at 14:39hrs/17.07.13 & Sayali - Khadoli section charged at 12:47hrs/17.07.13 | LD07/1041 | LD 07/1164 LD 07/1166
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 01:11 | 49 | 11
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 49.1833 |  |  |  |  | 28.549 | 1 | 0 | 0 | 744 | 28.549 | 21240.456 | 0 | 100%
77 | 907032 | DAMOH-BIRSINGHPUR I 400kV | 2013-07-07 | 07:18 | 2013-07-09 | 10:37 | - |  |  | - |  |  | - |  |  | 1900-01-01 03:19 | 51 | 18 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/415 | LD 07/543
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 03:19 | 51 | 18
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 51.3 |  |  |  |  | 228.474 | 2 | 0 | 0 | 744 | 456.948 | 339969.312 | 0 | 100%
78 |  | DAMOH-BIRSINGHPUR II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 228.474 | 2 | 0 | 0 | 744 | 456.948 | 339969.312 | 0 | 100%
79 |  | DEHGAM PIRANA I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 0 | 0 | 744 | 93.34 | 69444.96 | 0 | 100%
80 |  | DEHGAM PIRANA II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 0 | 0 | 744 | 93.34 | 69444.96 | 0 | 100%
81 |  | MUNDRA-BHACHAU I 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 99.468 | 3 | 0 | 0 | 744 | 298.404 | 222012.576 | 0 | 100%
82 |  | MUNDRA-BHACHAU II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 99.468 | 3 | 0 | 0 | 744 | 298.404 | 222012.576 | 0 | 100%
83 | 907020 | BHACHAU-RANCHODPURA I 400kV | 2013-07-05 | 03:25 | 2013-07-05 | 10:16 | - |  |  | - |  |  | - |  |  | 0.28542 | 6 | 50 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/278 | LD 07/293
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28542 | 6 | 50
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.8333 |  |  |  |  | 282.856 | 3 | 0 | 0 | 744 | 848.568 | 631334.592 | 0 | 100%
84 |  | BHACHAU-RANCHODPURA II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0 | 0 | 744 | 848.568 | 631334.592 | 0 | 100%
85 | 907006 | MUNDRA-LIMBDI I 400kV | 2013-07-01 | 11:15 | 2013-07-01 | 19:37 | - |  |  | - |  |  | - |  |  | 0.34861 | 8 | 22 | OSFD | Line H/T to avail S/D by GETCO for line isolator maintenance work. | LD07/30 | LD07/60
| 907054 | MUNDRA-LIMBDI I 400kV | 2013-07-12 | 09:31 | 2013-07-13 | 19:21 | - |  |  | - |  |  | - |  |  | 1899-12-31 09:50 | 33 | 50 | OSPD | Line H/T to avail OCC approved S/D by CGPL Mundra for replacement of CVT at CGPL S/Y | LD 07/785 | LD 07/942
| 907062 | MUNDRA-LIMBDI I 400kV | 2013-07-14 | 08:15 | 2013-07-14 | 18:30 | - |  |  | - |  |  | - |  |  | 0.42708 | 10 | 15 | LCSD | Line H/T for replacement of defective Porcelain insulator strings (due to tracking) with Polymer insulator strings. | LD/07/966 | LD07/994
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 04:27 | 51 | 87
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 52.45 |  |  |  |  | 314.053 | 3 | 0 | 0 | 744 | 942.159 | 700966.296 | 0 | 100%
86 | 907063 | MUNDRA-LIMBDI II 400kV | 2013-07-14 | 10:56 | 2013-07-14 | 11:46 | 0.010417 | 0 | 15 | 0.024306 | 0 | 35 | - |  |  | - |  |  | LEFT | Line A/T on R ph to E/F due to Humidity conditions clubbed with heavy wind prevailing during evening hours in coastal area of Rann of Kutch, Gujarat. Charging delayed due to normalization delay at CGPL/LIMBDI end. (Fault Location 40.4 km from Mundra & 226 km from Limbdi Line) |  | LD07/976
| 907066 | MUNDRA-LIMBDI II 400kV | 2013-07-15 | 09:24 | 2013-07-16 | 17:16 | - |  |  | - |  |  | - |  |  | 1899-12-31 07:52 | 31 | 51 | OSPD | Line H/T to avail OCC S/D by CGPL for CT replacement. | LD07/1027 | LD07/1103
| 907071 | MUNDRA-LIMBDI II 400kV | 2013-07-17 | 08:44 | 2013-07-17 | 19:02 | - |  |  | - |  |  | - |  |  | 0.42917 | 10 | 18 | LCSD | Line H/T to avail S/D for replacement of long rod Porcelain insulator string with Polymer insulators. | LD07/1146 | LD07/1186
| 907144 | MUNDRA- LIMBDI II 400kV | 2013-07-31 | 14:35 | 2013-07-31 | 16:04 | - |  |  | - |  |  | - |  |  | 0.061806 | 1 | 28 | OSPD | Emergency shutdown taken by CGPL for implementation of SPS | LD 07/2199 | LD 07/2205
|  | SUBTOTAL |  |  |  |  | 0.010417 | 0 | 15 | 0.024306 | 0 | 35 | 0 | 0 | 0 | 1899-12-31 19:39 | 42 | 97
|  | Element Availability= | [6 empty] | 0.25 |  |  | 0.58333 |  |  | 0 |  |  | 43.6167 |  |  |  |  | 314.053 | 3 | 0.25 | 235.5397 | 743.4167 | 942.159 | 700416.7033 | 0.00033629 | 99.97%
87 | 907005 | SATNA-BINA(PG ) I 765kV | 2013-07-01 | 18:20 | 2013-07-17 | 13:52 | - |  |  | - |  |  | - |  |  | 1900-01-14 19:32 | 379 | 31 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/56 | WR 07/1160 NLD 07/105
| 907118 | SATNA-BINA(PG ) I 765kV | 2013-07-25 | 11:55 | 2013-07-30 | 13:31 | - |  |  | - |  |  | - |  |  | 1900-01-04 01:36 | 121 | 35 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1750 ,175 | LD 07/2122 ,211
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-19 21:08 | 500 | 66
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 501.1 |  |  |  |  | 274.164 | 4 | 0 | 0 | 744 | 1096.656 | 815912.064 | 0 | 100%
88 | 906043 | SATNA-BINA(PG ) II 765kV | 2013-06-06 | 19:33 | 2013-07-01 | 16:30 | - |  |  | - |  |  | - |  |  | 1900-01-23 20:57 | 596 | 57 | LVRD | After declaration of readiness line kept out for volatge regulation on WRLDC instruction. Charging code was not issued by WRLDC due to persisting high voltage in the grid. |  | LD07/39
| 907074 | SATNA-BINA(PG ) II 765kV | 2013-07-17 | 16:20 | 2013-07-25 | 11:05 | - |  |  | - |  |  | - |  |  | 1900-01-06 18:45 | 186 | 45 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 07/1178 NLD 07/107 | WR 07/1734 NLD 07/169
| 907412 | SATNA-BINA(PG ) II 765kV | 2013-07-30 | 13:37 |  |  | - |  |  | - |  |  | - |  |  | 1899-12-31 10:23 | 34 | 23 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/2131 ,213
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-02-02 02:05 | 816 | 125
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 818.0833 |  |  |  |  | 275.635 | 4 | 0 | 0 | 744 | 1102.54 | 820289.76 | 0 | 100%
89 | 907003 | BINA (PG) -INDORE I 765kV | 2013-07-01 | 02:59 | 2013-07-01 | 03:09 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T due to Operation of O/V Protection at Indore end
| 907004 | BINA (PG) -INDORE I 765kV | 2013-07-01 | 03:09 | 2013-07-13 | 11:45 | - |  |  | - |  |  | - |  |  | 1900-01-11 08:36 | 296 | 36 | LVRD | After tripping on O/V, Line could not be charged due to persisting High Voltage. |  | WR 07/907 NLD 07/80
| 907061 | BINA (PG) -INDORE I 765kV | 2013-07-14 | 05:02 | 2013-07-17 | 20:52 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | 1900-01-02 15:40 | 87 | 40 | GOVC | Line A/T on Operation of O/V stage - I protection at Indore end & Subsequently kept out for Voltage regulation on WRLDC Instruction |  | LD 07/1191
| 907080 | BINA (PG) -INDORE I 765kV | 2013-07-17 | 23:45 | 2013-07-18 | 20:35 | - |  |  | - |  |  | - |  |  | 0.86806 | 20 | 49 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1203,110 | LD07/1281, 121
| 907084 | BINA (PG) -INDORE I 765kV | 2013-07-18 | 23:14 | 2013-07-20 | 19:22 | - |  |  | - |  |  | - |  |  | 1899-12-31 20:08 | 44 | 7 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1288,122 | WR 07/1439 NLD 07/138
| 907097 | BINA (PG) -INDORE I 765kV | 2013-07-20 | 23:53 | 2013-07-21 | 20:18 | - |  |  | - |  |  | - |  |  | 0.85069 | 20 | 25 | LVRD | Line A/T ON operation of O/V stage I at BINA and kept out on voltage regulation . | LD 07/1454 | LD 07/1504
| 907105 | BINA (PG) -INDORE I 765kV | 2013-07-22 | 01:07 | 2013-07-22 | 23:23 | - |  |  | - |  |  | - |  |  | 0.92778 | 22 | 16 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1512 | LD 07/1577
| 907110 | BINA (PG) -INDORE I 765kV | 2013-07-23 | 2:02 | 2013-07-25 | 16:15 | - |  |  | - |  |  | - |  |  | 1900-01-01 14:13 | 62 | 13 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1590 | WR 07/1752 NLD 07/176
| 907122 | BINA (PG) -INDORE I 765kV | 2013-07-25 | 18:00 | 2013-07-26 | 16:21 | - |  |  | - |  |  | 0.93125 | 22 | 21 | - |  |  | GOVC | Line A/T on operation of O/V stage-I at Indore. |  | WR 07/1854 NLD 07/194
| 907132 | BINA (PG) -INDORE I 765kV | 2013-07-26 | 23:07 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-04 00:53 | 120 | 53 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/1889, 197
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.94514 | 22 | 41 | 1900-01-27 03:01 | 671 | 239
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 22.6833 |  |  | 674.9833 |  |  |  |  | 311 | 4 | 0 | 0 | 721.3167 | 1244 | 897317.9333 | 0 | 100%
90 |  | GANDHAR-NAVSARI (PG) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 102.152 | 2 | 0 | 0 | 744 | 204.304 | 152002.176 | 0 | 100%
91 |  | GANDHAR-NAVSARI (PG) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 10.152 | 2 | 0 | 0 | 744 | 20.304 | 15106.176 | 0 | 100%
92 | 907013 | MUNDRA-JETPUR I 400kV | 2013-07-04 | 02:40 | 2013-07-04 | 05:16 | - |  |  | - |  |  | - |  |  | 0.10833 | 2 | 36 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/187 | LD 07/200
| 907024 | MUNDRA-JETPUR I 400kV | 2013-07-05 | 19:36 | 2013-07-05 | 19:45 | - |  |  | - |  |  | 0.00625 | 0 | 8 | - |  |  | LNCC | Line A/T on B Ph To E/F due to tracking across longrod porcelain insulators because of dust deposition clubbed with presence of moisture. F/L:62.29km from Jetpur |  | LD 07/334
| 907025 | MUNDRA-JETPUR I 400kV | 2013-07-05 | 23:11 | 2013-07-06 | 11:00 | - |  |  | - |  |  | 0.49236 | 11 | 49 | - |  |  | LNCC | Line A/T on B-ph to E/F due to tracking across longrod porcelain insulators because of dust deposition clubbed with presence of moisture. F/L:57.47km from Jetpur |  | LD 07/371
| 907050 | MUNDRA-JETPUR I 400kV | 2013-07-12 | 01:05 | 2013-07-12 | 08:45 | - |  |  | - |  |  | - |  |  | 0.31944 | 7 | 40 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/762
| 907081 | MUNDRA-JETPUR I 400kV | 2013-07-18 | 10:49 | 2013-07-18 | 19:35 | 0.36528 | 8 | 45 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC approved S/D for Line maintenance | LD07/1243 | LD07/1278
| 907087 | MUNDRA-JETPUR I 400kV | 2013-07-19 | 09:36 | 2013-07-19 | 19:40 | 0.41944 | 10 | 3 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail OCC S/D by POWERGRID for AMP & Line Maintenance work. | LD 07/1315 | LD 07/1364
| 907134 | MUNDRA-JETPUR I 400kV | 2013-07-27 | 10:10 | 2013-07-27 | 13:35 | - |  |  | - |  |  | - |  |  | 0.14236 | 3 | 24 | OSPD | H/T to avail S/D by CGPL Mundra for implementation of SPS system at Mundra. | LD 07/1913 | LD 07/1932
| 907413 | MUNDRA-JETPUR I 400KV | 2013-07-30 | 15:10 | 2013-07-30 | 18:00 | - |  |  | - |  |  | - |  |  | 0.11806 | 2 | 49 | OSPD | Line H/T for commissioning of SPS system by Mundra | LD 07/2134 | LD 07/2148
|  | SUBTOTAL |  |  |  |  | 0.78472 | 18 | 48 | 0 | 0 | 0 | 0.49861 | 11 | 57 | 0.68819 | 14 | 149
|  | Element Availability= | [6 empty] | 18.8 |  |  | 0 |  |  | 11.95 |  |  | 16.4833 |  |  |  |  | 337 | 3 | 18.8 | 19006.8 | 732.05 | 1011 | 740102.55 | 0.025681 | 97.43%
93 | 907021 | MUNDRA-JETPUR II 400kV | 2013-07-05 | 01:50 | 2013-07-05 | 07:25 | - |  |  | - |  |  | - |  |  | 0.23264 | 5 | 35 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/274
| 907023 | MUNDRA-JETPUR II 400kV | 2013-07-05 | 19:27 | 2013-07-05 | 19:37 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | LNCC | Line A/T on Y-ph to E/F due to tracking across longrod porcelain insulators because of dust deposition clubbed with presence of moisture. F/L:64.25km from Jetpur |  | LD 07/331
| 907026 | MUNDRA-JETPUR II 400kV | 2013-07-05 | 23:19 | 2013-07-06 | 11:21 | - |  |  | - |  |  | 0.50139 | 12 | 1 | - |  |  | LNCC | Line A/T on R-ph to E/F due to tracking across longrod porcelain insulators because of dust deposition clubbed with presence of moisture. F/L:44.46km from |  | LD 07/378
| 907088 | MUNDRA-JETPUR II 400kV | 2013-07-19 | 13:02 | 2013-07-19 | 14:22 | - |  |  | 0.055556 | 1 | 19 | - |  |  | - |  |  | SBBU | A/T due to operation of BB protection at Jetpur (GETCO). |  | LD 07/1340
| 907094 | 400kV MUNDRA-JETPUR II | 2013-07-20 | 10:58 | 2013-07-20 | 19:33 | - |  |  | - |  |  | - |  |  | 0.35764 | 8 | 35 | LCSD | Line H/T to avail S/D for replacement of long rod porcelain insulator string(due to Tracking) with polymer insulator strings. | LD 07/1407 | LD 07/1438
| 907102 | MUNDRA-JETPUR II 400kV | 2013-07-21 | 09:10 | 2013-07-22 | 18:40 | - |  |  | - |  |  | - |  |  | 1899-12-31 09:30 | 33 | 30 | OSPD | Line H/T to avail OCC S/D by CGPL for replacement of CVT | LD07/1469 | LD 07/1565
| 907112 | MUNDRA-JETPUR II 400kV | 2013-07-24 | 12:48 | 2013-07-24 | 12:56 | - |  |  | - |  |  | - |  |  | 0.0055556 | 0 | 8 | OSFD | Line H/T to avail emergency S/D by CGPL for checking of newly eracted CT at CGPL S/Y | LD 07/1681 | LD 07/1682
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.055556 | 1 | 19 | 0.50833 | 12 | 11 | 1899-12-31 23:48 | 46 | 108
|  | Element Availability= | [6 empty] | 0 |  |  | 1.3167 |  |  | 12.1833 |  |  | 47.8 |  |  |  |  | 337 | 3 | 0 | 0 | 730.5 | 1011 | 738535.5 | 0 | 100%
94 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 744 | 114.2 | 84964.8 | 0 | 100%
95 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 744 | 114.2 | 84964.8 | 0 | 100%
96 |  | VINDHYACHAL (NTPC) -SASAN (RELIANCE) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 744 | 10.886 | 8099.184 | 0 | 100%
97 |  | VINDHYACHAL (NTPC) -SASAN (RELIANCE) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 744 | 10.886 | 8099.184 | 0 | 100%
98 | 906156 | SASAN-SATNA I 765 kV | 2013-06-29 | 15:04 | 2013-07-05 | 10:58 | - |  |  | - |  |  | - |  |  | 1900-01-03 10:58 | 106 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 06/2333 NLD 06/354 | WR 07/290 NLD 07/29
| 907103 | SASAN-SATNA I 765kV | 2013-07-21 | 17:49 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-09 06:11 | 246 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD07/1496
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-13 17:09 | 352 | 69
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 353.15 |  |  |  |  | 245.7 | 4 | 0 | 0 | 744 | 982.8 | 731203.2 | 0 | 100%
99 |  | BINA(PG)-BINA(MPEB) III 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.8 | 2 | 0 | 0 | 744 | 1.6 | 1190.4 | 0 | 100%
100 |  | VAPI - NAVASARI (GIS) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 744 | 233.7 | 173872.8 | 0 | 100%
101 |  | VAPI - NAVASARI (GIS) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 744 | 233.7 | 173872.8 | 0 | 100%
102 | 907022 | SASAN-SATNA II 765kV | 2013-07-05 | 19:00 | 2013-07-21 | 19:21 | - |  |  | - |  |  | - |  |  | 1900-01-15 00:21 | 384 | 21 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/330, NL 07/32 | LD 07/1499
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-15 00:21 | 384 | 21
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 384.35 |  |  |  |  | 245.7 | 4 | 0 | 0 | 744 | 982.8 | 731203.2 | 0 | 100%
103 |  | BINA(PG)-BINA(MPEB) IV 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.8 | 2 | 0 | 0 | 744 | 1.6 | 1190.4 | 0 | 100%
104 |  | INDORE (MP) - INDORE (PG) I 400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 49.7 | 4 | 0 | 0 | 744 | 198.8 | 147907.2 | 0 | 100%
105 |  | INDORE (MP) - INDORE (PG) II 400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 49.7 | 4 | 0 | 0 | 744 | 198.8 | 147907.2 | 0 | 100%
[20 empty] | TRANSMISSION LINE AVAILABILITY | [5 empty] | 25734.501 |  |  | 29443993.9862
0.00087402
99.91%
1 |  | AGRA-GWALIOR I 765kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 129.435 | 4 | 0 | 0 | 744 | 517.74 | 385198.56 | 0 | 100%
2 |  | AGRA-GWALIOR II 765kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 127.934 | 4 | 0 | 0 | 744 | 511.736 | 380731.584 | 0 | 100%
ICTs
1 |  | ICT1 JABALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
2 |  | ICT2 JABALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
3 |  | ICT1 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
4 |  | ICT2 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
5 |  | ICT1 SATNA 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
6 |  | ICT2 SATNA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
7 |  | ICT1 KHANDWA 400/220kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
8 | 907101 | ICT2 KHANDWA 400/220kV | 2013-07-21 | 08:51 | 2013-07-21 | 09:25 | 0.023611 | 0 | 33 | - |  |  | - |  |  | - |  |  | OSPT | ICT H/T for testing of newly retrofitted differential relay | LD07/1468 | LD07/1472
|  | SUBTOTAL |  |  |  |  | 0.023611 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.55 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0.55 | 433.125 | 744 | 787.5 | 585900 | 0.00073925 | 99.93%
9 |  | ICT1 VAPI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
10 |  | ICT2 VAPI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
11 |  | ICT1 GWALIOR 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
12 |  | ICT1 RAJGARH 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
13 |  | ICT2 GWALIOR 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
14 |  | ICT ITARSI 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
15 |  | ICT1 DAMOH 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
16 |  | ICT2 DAMOH 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
17 |  | ICT2 RAJGARH 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
18 |  | ICT1 BINA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
19 |  | ICT1 PIRANA 400/220/33kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
20 |  | ICT2 PIRANA 400/220/33kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
21 |  | ICT3 GWALIOR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
22 |  | ICT1 SHUJALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
23 |  | ICT1 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
24 |  | ICT2 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
25 |  | ICT2 SHUJALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
26 |  | ICT1 SATNA 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
27 | 907046 | ICT2 NAVSARI 400/220/33kV | 2013-07-11 | 11:19 | 2013-07-11 | 14:42 | 0.14097 | 3 | 23 | - |  |  | - |  |  | - |  |  | OSPT | ICT H/T to Avail OCC approved S/D for AMP works. | LD 07/713 | LD 07/731
|  | SUBTOTAL |  |  |  |  | 0.14097 | 3 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.3833 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 3.3833 | 2664.375 | 744 | 787.5 | 585900 | 0.0045475 | 99.55%
28 | 907042 | ICT1 NAVSARI 400/220/33kV | 2013-07-09 | 10:17 | 2013-07-09 | 17:30 | 0.30069 | 7 | 12 | - |  |  | - |  |  | - |  |  | OSPT | ICT H/T to avail OCC approved S/D for AMP | LD 07/548 | LD 07/573
|  | SUBTOTAL |  |  |  |  | 0.30069 | 7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 7.2 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 7.2 | 5670 | 744 | 787.5 | 585900 | 0.0096774 | 99.03%
29 |  | ICT2 SATNA 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
30 |  | ICT1 BINA 765/400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
31 |  | ICT3 VAPI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
32 |  | ICT2 BINA 765/400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
33 |  | ICT1 GWALIOR 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
34 |  | ICT2 GWALIOR 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
35 |  | ICT2 GWALIOR 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
[20 empty] | ICT AVAILABILITY | [5 empty] | 8767.5 |  |  | 30191130.144
0.0002904
99.97%
Bus Reactors
1 |  | BUS REACTOR DEHGAM I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
2 |  | BUS REACTOR JABALPUR I 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 744 | 100 | 74400 | 0 | 100%
3 |  | BUS REACTOR JABALPUR II 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 744 | 100 | 74400 | 0 | 100%
4 |  | BUS REACTOR ITARSI I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
5 |  | BUS REACTOR ITARSI II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
6 |  | BUS REACTOR ITARSI III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
7 |  | BUS REACTOR JABALPUR III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
8 |  | BUS REACTOR DHULE 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 744 | 320 | 238080 | 0 | 100%
9 |  | BUS REACTOR SATNA 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
10 |  | Bus Reactor # 1 / Bina |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
11 |  | Bus Reactor / Damoh |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
12 |  | Bus Reactor / Gwalior |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
13 |  | BUS REACTOR KHANDWA 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
14 |  | Bus Reactor / Dehgam |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
15 |  | Bus Reactor / Bhachau |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
16 |  | Bus Reactor / Shujalpur |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
17 |  | Bus Reactor/ Rajgarh |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
18 | 907111 | BUS REACTOR SATNA 765kV | 2013-07-23 | 21:06 | 2013-07-24 | 08:24 | - |  |  | - |  |  | - |  |  | 0.47083 | 11 | 17 | SVRD | Reactor H/T for Voltage regulation | WR 07/1649 NLD 07/162 | WR 07/1661 NLD 07/163
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47083 | 11 | 17
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.2833 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
19 |  | Bus Reactor / Navsari |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
20 |  | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
21 |  | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
22 |  | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
23 |  | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
24 |  | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
25 |  | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
26 |  | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
[20 empty] | BUS REACTOR AVAILABILITY | [5 empty] | 0 |  |  | 7692960
0
100%
[20 empty] | SYSTEM AVAILABILITY | [5 empty] | 34502.001 |  |  | 67328084.1302
0.00051245
99.95%
Formulas:
OUTAGE HOURS ATTRIBUTED TO = IF((RIGHT([Outage Category],1)="T"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE HOURS ATTRIBUTED TO = SUM(H11:[OUTAGE HOURS ATTRIBUTED TO, row above])
OUTAGE DEEMED AVAILABLE = IF((RIGHT([Outage Category],1)="D"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE DEEMED AVAILABLE = SUM(Q11:[OUTAGE DEEMED AVAILABLE, row above])
OTHERS = SUM(K11:[OTHERS, row above])
OTHERS = SUM([OTHERS, row above])
SYSTEM CONSTR. = SUM(N11:[SYSTEM CONSTR., row above])
SYSTEM CONSTR. = SUM([SYSTEM CONSTR., row above])

## availability sheet
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR JULY-2013
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 0 | 100 | 100%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 0 | 100 | 100%
3 | 400kV Itarsi-Indore # 2 | 3 | 19 |  |  | 3.3167 | 0 | 744 | 214 | 2 | 1419.5333 | 428 | 318432 | 0.0044579 | 99.5542 | 99.55%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 0 | 100 | 100%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 0 | 100 | 100%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 0 | 100 | 100%
7 | 400 KV V'chal - Jabalpur # 2 |  |  | 0 | 43 | 0 | 0.71667 | 743.2833 | 360 | 2 | 0 | 720 | 535164 | 0 | 100 | 100%
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100%
12 | 400 KV Jabalpur-Sasan |  |  |  |  | 0 | 0 | 744 | 376 | 2 | 0 | 752 | 559488 | 0 | 100 | 100%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 744 | 21 | 2 | 0 | 42 | 31248 | 0 | 100 | 100%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 0 | 100 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 0 | 100 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 0 | 100 | 100%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 0 | 100 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 110 | 2 | 0 | 220 | 163680 | 0 | 100 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 0 | 100 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 0 | 100 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  | 1 | 0 | 0 | 1 | 743 | 58.149 | 1 | 0 | 58.149 | 43204.707 | 0 | 100 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 744 | 31.334 | 1 | 0 | 31.334 | 23312.496 | 0 | 100 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 |  |  |  |  | 0 | 0 | 744 | 31.334 | 1 | 0 | 31.334 | 23312.496 | 0 | 100 | 100%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100%
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 0 | 100 | 100%
33 | 220kV Kawas-Haldarwa # 2 | 4 | 45 |  |  | 4.75 | 0 | 744 | 81 | 1 | 384.75 | 81 | 60264 | 0.0063844 | 99.3616 | 99.36%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 0 | 100 | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 74 | 1 | 0 | 74 | 55056 | 0 | 100 | 100%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100%
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28 | 0 | 100 | 100%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 744 | 100.32 | 2 | 0 | 200.64 | 149276.16 | 0 | 100 | 100%
44 | 400kV Nigrie-Satna |  |  |  |  | 0 | 0 | 744 | 161.11 | 2 | 0 | 322.22 | 239731.68 | 0 | 100 | 100%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100%
49 | 765 kV Gwalior-Bina # 1 |  |  |  |  | 0 | 0 | 744 | 234.931 | 4 | 0 | 939.724 | 699154.656 | 0 | 100 | 100%
50 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 0 | 100 | 100%
51 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968 | 0 | 100 | 100%
52 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100%
54 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100%
55 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100%
56 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 0 | 100 | 100%
57 | 400KV Nagda - Dehgam # 1 | 6 | 54 |  |  | 6.9 | 0 | 744 | 331.442 | 2 | 4573.8996 | 662.884 | 493185.696 | 0.0092742 | 99.0726 | 99.07%
58 | 400KV Seoni - Khandwa # 1 |  |  | 11 | 21 | 0 | 11.35 | 732.65 | 351.729 | 4 | 0 | 1406.916 | 1030777.0074 | 0 | 100 | 100%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504 | 0 | 100 | 100%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88 | 0 | 100 | 100%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88 | 0 | 100 | 100%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100%
66 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100%
67 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100%
68 | 220 KV Vapi - Karadpada # 1 | 4 | 6 |  |  | 4.1 | 0 | 744 | 29.66 | 1 | 121.606 | 29.66 | 22067.04 | 0.0055108 | 99.4489 | 99.45%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 0 | 100 | 100%
70 | 765 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352 | 0 | 100 | 100%
71 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 0 | 100 | 100%
72 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 0 | 100 | 100%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 0 | 100 | 100%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 0 | 100 | 100%
75 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 0 | 100 | 100%
76 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100%
77 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100%
78 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 0 | 100 | 100%
79 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 0 | 100 | 100%
80 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100%
81 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100%
82 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100%
83 | 400kV Bhachau - Ranchodpura # 2 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100%
84 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 0 | 100 | 100%
85 | 400kV Mundra - Limbdi # 2 | 0 | 15 | 0 | 35 | 0.25 | 0.58333 | 743.4167 | 314.053 | 3 | 235.5397 | 942.159 | 700416.7033 | 0.00033629 | 99.9664 | 99.97%
86 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 0 | 100 | 100%
87 | 765kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 275.635 | 4 | 0 | 1102.54 | 820289.76 | 0 | 100 | 100%
88 | 765kV Bina - Indore |  |  | 22 | 41 | 0 | 22.6833 | 721.3167 | 311 | 4 | 0 | 1244 | 897317.9333 | 0 | 100 | 100%
89 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100%
90 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100%
91 | 400kV Mundra-Jetpur#1 | 18 | 50 | 11 | 58 | 18.8333 | 11.9667 | 732.0333 | 337 | 3 | 19040.5 | 1011 | 740085.7 | 0.025727 | 97.4273 | 97.43%
92 | 400kV Mundra-Jetpur#2 |  |  | 13 | 32 | 0 | 13.5333 | 730.4667 | 337 | 3 | 0 | 1011 | 738501.8 | 0 | 100 | 100%
93 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100%
95 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100%
96 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100%
97 | 765kV Sasan - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 245.7 | 4 | 0 | 982.8 | 731203.2 | 0 | 100 | 100%
98 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100%
99 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 744 | 116.85 | 2 | 0 | 233.7 | 173872.8 | 0 | 100 | 100%
100 | 400kV Vapi-Navsari#2 |  |  |  |  | 0 | 0 | 744 | 116.85 | 2 | 0 | 233.7 | 173872.8 | 0 | 100 | 100%
101 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 245.7 | 4 | 0 | 982.8 | 731203.2 | 0 | 100 | 100%
102 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100%
103 | 400kV Indore (MP)-Indore (PG)#1 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100%
104 | 400kV Indore (MP)-Indore (PG)#2 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100%
| Total Sr.No. 1 to 104 | 35 | 189 | 58 | 230 |  |  |  | 16433.683 |  | 25775.8287 |  | 29542859.019
* | Lines charged with 400kV level
|  | 38.15 |  | 61.8333
[10 empty] | NAFM | 0.00087249
Availability of ( Sl no 1 to 104) transmission lines during JULY-2013 = | [9 empty] | TAFM | 99.9128
1 | 765 kV Gwalior -Agra # 1 |  |  | 0 | 0 | 0 | 0 | 744 | 129.435 | 4 | 0 | 517.74 | 385198.56 | 0 | 100 | 100%
1 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 0 | 100 | 100%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
8 | 400/220kV ICT # 2 / Khandwa | 0 | 34 |  |  | 0.56667 | 0 | 744 | 315 | 2.5 | 446.25 | 787.5 | 585900 | 0.00076165 | 99.9238 | 99.92%
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
10 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
14 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
20 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
21 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
22 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
23 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
24 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
25 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
26 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
27 | 400/220 KV ICT # 2 / Navsari | 3 | 23 |  |  | 3.3833 | 0 | 744 | 315 | 2.5 | 2664.375 | 787.5 | 585900 | 0.0045475 | 99.5453 | 99.55%
28 | 400/220 KV ICT # 1 / Navsari | 7 | 13 |  |  | 7.2167 | 0 | 744 | 315 | 2.5 | 5683.125 | 787.5 | 585900 | 0.0096998 | 99.03 | 99.03%
29 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
30 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
31 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
32 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
33 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100%
34 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100%
35 | 765/400KV ICT# 2 / INDORE |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100%
| Total Sr.No. 1 to 35 | 10 | 70 | 0 | 0 |  |  |  | 17320 |  | 8793.75 |  | 32215200
|  | 11.1667 |  | 0 | [5 empty] | NAFM | 0.00027297
Availability of 35 ( Sl no 1 to 35) ICTs in JULY-2013 = | [9 empty] | TAFM | 99.9727
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100%
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100%
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 0 | 100 | 100%
9 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
15 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
16 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
17 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
18 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
19 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
20 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
21 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
22 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
23 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
24 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
25 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
26 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
| Total of sl no 1 to 26 | 0 | 0 | 0 | 0 |  |  |  | 2585 |  | 0 |  | 7692960
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 26 ( Sl no 1 to 26) Bus Reactors in JULY-2013 = | [7 empty] | TAFM | 100
[11 empty] | 34569.5787 |  | 69451019.019
[8 empty] | NAFM = | 0.00049775
% System Availability for JULY-2013 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9502
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B135: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B136: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## ANX-II
MONTH : JULY-2013
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : JULY-2013
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
July 2013
Sl. No. | Name of Elements | Type of failures | Restoration Time (Days) |  |  | Remarks
A |  | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 |  | Insualtor Failure | Terrain Type
|  |  | Plain | River bed | Hilly
i | NAGDA-DEHGAM I 400KV | Insualtor Failure in single phase | Less than 1 day
| KAWAS-HALDARWA II 220kV |  | Less than 1 day
ii |  | Insualtor Failure in two phases | NIL
ii |  | Insualtor Failure in three phases
2 |  | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 |  | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 |  | Tower Damage ( not collapse)
i |  | One arm damage
ii |  | Two arm damage
5 |  | Snapping of phase conductor
i |  | Conductor snapping in single phase
ii |  | Conductor snapping in two phases
iii |  | Conductor snapping in three phases
6 |  | Failure of Earth wire
7 |  | Insulator failure with conductor snapping
8 |  | Any other combination of failures
B |  | Elements of sub-station for each KV class seperately
1 |  | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
|  | Other major failures in ICTs | Single phase Unit |  | Three phase Unit
|  | (i) Replacement of faulty bushings | NIL
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 |  | Failures of Reactors
Restoration of failed Reactors

## Supporting Annex V
Supporting Annex V
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF JULY'2013
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | Outage Category | Details | WRLDC CODE FOR |  | Outage in Days |  |  | REMARKS
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING | Flashover | Snapping | Collapes of Tower
1 | 907011 | NAGDA-DEHGAM I 400KV | 2013-07-04 | 01:04 | 2013-07-05 | 13:54 | 0.2875 | - | - | 1899-12-31 05:56 | LHWT | Line A/T on Y ph to Earth fault due to Flashover of at loc 641. The patrolling could not be carried out in night hours due to poor visibility. Further, Restoration work get delayed due to Continuous heavy rain and inaccessable location. Hence outage from 01:04 Hrs/04.07.2013 to 07:00 hrs/05.07.2013 may not be attributable to POWERGRID Account(F/L 96.7KM from Dehgam) |  | LD 07/308 | 0.2875
2 | 907116 | KAWAS-HALDARWA II 220kV | 2013-07-24 | 17:11 | 2013-07-25 | 10:45 | 0.19792 | - | - | 0.53403 | LHWT | Line A/T on R-ph to E/F due to Insulator string flashover at Loc no 118. Patrolling could not be carried out due to poor visibility during heavy rains and heavy water logged around tower location. Hence outage from 24.07.2013/17:11 hrs to 25.07.2013/06:00 Hrs may not be attributable to POWERGRID( F/L - 41.8kms from Haldarwa). |  | LD 07/1741 | 0.19792