## Tripping AC SYSTEM (hidden)
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR MARCH- 2011
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032
5 | 400kV Indore-Asoj # 2 | 8 | 38 |  |  | 8.6333 | 0 | 744 | 273 | 2 | 4713.8 | 546 | 406224
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
8 | 400 KV Jabalpur - Itarsi # 1 | 4 | 54 |  |  | 4.9 | 0 | 744 | 232 | 2 | 2273.6 | 464 | 345216
9 | 400 KV Jabalpur - Itarsi # 2 | 6 | 25 |  |  | 6.4167 | 0 | 744 | 232 | 2 | 2977.3333 | 464 | 345216
10 | 400kV Jhanor-Dehgam#1 | 0 | 0 |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616
11 | 400kV Jhanor-Dehgam#2 | 12 | 59 |  |  | 12.9833 | 0 | 744 | 157 | 2 | 4076.7667 | 314 | 233616
12 | 400 KV V'chal - Jabalpur # 3 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
13 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
14 | 400 KV Jabalpur - Itarsi # 3 | 4 | 45 |  |  | 4.75 | 0 | 744 | 234 | 2 | 2223 | 468 | 348192
15 | 400 KV Jabalpur - Itarsi # 4 | 5 | 52 |  |  | 5.8667 | 0 | 744 | 234 | 2 | 2745.6 | 468 | 348192
16 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
17 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
18 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
19 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
20 | 400 KV Jhanor - Sugen(PGCIL portion) | 13 | 31 | 0 | 51 | 13.5167 | 0.85 | 743.15 | 57 | 2 | 1540.9 | 114 | 84719.1
21 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 9 | 3 | 0 | 9.05 | 734.95 | 110 | 2 | 0 | 220 | 161689
22 | 400 KV Jhanor - Jhanor(GPEC) |  |  | 1 | 88 | 0 | 2.4667 | 741.5333 | 13 | 2 | 0 | 26 | 19279.8667
23 | 220kV Jhanor-Haldarwa ckI # 1 | 0 | 15 | 3 | 42 | 0.25 | 3.7 | 740.3 | 13 | 1 | 3.25 | 13 | 9623.9
24 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  | 71 | 0 | 1.1833 | 742.8167 | 13 | 1 | 0 | 13 | 9656.6167
25 | 220kV Kawas-Navsari ckt # 1 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 49 | 1 | 17.9667 | 49 | 36456
26 | 220kV Kawas-Navsari ckt # 2 | 0 | 13 | 0 | 52 | 0.21667 | 0.86667 | 743.1333 | 49 | 1 | 10.6167 | 49 | 36413.5333
27 | 220kV Kawas-Ichchapur |  |  |  |  | 0 | 0 | 744 | 3 | 1 | 0 | 3 | 2232
28 | 220kV Kawas-Vav |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528
29 | 220kV Kawas - Haldarwa # 1 | 0 | 80 | 8 | 25 | 1.3333 | 8.4167 | 735.5833 | 81 | 1 | 108 | 81 | 59582.25
30 | 220kV Kawas-Haldarwa # 2 |  |  | 0 | 33 | 0 | 0.55 | 743.45 | 81 | 1 | 0 | 81 | 60219.45
31 | 220 kV Kakrapar - Haldarwa # 1 | 5 | 20 |  | 74 | 5.3333 | 1.2333 | 742.7667 | 74 | 1 | 394.6667 | 74 | 54964.7333
32 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 74 | 1 | 0 | 74 | 55012.8333
33 | 220 KV Kakrapar - Vav # 1 |  |  | 1 | 18 | 0 | 1.3 | 742.7 | 43 | 1 | 0 | 43 | 31936.1
35 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992
35 | 220kV Kakrapar-Vapi ckt # 1 | 0 | 26 |  |  | 0.43333 | 0 | 744 | 117 | 1 | 50.7 | 117 | 87048
36 | 220kV Kakrapar-Vapi ckt # 2 | 0 | 53 | 7 | 82 | 0.88333 | 8.3667 | 735.6333 | 117 | 1 | 103.35 | 117 | 86069.1
37 | 220kV Ichchapur-Vav |  |  |  |  | 0 | 0 | 744 | 34 | 1 | 0 | 34 | 25296
38 | 400kV V'chal - Satna # 1 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 267 | 2 | 0 | 534 | 397171.4
39 | 400kV V'chal - Satna # 2 | 0 | 50 | 0 | 18 | 0.83333 | 0.3 | 743.7 | 267 | 2 | 445 | 534 | 397135.8
40 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
41 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
42 | 400kV Satna - Bina # 1 | 0 | 24 |  |  | 0.4 | 0 | 744 | 276 | 2 | 220.8 | 552 | 410688
43 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688
44 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  | 1 | 49 | 0 | 1.8167 | 742.1833 | 0.742 | 2 | 0 | 1.484 | 1101.4001
45 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  | 1 | 50 | 0 | 1.8333 | 742.1667 | 0.742 | 2 | 0 | 1.484 | 1101.3753
46 | 400 kV Gwalior-Bina # 1 | 5 | 38 |  |  | 5.6333 | 0 | 744 | 234.931 | 4 | 5293.7785 | 939.724 | 699154.656
47 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
48 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
49 | 400KV Bina - Nagda # 1 | 0 | 18 |  |  | 0.3 | 0 | 744 | 330.155 | 2 | 198.093 | 660.31 | 491270.64
50 | 400KV Bina - Nagda # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 330.155 | 2 | 0 | 660.31 | 491160.5883
51 | 400KV Nagda - Dehgam # 2 |  |  | 3 | 58 | 0 | 3.9667 | 740.0333 | 331.442 | 2 | 0 | 662.884 | 490556.2561
52 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696
53 | 400KV Seoni - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
54 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
55 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
56 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
57 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
58 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
59 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
60 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
61 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
62 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
63 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
64 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
65 | 400 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352
66 | 400 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2
67 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848
68 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4
69 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
70 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
71 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
72 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
73 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
74 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
| Total Sr.No. 1 to 74 | 73 | 705 | 34 | 773 | 73.05 |  |  | 12271.634 |  | 27397.2215 |  | 19691267.3032
|  |  | 84.75 |  | 46.8833 |  |  |  |  | NAFM | 0.0013913
| Availability of 74 ( Sl no 1 to 74) transmission lines during MARCH-2011 = | [8 empty] | TAFM | 99.8609
Sr.No. 71,72,73 & 74 lines are declared for commercial operation w.e.f. 01.03.11
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
0.63333
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0.83333
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
10 | 400/220kV ICT # 2 / Vapi | 11 | 51 |  |  | 11.85 | 0 | 744 | 315 | 2.5 | 9331.875 | 787.5 | 585900
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
14 | 400/220kV ICT # 1 / Itarsi | 2 | 48 |  |  | 2.8 | 0 | 744 | 315 | 2.5 | 2205 | 787.5 | 585900
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
| Total Sr.No. 1 to 19 | 13 | 99 | 0 | 0 | 14.65 |  |  | 5040 | 47.5 | 11536.875 |  | 11132100
|  | 14.65 |  | 0 | [5 empty] | NAFM | 0.0010364
[10 empty] | TAFM | 99.8964
Availability of 19 ( Sl no 1 to 19) ICTs in MARCH-2011 =
ICT # 1 at Pirana was declared for commercial operation w.e.f. 01.03.11
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
| Total of sl no 1 to 14 | 0 | 0 | 0 | 0 |  |  |  | 882 | 56 | 0 |  | 2624832
0
[8 empty] | NAFM | 0
| Availability of 14( Sl no 1 to 14) Bus Reactors in MARCH-2011 = | [6 empty] | TAFM | 100
[11 empty] | 38934.0965 |  | 33448199.3032
[8 empty] | NAFM = | 0.001164
| % System Availability for MARCH 2011 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.8836
3
Note on B43: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B45: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B47: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B49: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B187: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B189: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-II) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-II) Transmission System in Western Region for the month of Sep - 2013 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 400kV Satpura-Itarsi | 100% | 37 | 220 KV Kakrapar - Vav # 2 | 100%
2 | 400kV Itarsi-Indore # 1 | 99.71% | 38 | 220kV Kakrapar-Vapi ckt # 1 | 100%
3 | 400kV Itarsi-Indore # 2 | 100% | 39 | 220kV Kakrapar-Vapi ckt # 2 | 100%
4 | 400kV Indore-Asoj # 1 | 100% | 40 | 400kV V'chal - Satna # 1 | 100%
5 | 400kV Indore-Asoj # 2 | 100% | 41 | 400kV V'chal - Satna # 2 | 100%
6 | 400 KV V'chal - Jabalpur # 1 | 99.98% | 42 | 400kV V'chal - Satna # 3 | 100%
7 | 400 KV V'chal - Jabalpur # 2 | 100% | 43 | 400kV V'chal -Nigrie | 100%
8 | 400 KV Jabalpur - Itarsi # 1 | 99.86% | 44 | 400kV Nigrie-Satna | 100%
9 | 400 KV Jabalpur - Itarsi # 2 | 100% | 45 | 400kV Satna - Bina # 1 | 100%
10 | 400kV Jhanor-Dehgam#1 | 100% | 46 | 400kV Satna - Bina # 2 | 100%
11 | 400kV Jhanor-Dehgam#2 | 100% | 47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 | 100%
12 | 400 KV Jabalpur-Sasan | 99.54% | 48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 | 100%
13 | 400kV Sasan-Vindhyachal | 100% | 49 | 765 kV Gwalior-Bina # 1 | 100%
14 | 400 KV V'chal - Jabalpur # 4 | 100% | 50 | 400KV Satna-Bina # 4 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 | 100% | 51 | 400KV Satna-Bina # 3 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 | 100% | 52 | 400KV Bina - Sujalpur # 1 | 99.37%
17 | 400 KV Itarsi - Khandwa # 1 | 100% | 53 | 400KV Bina - Sujalpur # 2 | 100%
18 | 400 KV Itarsi - Khandwa # 2 | 100% | 54 | 400KV Sujalpur - Nagda # 1 | 99.65%
19 | 400 KV Khandwa - Dhule # 1 | 99.22% | 55 | 400KV Sujalpur - Nagda # 2 | 99.64%
20 | 400 KV Khandwa - Dhule # 2 | 100% | 56 | 400KV Nagda - Dehgam # 2 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) | 100% | 57 | 400KV Nagda - Dehgam # 1 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) | 100% | 58 | 400KV Seoni - Khandwa # 1 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) | 100% | 59 | 400KV Seoni - Khandwa # 2 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 | 100% | 60 | 400KV Khandwa - Rajgarh # 2 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 | 100% | 61 | 400KV Rajgarh - SSP (LILO portion) # 1 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 | 99.56% | 62 | 400KV Rajgarh - SSP (LILO portion) # 2 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 | 100% | 63 | 400KV Rajgarh - Nagda (LILO portion) # 1 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 100% | 64 | 400KV Rajgarh - Nagda (LILO portion) # 2 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 93.27% | 65 | 400KV Khandwa - Rajgarh # 1 | 100%
30 | 220kV Kawas-Vav#1 | 100% | 66 | 220 KV Vapi - Magarwada # 1 | 100%
31 | 220kV Kawas-Vav#2 | 100% | 67 | 220 KV Vapi - Magarwada # 2 | 100%
32 | 220kV Kawas - Haldarwa # 1 | 100% | 68 | 220 KV Vapi - Karadpada # 1 | 100%
33 | 220kV Kawas-Haldarwa # 2 | 100% | 69 | 220 KV Vapi - Karadpada # 2 | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 | 100% | 70 | 765 kV Gwalior-Bina # 2 | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 | 100% | 71 | 765 kV Seoni - Bina | 99.88%
36 | 220 KV Kakrapar - Vav # 1 | 100% | 72 | 400kV Damoh - Bhopal # 1 | 100%
73 | 400kV Damoh - Bhopal # 2 | 100% | 121 | 400/220kV ICT # 1 / Itarsi | 100%
74 | 220 KV Vapi - Khadoli # 1 | 100% | 122 | 400/220kV ICT # 1 / Damoh | 99.87%
75 | 220 KV Vapi - Sayali | 100% | 123 | 400/220kV ICT # 2 / Damoh | 99.85%
76 | 220kV Sayali-Khadoli | 100% | 124 | 400/220 KV ICT # 2 / Rajgarh | 99.83%
77 | 400kV Damoh-Birsinghpur#1 | 99.91% | 125 | 400/220 KV ICT / Bina | 100%
78 | 400kV Damoh-Birsinghpur#2 | 99.78% | 126 | 400/220 KV ICT # 1 / Pirana | 100%
79 | 400kV Dehgam-Pirana#1 | 99.53% | 127 | 400/220 KV ICT # 2 / Pirana | 100%
80 | 400kV Dehgam-Pirana#2 | 99.71% | 128 | 400/220 KV ICT # 3 / Gwalior | 100%
81 | 400kV Mundra - Bhachau # 1 | 100% | 129 | 400/220 KV ICT # 1 / Shujalpur | 99.83%
82 | 400kV Mundra - Bhachau # 2 | 100% | 130 | 400/220 KV ICT # 1 / Bhachau | 100%
83 | 400kV Bhachau - Ranchodpura # 1 | 100% | 131 | 400/220 KV ICT # 2 / Bhachau | 100%
84 | 400kV Bhachau - Ranchodpura # 2 | 100% | 132 | 400/220 KV ICT # 2 / Shujalpur | 100%
85 | 400kV Mundra - Limbdi # 1 | 100% | 133 | 765/400KV ICT# 1 / Satna | 100%
86 | 400kV Mundra - Limbdi # 2 | 100% | 134 | 400/220 KV ICT # 2 / Navsari | 100%
87 | 765kV Satna - Bina # 1 | 100% | 135 | 400/220 KV ICT # 1 / Navsari | 100%
88 | 765kV Satna - Bina # 2 | 100% | 136 | 765/400KV ICT# 2 / Satna | 100%
89 | 765kV Bina - Indore | 100% | 137 | 765/400KV ICT# 1 / Bina | 100%
90 | 400kV Gandhar - Navsari # 2 | 100% | 138 | 400kV ICT#3/Vapi | 100%
91 | 400kV Gandhar - Navsari # 1 | 100% | 139 | 765/400KV ICT# 2 / Bina | 100%
92 | 400kV Mundra-Jetpur#1 | 100% | 140 | 765/400KV ICT# 1 / Gwalior | 100%
93 | 400kV Mundra-Jetpur#2 | 100% | 141 | 765/400KV ICT# 2 / Gwalior | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 | 100% | 142 | 765/400KV ICT# 2 / INDORE | 99.76%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 | 100% | 143 | Bus reactor / Dehgam | 100%
96 | 400kV V'chal (Pooling) - Sasan #1 | 100% | 144 | 25 MVAR reactor # 1 / Jabalpur | 100%
97 | 400k V'chal (Pooling) - Sasan # 2 | 100% | 145 | 25 MVAR reactor # 2 / Jabalpur | 100%
98 | 765kV Sasan - Satna # 1 | 100% | 146 | Bus reactor # 1 / Itarsi | 100%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 | 100% | 147 | Bus reactor # 2 / Itarsi | 100%
100 | 400kV Vapi-Navsari#1 | 100% | 148 | Bus Reactor # 3 / Itarsi | 100%
101 | 400kV Vapi-Navsari#2 | 100% | 149 | Bus Reactor # 3 / Jabalpur | 100%
102 | 765kV Sasan - Satna # 2 | 100% | 150 | Bus Reactor / Dhule | 100%
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 | 100% | 151 | Bus Reactor-I (50 MVAR) / Satna | 100%
104 | 400kV Indore (MP)-Indore (PG)#1 | 99.35% | 152 | Bus Reactor # 1 / Bina | 100%
105 | 400kV Indore (MP)-Indore (PG)#2 | 99.9% | 153 | Bus Reactor / Damoh | 100%
106 | 765 kV Gwalior -Agra # 1 | 100% | 154 | Bus Reactor / Gwalior | 100%
107 | 765 kV Gwalior -Agra # 2 | 100% | 155 | Bus Reactor / Khandwa | 100%
108 | 400/220kV ICT # 1 / Jabalpur. | 100% | 156 | Bus Reactor / Dehgam | 100%
109 | 400/220kV ICT # 2 /Jabalpur. | 100% | 157 | Bus Reactor / Bhachau | 100%
110 | 400/220 KV ICT # 1 / Dehgam | 100% | 158 | Bus Reactor / Shujalpur | 100%
111 | 400/220 KV ICT # 2/ Dehgam | 100% | 159 | Bus Reactor/ Rajgarh | 100%
112 | 400/220kV ICT # 1 / Satna | 100% | 160 | Bus Reactor / Satna 765KV | 100%
113 | 400/220kV ICT # 2 / Satna | 99.81% | 161 | Bus Reactor / Navsari | 100%
114 | 400/220kV ICT # 1 / Khandwa | 100% | 162 | Switchable Bina-I Line Reactor / Satna 765KV | 100%
115 | 400/220kV ICT # 2 / Khandwa | 100% | 163 | Switchable Bina-II Line Reactor / Satna 765KV | 100%
116 | 400/220kV ICT # 1 / Vapi | 100% | 164 | Bus Reactor-II (63 MVAR)/Satna | 100%
117 | 400/220kV ICT # 2 / Vapi | 100% | 165 | Switchable Bina-I Line Reactor / Gwalior 765KV | 100%
118 | 400/220kV ICT # 1 / Gwalior | 100% | 166 | Switchable Bina-II Line Reactor / Gwalior 765KV | 100%
119 | 400/220 KV ICT # 1 / Rajgarh | 100% | 167 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV | 100%
120 | 400/220kV ICT # 2 / Gwalior | 100% | 168 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV | 100%
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
Availability Bus Reactors =
System Availability :-
Note on B23: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B24: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B25: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B83: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B84: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## INDEX
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR SEPTEMBER-2013
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =30*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 720 | 79 | 2 | 0 | 158 | 113760 | 0 | 100 | 100% | 90%
2 | 400kV Itarsi-Indore # 1 | 2 | 4 |  |  | 2.0667 | 0 | 720 | 207 | 2 | 855.6 | 414 | 298080 | 0.0028704 | 99.713 | 99.71% | 90%
3 | 400kV Itarsi-Indore # 2 |  |  | 0 | 48 | 0 | 0.8 | 719.2 | 214 | 2 | 0 | 428 | 307817.6 | 0 | 100 | 100% | 90%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 720 | 289 | 2 | 0 | 578 | 416160 | 0 | 100 | 100% | 90%
5 | 400kV Indore-Asoj # 2 |  |  | 1 | 57 | 0 | 1.95 | 718.05 | 273 | 2 | 0 | 546 | 392055.3 | 0 | 100 | 100% | 90%
6 | 400 KV V'chal - Jabalpur # 1 | 0 | 10 | 1 | 24 | 0.16667 | 1.4 | 718.6 | 360 | 2 | 120 | 720 | 517392 | 0.00023193 | 99.9768 | 99.98% | 90%
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 720 | 360 | 2 | 0 | 720 | 518400 | 0 | 100 | 100% | 90%
8 | 400 KV Jabalpur - Itarsi # 1 | 0 | 59 |  |  | 0.98333 | 0 | 720 | 232 | 2 | 456.2667 | 464 | 334080 | 0.0013657 | 99.8634 | 99.86% | 90%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 720 | 232 | 2 | 0 | 464 | 334080 | 0 | 100 | 100% | 90%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 720 | 157 | 2 | 0 | 314 | 226080 | 0 | 100 | 100% | 90%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 720 | 157 | 2 | 0 | 314 | 226080 | 0 | 100 | 100% | 90%
12 | 400 KV Jabalpur-Sasan | 3 | 20 |  |  | 3.3333 | 0 | 720 | 376 | 2 | 2506.6667 | 752 | 541440 | 0.0046296 | 99.537 | 99.54% | 90%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 720 | 21 | 2 | 0 | 42 | 30240 | 0 | 100 | 100% | 90%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 720 | 389 | 2 | 0 | 778 | 560160 | 0 | 100 | 100% | 90%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 720 | 234 | 2 | 0 | 468 | 336960 | 0 | 100 | 100% | 90%
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 720 | 234 | 2 | 0 | 468 | 336960 | 0 | 100 | 100% | 90%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 720 | 196.64 | 2 | 0 | 393.28 | 283161.6 | 0 | 100 | 100% | 90%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 720 | 196.64 | 2 | 0 | 393.28 | 283161.6 | 0 | 100 | 100% | 90%
19 | 400 KV Khandwa - Dhule # 1 | 5 | 36 |  |  | 5.6 | 0 | 720 | 261.78 | 2 | 2931.936 | 523.56 | 376963.2 | 0.0077778 | 99.2222 | 99.22% | 90%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 720 | 261.78 | 2 | 0 | 523.56 | 376963.2 | 0 | 100 | 100% | 90%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 720 | 57 | 2 | 0 | 114 | 82080 | 0 | 100 | 100% | 90%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  |  |  | 0 | 0 | 720 | 110 | 2 | 0 | 220 | 158400 | 0 | 100 | 100% | 90%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 720 | 13 | 2 | 0 | 26 | 18720 | 0 | 100 | 100% | 90%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 720 | 13 | 1 | 0 | 13 | 9360 | 0 | 100 | 100% | 90%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 720 | 13 | 1 | 0 | 13 | 9360 | 0 | 100 | 100% | 90%
26 | 220kV Kawas-Navsari (GIS)#1 | 3 | 11 | 1 | 35 | 3.1833 | 1.5833 | 718.4167 | 58.149 | 1 | 185.1077 | 58.149 | 41775.2107 | 0.004431 | 99.5569 | 99.56% | 90%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  | 0 | 38 | 0 | 0.63333 | 719.3667 | 58.149 | 1 | 0 | 58.149 | 41830.4523 | 0 | 100 | 100% | 90%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 720 | 31.334 | 1 | 0 | 31.334 | 22560.48 | 0 | 100 | 100% | 90%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 48 | 29 |  |  | 48.4833 | 0 | 720 | 31.334 | 1 | 1519.1768 | 31.334 | 22560.48 | 0.067338 | 93.2662 | 93.27% | 90%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 720 | 37 | 1 | 0 | 37 | 26640 | 0 | 100 | 100% | 90%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 720 | 37 | 1 | 0 | 37 | 26640 | 0 | 100 | 100% | 90%
32 | 220kV Kawas - Haldarwa # 1 |  |  | 25 | 56 | 0 | 25.9333 | 694.0667 | 81 | 1 | 0 | 81 | 56219.4 | 0 | 100 | 100% | 90%
33 | 220kV Kawas-Haldarwa # 2 |  |  | 1 | 8 | 0 | 1.1333 | 718.8667 | 81 | 1 | 0 | 81 | 58228.2 | 0 | 100 | 100% | 90%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 720 | 74 | 1 | 0 | 74 | 53280 | 0 | 100 | 100% | 90%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 720 | 74 | 1 | 0 | 74 | 53280 | 0 | 100 | 100% | 90%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 720 | 43 | 1 | 0 | 43 | 30960 | 0 | 100 | 100% | 90%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 720 | 43 | 1 | 0 | 43 | 30960 | 0 | 100 | 100% | 90%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  | 0 | 47 | 0 | 0.78333 | 719.2167 | 117 | 1 | 0 | 117 | 84148.35 | 0 | 100 | 100% | 90%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 720 | 117 | 1 | 0 | 117 | 84240 | 0 | 100 | 100% | 90%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 720 | 267 | 2 | 0 | 534 | 384480 | 0 | 100 | 100% | 90%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 720 | 267 | 2 | 0 | 534 | 384480 | 0 | 100 | 100% | 90%
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 720 | 258.31 | 2 | 0 | 516.62 | 371966.4 | 0 | 100 | 100% | 90%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 720 | 100.32 | 2 | 0 | 200.64 | 144460.8 | 0 | 100 | 100% | 90%
44 | 400kV Nigrie-Satna |  |  |  |  | 0 | 0 | 720 | 161.11 | 2 | 0 | 322.22 | 231998.4 | 0 | 100 | 100% | 90%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 720 | 276 | 2 | 0 | 552 | 397440 | 0 | 100 | 100% | 90%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 720 | 276 | 2 | 0 | 552 | 397440 | 0 | 100 | 100% | 90%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 720 | 0.742 | 2 | 0 | 1.484 | 1068.48 | 0 | 100 | 100% | 90%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 720 | 0.742 | 2 | 0 | 1.484 | 1068.48 | 0 | 100 | 100% | 90%
49 | 765 kV Gwalior-Bina # 1 |  |  |  |  | 0 | 0 | 720 | 234.931 | 4 | 0 | 939.724 | 676601.28 | 0 | 100 | 100% | 90%
50 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 720 | 272.586 | 2 | 0 | 545.172 | 392523.84 | 0 | 100 | 100% | 90%
51 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 720 | 272.586 | 2 | 0 | 545.172 | 392523.84 | 0 | 100 | 100% | 90%
52 | 400KV Bina - Sujalpur # 1 | 4 | 34 |  |  | 4.5667 | 0 | 720 | 199.936 | 2 | 1826.0821 | 399.872 | 287907.84 | 0.0063426 | 99.3657 | 99.37% | 90%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 720 | 199.936 | 2 | 0 | 399.872 | 287907.84 | 0 | 100 | 100% | 90%
54 | 400KV Sujalpur - Nagda # 1 | 2 | 33 |  |  | 2.55 | 0 | 720 | 152.229 | 2 | 776.3679 | 304.458 | 219209.76 | 0.0035417 | 99.6458 | 99.65% | 90%
55 | 400KV Sujalpur - Nagda # 2 | 2 | 37 |  |  | 2.6167 | 0 | 720 | 152.229 | 2 | 796.6651 | 304.458 | 219209.76 | 0.0036343 | 99.6366 | 99.64% | 90%
56 | 400KV Nagda - Dehgam # 2 |  |  | 1 | 18 | 0 | 1.3 | 718.7 | 331.442 | 2 | 0 | 662.884 | 476414.7308 | 0 | 100 | 100% | 90%
57 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 720 | 331.442 | 2 | 0 | 662.884 | 477276.48 | 0 | 100 | 100% | 90%
58 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 719.8333 | 351.729 | 4 | 0 | 1406.916 | 1012745.034 | 0 | 100 | 100% | 90%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 720 | 351.729 | 4 | 0 | 1406.916 | 1012979.52 | 0 | 100 | 100% | 90%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 720 | 220.588 | 2 | 0 | 441.176 | 317646.72 | 0 | 100 | 100% | 90%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 65 | 65 | 0 | 66.0833 | 653.9167 | 4.01 | 2 | 0 | 8.02 | 5244.4117 | 0 | 100 | 100% | 90%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 78 | 5 | 0 | 78.0833 | 641.9167 | 4.01 | 2 | 0 | 8.02 | 5148.1717 | 0 | 100 | 100% | 90%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 720 | 4.12 | 2 | 0 | 8.24 | 5932.8 | 0 | 100 | 100% | 90%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 720 | 4.12 | 2 | 0 | 8.24 | 5932.8 | 0 | 100 | 100% | 90%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 720 | 220.588 | 2 | 0 | 441.176 | 317646.72 | 0 | 100 | 100% | 90%
66 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 720 | 25.71 | 1 | 0 | 25.71 | 18511.2 | 0 | 100 | 100% | 90%
67 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 720 | 25.71 | 1 | 0 | 25.71 | 18511.2 | 0 | 100 | 100% | 90%
68 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 720 | 29.66 | 1 | 0 | 29.66 | 21355.2 | 0 | 100 | 100% | 90%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 720 | 29.66 | 1 | 0 | 29.66 | 21355.2 | 0 | 100 | 100% | 90%
70 | 765 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 720 | 233.652 | 4 | 0 | 934.608 | 672917.76 | 0 | 100 | 100% | 90%
71 | 765 kV Seoni - Bina | 0 | 52 | 18 | 1 | 0.86667 | 18.0167 | 701.9833 | 292.45 | 4 | 1013.8267 | 1169.8 | 821180.1033 | 0.0012346 | 99.8765 | 99.88% | 90%
72 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 720 | 214.471 | 2 | 0 | 428.942 | 308838.24 | 0 | 100 | 100% | 90%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 720 | 213.8 | 2 | 0 | 427.6 | 307872 | 0 | 100 | 100% | 90%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 720 | 28.549 | 1 | 0 | 28.549 | 20555.28 | 0 | 100 | 100% | 90%
75 | 220 KV Vapi - Sayali |  |  |  |  | 0 | 0 | 720 | 18.3 | 1 | 0 | 18.3 | 13176 | 0 | 100 | 100% | 90%
76 | 220kV Sayali-Khadoli |  |  |  |  | 0 | 0 | 720 | 12.235 | 1 | 0 | 12.235 | 8809.2 | 0 | 100 | 100% | 90%
77 | 400kV Damoh-Birsinghpur#1 | 0 | 37 |  |  | 0.61667 | 0 | 720 | 228.474 | 2 | 281.7846 | 456.948 | 329002.56 | 0.00085648 | 99.9144 | 99.91% | 90%
78 | 400kV Damoh-Birsinghpur#2 | 1 | 37 |  |  | 1.6167 | 0 | 720 | 228.474 | 2 | 738.7326 | 456.948 | 329002.56 | 0.0022454 | 99.7755 | 99.78% | 90%
79 | 400kV Dehgam-Pirana#1 | 3 | 22 |  |  | 3.3667 | 0 | 720 | 46.67 | 2 | 314.2447 | 93.34 | 67204.8 | 0.0046759 | 99.5324 | 99.53% | 90%
80 | 400kV Dehgam-Pirana#2 | 2 | 5 |  |  | 2.0833 | 0 | 720 | 46.67 | 2 | 194.4583 | 93.34 | 67204.8 | 0.0028935 | 99.7106 | 99.71% | 90%
81 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 720 | 99.468 | 3 | 0 | 298.404 | 214850.88 | 0 | 100 | 100% | 90%
82 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 720 | 99.468 | 3 | 0 | 298.404 | 214850.88 | 0 | 100 | 100% | 90%
83 | 400kV Bhachau - Ranchodpura # 1 |  |  | 0 | 29 | 0 | 0.48333 | 719.5167 | 282.856 | 3 | 0 | 848.568 | 610558.8188 | 0 | 100 | 100% | 90%
84 | 400kV Bhachau - Ranchodpura # 2 |  |  | 1 | 30 | 0 | 1.5 | 718.5 | 282.856 | 3 | 0 | 848.568 | 609696.108 | 0 | 100 | 100% | 90%
85 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 720 | 314.053 | 3 | 0 | 942.159 | 678354.48 | 0 | 100 | 100% | 90%
86 | 400kV Mundra - Limbdi # 2 |  |  | 3 | 49 | 0 | 3.8167 | 716.1833 | 314.053 | 3 | 0 | 942.159 | 674758.5731 | 0 | 100 | 100% | 90%
87 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 720 | 274.164 | 4 | 0 | 1096.656 | 789592.32 | 0 | 100 | 100% | 90%
88 | 765kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 720 | 275.635 | 4 | 0 | 1102.54 | 793828.8 | 0 | 100 | 100% | 90%
89 | 765kV Bina - Indore |  |  | 8 | 28 | 0 | 8.4667 | 711.5333 | 311 | 4 | 0 | 1244 | 885147.4667 | 0 | 100 | 100% | 90%
90 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 720 | 102.152 | 2 | 0 | 204.304 | 147098.88 | 0 | 100 | 100% | 90%
91 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 720 | 102.152 | 2 | 0 | 204.304 | 147098.88 | 0 | 100 | 100% | 90%
92 | 400kV Mundra-Jetpur#1 |  |  |  |  | 0 | 0 | 720 | 337 | 3 | 0 | 1011 | 727920 | 0 | 100 | 100% | 90%
93 | 400kV Mundra-Jetpur#2 |  |  | 3 | 49 | 0 | 3.8167 | 716.1833 | 337 | 3 | 0 | 1011 | 724061.35 | 0 | 100 | 100% | 90%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 720 | 28.55 | 4 | 0 | 114.2 | 82224 | 0 | 100 | 100% | 90%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 720 | 28.55 | 4 | 0 | 114.2 | 82224 | 0 | 100 | 100% | 90%
96 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 720 | 5.443 | 2 | 0 | 10.886 | 7837.92 | 0 | 100 | 100% | 90%
97 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 720 | 5.443 | 2 | 0 | 10.886 | 7837.92 | 0 | 100 | 100% | 90%
98 | 765kV Sasan - Satna # 1 |  |  |  |  | 0 | 0 | 720 | 245.7 | 4 | 0 | 982.8 | 707616 | 0 | 100 | 100% | 90%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 720 | 0.8 | 2 | 0 | 1.6 | 1152 | 0 | 100 | 100% | 90%
100 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 720 | 116.85 | 2 | 0 | 233.7 | 168264 | 0 | 100 | 100% | 90%
101 | 400kV Vapi-Navsari#2 |  |  |  |  | 0 | 0 | 720 | 116.85 | 2 | 0 | 233.7 | 168264 | 0 | 100 | 100% | 90%
102 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 720 | 245.7 | 4 | 0 | 982.8 | 707616 | 0 | 100 | 100% | 90%
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 720 | 0.8 | 2 | 0 | 1.6 | 1152 | 0 | 100 | 100% | 90%
104 | 400kV Indore (MP)-Indore (PG)#1 | 4 | 39 |  |  | 4.65 | 0 | 720 | 49.7 | 4 | 924.42 | 198.8 | 143136 | 0.0064583 | 99.3542 | 99.35% | 90%
105 | 400kV Indore (MP)-Indore (PG)#2 | 0 | 42 |  |  | 0.7 | 0 | 720 | 49.7 | 4 | 139.16 | 198.8 | 143136 | 0.00097222 | 99.9028 | 99.9% | 90%
| Total Sr.No. 1 to 105 | 79 | 507 | 206 | 597 |  |  |  | 16435.669 |  | 15580.4958 |  | 28612264.5611
* | Lines charged with 400kV level
|  | 87.45 |  | 215.95
[10 empty] | NAFM | 0.00054454
Availability of ( Sl no 1 to 105) transmission lines during SEPTEMBER-2013 = | [9 empty] | TAFM | 99.9455
106 | 765 kV Gwalior -Agra # 1 |  |  | 0 | 0 | 0 | 0 | 720 | 129.435 | 4 | 0 | 517.74 | 372772.8 | 0 | 100 | 100% | 90%
107 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 127.934 | 4 | 0 | 511.736 | 368449.92 | 0 | 100 | 100% | 90%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =30*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
108 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
109 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
110 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
111 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
112 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
113 | 400/220kV ICT # 2 / Satna | 1 | 24 |  |  | 1.4 | 0 | 720 | 315 | 2.5 | 1102.5 | 787.5 | 567000 | 0.0019444 | 99.8056 | 99.81% | 90%
114 | 400/220kV ICT # 1 / Khandwa |  |  | 0 | 56 | 0 | 0.93333 | 719.0667 | 315 | 2.5 | 0 | 787.5 | 566265 | 0 | 100 | 100% | 90%
115 | 400/220kV ICT # 2 / Khandwa |  |  | 1 | 5 | 0 | 1.0833 | 718.9167 | 315 | 2.5 | 0 | 787.5 | 566146.875 | 0 | 100 | 100% | 90%
116 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
117 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
118 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
119 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
120 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
121 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
122 | 400/220kV ICT # 1 / Damoh | 0 | 58 |  |  | 0.96667 | 0 | 720 | 315 | 2.5 | 761.25 | 787.5 | 567000 | 0.0013426 | 99.8657 | 99.87% | 90%
123 | 400/220kV ICT # 2 / Damoh | 1 | 5 |  |  | 1.0833 | 0 | 720 | 315 | 2.5 | 853.125 | 787.5 | 567000 | 0.0015046 | 99.8495 | 99.85% | 90%
124 | 400/220 KV ICT # 2 / Rajgarh | 1 | 14 |  |  | 1.2333 | 0 | 720 | 315 | 2.5 | 971.25 | 787.5 | 567000 | 0.001713 | 99.8287 | 99.83% | 90%
125 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
126 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
127 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
128 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
129 | 400/220 KV ICT # 1 / Shujalpur | 1 | 13 |  |  | 1.2167 | 0 | 720 | 315 | 2.5 | 958.125 | 787.5 | 567000 | 0.0016898 | 99.831 | 99.83% | 90%
130 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
131 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
132 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
133 | 765/400KV ICT# 1 / Satna |  |  | 1 | 19 | 0 | 1.3167 | 718.6833 | 1000 | 2.5 | 0 | 2500 | 1796708.3333 | 0 | 100 | 100% | 90%
134 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
135 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
136 | 765/400KV ICT# 2 / Satna |  |  | 0 | 56 | 0 | 0.93333 | 719.0667 | 1000 | 2.5 | 0 | 2500 | 1797666.6667 | 0 | 100 | 100% | 90%
137 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 720 | 1000 | 2.5 | 0 | 2500 | 1800000 | 0 | 100 | 100% | 90%
138 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100% | 90%
139 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 720 | 1000 | 2.5 | 0 | 2500 | 1800000 | 0 | 100 | 100% | 90%
140 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100% | 90%
141 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100% | 90%
142 | 765/400KV ICT# 2 / INDORE | 1 | 44 |  |  | 1.7333 | 0 | 720 | 1500 | 2.5 | 6500 | 3750 | 2700000 | 0.0024074 | 99.7593 | 99.76% | 90%
| Total Sr.No. 1 to 35 | 5 | 158 | 2 | 136 |  |  |  | 17320 |  | 11146.25 |  | 31168786.875
|  | 7.6333 |  | 4.2667 | [5 empty] | NAFM | 0.00035761
Availability of 35 ( Sl no 1 to 35) ICTs in SEPTEMBER-2013 = | [9 empty] | TAFM | 99.9642
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =30*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
143 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
144 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 720 | 25 | 4 | 0 | 100 | 72000 | 0 | 100 | 100% | 90%
145 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 720 | 25 | 4 | 0 | 100 | 72000 | 0 | 100 | 100% | 90%
146 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90%
147 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90%
148 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90%
149 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
150 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 0 | 100 | 100% | 90%
151 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90%
152 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
153 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
154 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100% | 90%
155 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 720 | 125 | 4 | 0 | 500 | 360000 | 0 | 100 | 100% | 90%
156 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 720 | 125 | 4 | 0 | 500 | 360000 | 0 | 100 | 100% | 90%
157 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
158 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
159 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 720 | 125 | 4 | 0 | 500 | 360000 | 0 | 100 | 100% | 90%
160 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100% | 90%
161 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
162 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100% | 90%
163 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100% | 90%
164 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
165 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100% | 90%
166 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100% | 90%
167 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
168 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100% | 90%
| Total of sl no 1 to 26 | 0 | 0 | 0 | 0 |  |  |  | 2585 |  | 0 |  | 7444800
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 26 ( Sl no 1 to 26) Bus Reactors in SEPTEMBER-2013 = | [7 empty] | TAFM | 100
[11 empty] | 26726.7457 |  | 67225851.4361
[8 empty] | NAFM = | 0.00039757
% System Availability for SEPTEMBER-2013 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9602
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B136: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B137: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## Sept'13 Tripping details
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF September'2013
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | OUTAGE HOURS ATTRIBUTED TO | [11 empty] | Outage Category | Details | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM E | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
[8 empty] | ATTRIBUTED TO PGCIL |  | OTHERS | OTHERS |  | SYSTEM CONSTR. | SYSTEM CONSTR. |  | OUTAGE DEEMED AVAILABLE |  |  |  |  | TRIPPING | CHARGING
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  |  |  |  | A | B | C | D=A*B*C | 720 | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 |  | SATPURA-ITARSI 400kV |  |  |  |  | - | [5 empty] | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 79 | 2 | 0 | 0 | 720 | 158 | 113760 | 0 | 100%
2 | 909024 | ITARSI-INDORE I 400kV | 2013-09-05 | 14:34 | 2013-09-05 | 16:38 | 2:04 | 2 | 4 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC S/D for replacement of back up impedance relay at itarsi. | LD09/341
|  | SUBTOTAL |  |  |  |  | 0.086111 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 2.0667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 207 | 2 | 2.0667 | 855.6 | 720 | 414 | 298080 | 0.0028704 | 99.71%
3 | 909159 | ITARSI-INDORE II 400kV | 2013-09-30 | 18:33 | 2013-09-30 | 19:21 | - |  |  | 0.033333 | 0 | 47 | - |  |  | - |  |  | SBBU | LINE AUTO-TRIPPED DUE TO MALOPERATION OF BUS BAR AT INDORE(MPEB) |  | LD09/2322
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.033333 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.78333 |  |  | 0 |  |  | 0 |  |  |  |  | 214 | 2 | 0 | 0 | 719.2167 | 428 | 307824.7333 | 0 | 100%
4 | 909130 | INDORE-ASOJ I 400kV | 2013-09-25 | 23:42 | 2013-09-30 | 08:57 | - |  |  | - |  |  | - |  |  | 1900-01-03 09:15 | 105 | 14 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1982 | LD 09/2282
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 09:15 | 105 | 14
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 105.2333 |  |  |  |  | 289 | 2 | 0 | 0 | 720 | 578 | 416160 | 0 | 100%
5 | 909160 | INDORE-ASOJ II 400kV | 2013-09-30 | 18:33 | 2013-09-30 | 20:30 | - |  |  | 0.08125 | 1 | 56 | - |  |  | - |  |  | SBBU | LINE AUTO-TRIPPED DUE TO MALOPERATION OF BUS BAR AT INDORE(MPEB) |  | LD09/2325
| 909161 | INDORE-ASOJ II 400kV | 2013-09-30 | 20:30 |  |  | - |  |  | - |  |  | - |  |  | 0.14583 | 3 | 30 | LVRD | Line kept out on voltage regulation on WRLDC instruction | LD09/2327
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.08125 | 1 | 56 | 0 | 0 | 0 | 0.14583 | 3 | 30
|  | Element Availability= | [6 empty] | 0 |  |  | 1.9333 |  |  | 0 |  |  | 3.5 |  |  |  |  | 273 | 2 | 0 | 0 | 718.0667 | 546 | 392064.4 | 0 | 100%
6 | 909086 | VINDHYACHAL-JABALPUR I 400kV | 2013-09-19 | 13:16 | 2013-09-19 | 14:16 | - |  |  | 0.041667 | 1 | 0 | - |  |  | - |  |  | OMSU | S/D availed by NTPC to carry out PMU CT extension work. | LD09/1366 | LD09/1374
| 909134 | VINDHYACHAL-JABALPUR I 400kV | 2013-09-26 | 09:45 | 2013-09-26 | 09:55 | 0.0069444 | 0 | 10 | - |  |  | - |  |  | - |  |  | OMST | Line Auto triiped due to DT send from Jabalpur due to DC earth leakage.
| 909135 | VINDHYACHAL-JABALPUR I 400kV | 2013-09-26 | 09:55 | 2013-09-26 | 10:19 | - |  |  | 0.016667 | 0 | 23 | - |  |  | - |  |  | OMSU | Line charging delayed due to delay in charging at NTPC end. |  | LD09/2018
|  | SUBTOTAL |  |  |  |  | 0.0069444 | 0 | 10 | 0.058333 | 1 | 23 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.16667 |  |  | 1.3833 |  |  | 0 |  |  | 0 |  |  |  |  | 360 | 2 | 0.16667 | 120 | 718.6167 | 720 | 517404 | 0.00023193 | 99.98%
7 |  | VINDHYACHAL-JABALPUR II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 360 | 2 | 0 | 0 | 720 | 720 | 518400 | 0 | 100%
8 | 909003 | JABALPUR-ITARSI I 400kV | 2013-09-01 | 15:23 | 2013-09-01 | 16:22 | 0.040972 | 0 | 58 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC S/D for replacement of Reactor back up impedance relay at Itarsi S/S. | LD09/31 | LD09/35
|  | SUBTOTAL |  |  |  |  | 0.040972 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.96667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 232 | 2 | 0.96667 | 448.5333 | 720 | 464 | 334080 | 0.0013426 | 99.87%
9 | 909004 | JABALPUR-ITARSI II 400kV | 2013-09-02 | 06:01 | 2013-09-04 | 10:20 | - |  |  | - |  |  | - |  |  | 1900-01-01 04:19 | 52 | 18 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/68 | LD 09/244
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 04:19 | 52 | 18
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 52.3 |  |  |  |  | 232 | 2 | 0 | 0 | 720 | 464 | 334080 | 0 | 100%
10 |  | GANDHAR-DEHGAM I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 720 | 314 | 226080 | 0 | 100%
11 |  | GANDHAR-DEHGAM II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 720 | 314 | 226080 | 0 | 100%
12 | 909013 | SASAN-JABALPUR 400kV | 2013-09-03 | 13:07 | 2013-09-03 | 16:27 | 0.13889 | 3 | 20 | - |  |  | - |  |  | - |  |  | OMST | Line H/T to avail S/D to attend Hot Spot at Loc no: 310 | LD09/184 | LD09/192
|  | SUBTOTAL |  |  |  |  | 0.13889 | 3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.3333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 376 | 2 | 3.3333 | 2506.6667 | 720 | 752 | 541440 | 0.0046296 | 99.54%
13 |  | 400kV Sasan-Vindhyachal
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21 | 2 | 0 | 0 | 720 | 42 | 30240 | 0 | 100%
14 |  | VINDHYACHAL-JABALPUR IV 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 389 | 2 | 0 | 0 | 720 | 778 | 560160 | 0 | 100%
15 | 909025 | JABALPUR-ITARSI III 400kV | 2013-09-05 | 15:57 | 2013-09-14 | 18:12 | - |  |  | - |  |  | - |  |  | 1900-01-08 02:15 | 218 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/349
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 02:15 | 218 | 15
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 218.25 |  |  |  |  | 234 | 2 | 0 | 0 | 720 | 468 | 336960 | 0 | 100%
16 | 908103 | JABALPUR-ITARSI IV 400kV | 2013-08-26 | 01:36 | 2013-09-02 | 05:57 | - |  |  | - |  |  | - |  |  | 1899-12-31 05:57 | 29 | 57 | LVRD | Line kept out on V/R on WRLDC instruction | LD08/1853 | LD09/65
| 909021 | JABALPUR-ITARSI IV 400kV | 2013-09-04 | 14:22 | 2013-09-05 | 15:52 | - |  |  | - |  |  | - |  |  | 1899-12-31 01:30 | 25 | 30 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/275 | LD 09/346
| 909095 | JABALPUR-ITARSI IV 400kV | 2013-09-20 | 16:06 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-09 07:54 | 247 | 54 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD09/1485
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-11 15:21 | 301 | 141
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 303.35 |  |  |  |  | 234 | 2 | 0 | 0 | 720 | 468 | 336960 | 0 | 100%
17 | 909008 | ITARSI-KHANDWA I 400kV | 2013-09-02 | 23:57 | 2013-09-03 | 08:16 | - |  |  | - |  |  | - |  |  | 0.34653 | 8 | 19 | LVRD | Line kept out on V/R on WRLDC instruction | LD09/142 | LD 08/155
| 909035 | ITARSI-KHANDWA I 400kV | 2013-09-10 | 23:07 | 2013-09-12 | 12:22 | - |  |  | - |  |  | - |  |  | 1899-12-31 13:15 | 37 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/715
| 909054 | ITARSI-KHANDWA I 400kV | 2013-09-14 | 00:05 | 2013-09-26 | 10:15 | - |  |  | - |  |  | - |  |  | 1900-01-11 10:10 | 298 | 10 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/955 | LD 09/2016
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-13 07:44 | 343 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 343.7333 |  |  |  |  | 196.64 | 2 | 0 | 0 | 720 | 393.28 | 283161.6 | 0 | 100%
18 | 908111 | ITARSI-KHANDWA II 400kV | 2013-08-28 | 17:03 | 2013-09-02 | 11:05 | - |  |  | - |  |  | - |  |  | 1899-12-31 11:05 | 35 | 5 | LVRD | Line kept out on V/R on WRLDC instruction | LD08/2051 | LD 09/846
| 909015 | ITARSI-KHANDWA II 400kV | 2013-09-03 | 23:02 | 2013-09-07 | 0.4125 | - |  |  | - |  |  | - |  |  | 1900-01-02 10:52 | 82 | 51 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/215 | LD 09/467
| 909137 | ITARSI-KHANDWA II 400kV | 2013-09-26 | 21:54 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-03 02:06 | 98 | 6 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2060
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 00:03 | 215 | 62
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 216.0333 |  |  |  |  | 196.64 | 2 | 0 | 0 | 720 | 393.28 | 283161.6 | 0 | 100%
19 | 909051 | KHANDWA-DHULE I 400kV | 2013-09-13 | 14:31 | 2013-09-14 | 16:38 | 0.23333 | 5 | 36 | - |  |  | - |  |  | 0.75 | 18 | 0 | LHWT | Line A/T on R ph to E/F due to flashover at loc no: 878(WR-I portion). Line restoration got delayed due to continuous rains & poor visibility at site Hence outage from 1600hrs/13.09.2013 to 1000/14.09.2013 may not be attributable to POWERGRID(F/L- 195.1Km from Khandwa, WR-I jurisdiction). |  | LD 09/991
|  | SUBTOTAL |  |  |  |  | 0.23333 | 5 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 18 | 0
|  | Element Availability= | [6 empty] | 5.6 |  |  | 0 |  |  | 0 |  |  | 18 |  |  |  |  | 261.78 | 2 | 5.6 | 2931.936 | 720 | 523.56 | 376963.2 | 0.0077778 | 99.22%
20 |  | KHANDWA-DHULE II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 261.78 | 2 | 0 | 0 | 720 | 523.56 | 376963.2 | 0 | 100%
21 |  | JHANOR - SUGEN 400kV | [17 empty] | Line H/T for power regulation on WRLDC Instruction | LD 08/524 | LD 08/539
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 57 | 2 | 0 | 0 | 720 | 114 | 82080 | 0 | 100%
22 |  | SUGEN-VAPI 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 110 | 2 | 0 | 0 | 720 | 220 | 158400 | 0 | 100%
23 |  | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 2 | 0 | 0 | 720 | 26 | 18720 | 0 | 100%
24 |  | JHANOR - HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 720 | 13 | 9360 | 0 | 100%
25 |  | JHANOR - HALDARWA II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 720 | 13 | 9360 | 0 | 100%
26 | 909014 | KAWAS-NAVSARI (PG GIS) I 220kV | 2013-09-03 | 14:45 | 2013-09-03 | 17:56 | 0.13264 | 3 | 10 | - |  |  | - |  |  | - |  |  | OMST | Line H/T to avail emergency S/D to attend Hot Spot . | LD09/190 | LD09/203
| 909043 | KAWAS-NAVSARI (PG GIS) I 220kV | 2013-09-11 | 20:53 | 2013-09-11 | 21:08 | - |  |  | - |  |  | 0.010417 | 0 | 15 | - |  |  | LNCC | Line A/T on R ph to E/F during severe lightning and thunderstrome(F/L: 36 km from navsari(GIS),13km from Kawas). |  | LD09/793
| 909057 | KAWAS-NAVSARI (PG GIS) I 220kV | 2013-09-14 | 12:21 | 2013-09-14 | 13:14 | - |  |  | 0.036806 | 0 | 53 | - |  |  | - |  |  | OMSU | A/T on D/T received from Kawas NTPC due to PLCC problem. |  | LD 09/981
| 909058 | KAWAS-NAVSARI (PG GIS) I 220kV | 2013-09-14 | 15:10 | 2013-09-14 | 15:37 | - |  |  | - |  |  | 0.01875 | 0 | 26 | - |  |  | LNCC | A/T on B-ph to E/F during severe lightning and thunderstrome. |  | LD 09/992
|  | SUBTOTAL |  |  |  |  | 0.13264 | 3 | 10 | 0.036806 | 0 | 53 | 0.029167 | 0 | 41 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.1667 |  |  | 0.88333 |  |  | 0.68333 |  |  | 0 |  |  |  |  | 58.149 | 1 | 3.1667 | 184.1385 | 718.4333 | 58.149 | 41776.1799 | 0.0044077 | 99.56%
27 | 909052 | KAWAS-NAVSARI II 220kV | 2013-09-13 | 16:37 | 2013-09-13 | 17:15 | - |  |  | - |  |  | 0.026389 | 0 | 37 | - |  |  | LNCC | Line A/T on R ph to E/F during severe lightning and thunderstrome (FL-11.22Km from Navsari) |  | LD09/935
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.026389 | 0 | 37 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.61667 |  |  | 0 |  |  |  |  | 58.149 | 1 | 0 | 0 | 719.3833 | 58.149 | 41831.4215 | 0 | 100%
28 |  | NAVSARI (PG GIS)-NAVSARI I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 31.334 | 1 | 0 | 0 | 720 | 31.334 | 22560.48 | 0 | 100%
29 | 909005 | NAVSARI(PG)-NAVSARI(GETCO) II 220kV | 2013-09-02 | 11:38 | 2013-09-04 | 0.50486 | 1900-01-01 00:29 | 48 | 29 | - |  |  | - |  |  | - |  |  | OSPT | To avail OCC S/D for attend SF6 Gas leakage. | LD09/97 | LD 09/256
|  | SUBTOTAL |  |  |  |  | 1900-01-01 00:29 | 48 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 48.4833 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 31.334 | 1 | 48.4833 | 1519.1768 | 720 | 31.334 | 22560.48 | 0.067338 | 93.27%
30 | 909046 | KAWAS-VAV I 220kV | 2013-09-12 | 12:55 | 2013-09-12 | 15:22 | - |  |  | - |  |  | - |  |  | 0.10208 | 2 | 26 | LPRD | Line H/T for Power regulation on WRLDC Instruction | LD 09/841 | LD 09/846
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10208 | 2 | 26
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 2.4333 |  |  |  |  | 37 | 1 | 0 | 0 | 720 | 37 | 26640 | 0 | 100%
31 | 909047 | KAWAS-VAV II 220kV | 2013-09-12 | 12:58 | 2013-09-12 | 15:23 | - |  |  | - |  |  | - |  |  | 0.10069 | 2 | 25 | LPRD | Line H/T for Power regulation on WRLDC Instruction | LD 09/841 | LD 09/846
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10069 | 2 | 25
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 2.4167 |  |  |  |  | 37 | 1 | 0 | 0 | 720 | 37 | 26640 | 0 | 100%
32 | 909038 | KAWAS-HALDARWA I 220kV | 2013-09-11 | 10:30 | 2013-09-11 | 21:22 | - |  |  | - |  |  | - |  |  | 0.45278 | 10 | 51 | OSPD | Line H/T to avail OCC S/D by GETCO for bay maintenance | LD09/738 | LD09/791
| 909059 | KAWAS-HALDARWA I 220kV | 2013-09-14 | 20:11 | 2013-09-14 | 21:41 | - |  |  | 0.0625 | 1 | 30 | - |  |  | - |  |  | OMSU | A/T on B-ph to E/F due to some problem at Kawas NTPC (F/L-86.77kM from HAL) . Fault Jurisdication is beyond Line Length. |  | LD 09/1010
| 909127 | KAWAS-HALDARWA I 220kV | 2013-09-25 | 09:20 | 2013-09-26 | 09:46 | - |  |  | - |  |  | 1899-12-31 00:26 | 24 | 26 | - |  |  | LNCC | Line H/T due to Heavy rain and flood at Hardarwa S/S | LD 09/1902 | LD 09/2004
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.0625 | 1 | 30 | 1899-12-31 00:26 | 24 | 26 | 0.45278 | 10 | 51
|  | Element Availability= | [6 empty] | 0 |  |  | 1.5 |  |  | 24.4333 |  |  | 10.85 |  |  |  |  | 81 | 1 | 0 | 0 | 694.0667 | 81 | 56219.4 | 0 | 100%
33 | 909050 | KAWAS-HALDARWA II 220kV | 2013-09-13 | 11:28 | 2013-09-13 | 20:39 | - |  |  | - |  |  | - |  |  | 0.38264 | 9 | 11 | OSPD | To avail OCC approved outage by GETCO for Bay equipments works | LD09/913
| 909060 | KAWAS-HALDARWA II 220kV | 2013-09-14 | 20:11 | 2013-09-14 | 21:19 | - |  |  | 0.047222 | 1 | 8 | - |  |  | - |  |  | OMSU | A/T on B-ph to E/F due to some problem at Kawas NTPC (F/L- 92.34kM from HAL) . Fault Jurisdication is beyond Line Length. |  | LD 09/1008
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.047222 | 1 | 8 | 0 | 0 | 0 | 0.38264 | 9 | 11
|  | Element Availability= | [6 empty] | 0 |  |  | 1.1333 |  |  | 0 |  |  | 9.1833 |  |  |  |  | 81 | 1 | 0 | 0 | 718.8667 | 81 | 58228.2 | 0 | 100%
34 |  | KAKRAPAR-HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 0 | 0 | 720 | 74 | 53280 | 0 | 100%
35 |  | KAKRAPAR-HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 0 | 0 | 720 | 74 | 53280 | 0 | 100%
36 |  | KAKRAPAR-VAV I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 43 | 1 | 0 | 0 | 720 | 43 | 30960 | 0 | 100%
37 |  | KAKRAPAR-VAV II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 43 | 1 | 0 | 0 | 720 | 43 | 30960 | 0 | 100%
38 | 909071 | KAKRAPAR-VAPI I 220kV | 2013-09-17 | 08:45 | 2013-09-17 | 09:32 | - |  |  | 0.032639 | 0 | 46 | - |  |  | - |  |  | OMSU | Line H/T for testing of relay at Vapi(GETCO) with breaker operation. | LD09/1175 | LD09/1182
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.032639 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.76667 |  |  | 0 |  |  | 0 |  |  |  |  | 117 | 1 | 0 | 0 | 719.2333 | 117 | 84150.3 | 0 | 100%
39 |  | KAKRAPAR-VAPI II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 117 | 1 | 0 | 0 | 720 | 117 | 84240 | 0 | 100%
40 |  | VINDHYACHAL-SATNA I 400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 720 | 534 | 384480 | 0 | 100%
41 |  | VINDHYACHAL-SATNA II 400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 720 | 534 | 384480 | 0 | 100%
42 |  | VINDHYACHAL-SATNA III 400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 258.31 | 2 | 0 | 0 | 720 | 516.62 | 371966.4 | 0 | 100%
43 |  | VINDHYACHAL-NIGRIE 400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 100.32 | 2 | 0 | 0 | 720 | 200.64 | 144460.8 | 0 | 100%
44 |  | NIGRIE-SATNA 400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 161.11 | 2 | 0 | 0 | 720 | 322.22 | 231998.4 | 0 | 100%
45 |  | SATNA-BINA(PG ) I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 276 | 2 | 0 | 0 | 720 | 552 | 397440 | 0 | 100%
46 |  | SATNA-BINA(PG ) II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 276 | 2 | 0 | 0 | 720 | 552 | 397440 | 0 | 100%
47 |  | BINA(PG)-BINA(MPEB) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 720 | 1.484 | 1068.48 | 0 | 100%
48 |  | BINA(PG)-BINA(MPEB) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 720 | 1.484 | 1068.48 | 0 | 100%
49 |  | GWALIOR-BINA I 765KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 234.931 | 4 | 0 | 0 | 720 | 939.724 | 676601.28 | 0 | 100%
50 | 909113 | SATNA-BINA(PG) IV 400kV | 2013-09-23 | 12:01 | 2013-09-25 | 11:41 | - |  |  | - |  |  | - |  |  | 1899-12-31 23:40 | 47 | 39 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1720 | LD 09/1905
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 23:40 | 47 | 39
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 47.65 |  |  |  |  | 272.586 | 2 | 0 | 0 | 720 | 545.172 | 392523.84 | 0 | 100%
51 | 909040 | SATNA-BINA(PG) III 400kV | 2013-09-11 | 13:42 | 2013-09-11 | 17:02 | - |  |  | - |  |  | - |  |  | 0.13889 | 3 | 20 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/758 | LD09/770
| 909107 | SATNA-BINA(PG) III 400kV | 2013-09-22 | 09:52 | 2013-09-23 | 11:10 | - |  |  | - |  |  | - |  |  | 1899-12-31 01:18 | 25 | 18 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1626 | LD 09/1715
| 909138 | SATNA-BINA(PG) III 400kV | 2013-09-27 | 00:22 | 2013-09-30 | 06:36 | - |  |  | - |  |  | - |  |  | 1900-01-02 06:14 | 78 | 14 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2067 | LD 09/2272
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 10:52 | 106 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 106.8667 |  |  |  |  | 272.586 | 2 | 0 | 0 | 720 | 545.172 | 392523.84 | 0 | 100%
52 | 909009 | BINA-SHUJALPUR I 400kV | 2013-09-03 | 00:01 | 2013-09-03 | 08:41 | - |  |  | - |  |  | - |  |  | 0.36111 | 8 | 39 | LVRD | Line kept out on V/R on WRLDC instruction | LD09/141 | LD 08/154
| 909016 | BINA-SHUJALPUR I 400kV | 2013-09-03 | 23:09 | 2013-09-04 | 0.35069 | - |  |  | - |  |  | - |  |  | 0.38611 | 9 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/216 | LD 09/234
| 909031 | BINA-SHUJALPUR I 400kV | 2013-09-10 | 11:28 | 2013-09-10 | 16:02 | 0.19028 | 4 | 34 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC S/D for modification in A/R logic | LD09/657 | LD09/683
| 909037 | BINA-SHUJALPUR I 400kV | 2013-09-11 | 01:15 | 2013-09-11 | 07:40 | - |  |  | - |  |  | - |  |  | 0.26736 | 6 | 24 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/723 | LD09/732
| 909045 | BINA-SHUJALPUR I 400kV | 2013-09-12 | 00:47 | 2013-09-12 | 07:43 | - |  |  | - |  |  | - |  |  | 0.28889 | 6 | 56 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/802 | LD 09/812
| 909061 | BINA-SHUJALPUR I 400kV | 2013-09-15 | 12:14 | 2013-09-16 | 07:04 | - |  |  | - |  |  | - |  |  | 0.78472 | 18 | 49 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1032 | LD09/1077
| 909088 | BINA-SHUJALPUR I 400kV | 2013-09-19 | 21:51 | 2013-09-20 | 07:46 | - |  |  | - |  |  | - |  |  | 0.41319 | 9 | 55 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD09/1410 | LD09/1433
| 909108 | BINA-SHUJALPUR I 400kV | 2013-09-22 | 16:13 | 2013-09-23 | 09:24 | - |  |  | - |  |  | - |  |  | 0.71597 | 17 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1651 | LD 09/1700
| 909123 | BINA-SHUJALPUR I 400kV | 2013-09-25 | 02:28 | 2013-09-27 | 07:58 | - |  |  | - |  |  | - |  |  | 1900-01-01 05:30 | 53 | 29 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1881 | LD 09/2076
| 909146 | BINA-SHUJALPUR I 400kV | 2013-09-27 | 21:43 | 2013-09-29 | 10:50 | - |  |  | - |  |  | - |  |  | 1899-12-31 13:07 | 37 | 6 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2128 | LD 09/2235
|  | SUBTOTAL |  |  |  |  | 0.19028 | 4 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-05 23:50 | 163 | 284
|  | Element Availability= | [6 empty] | 4.5667 |  |  | 0 |  |  | 0 |  |  | 167.7333 |  |  |  |  | 199.936 | 2 | 4.5667 | 1826.0821 | 720 | 399.872 | 287907.84 | 0.0063426 | 99.37%
53 | 909039 | BINA-SHUJALPUR II 400kV | 2013-09-11 | 13:17 | 2013-09-11 | 18:19 | - |  |  | - |  |  | - |  |  | 0.20972 | 5 | 1 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/755 | LD09/773
| 909048 | BINA-SHUJALPUR II 400kV | 2013-09-13 | 03:47 | 2013-09-14 | 10:03 | - |  |  | - |  |  | - |  |  | 1899-12-31 06:16 | 30 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/891 | LD 09/966
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 11:18 | 35 | 16
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 35.2667 |  |  |  |  | 199.936 | 2 | 0 | 0 | 720 | 399.872 | 287907.84 | 0 | 100%
54 | 909062 | SHUJALPUR-NAGDA I 400kV | 2013-09-15 | 16:02 | 2013-09-15 | 18:35 | 0.10625 | 2 | 32 | - |  |  | - |  |  | - |  |  | OSPT | LINE H/T TO AVAIL S/D FOR MODIFICATION IN AUTORECLOSE LOGIC AT SHUJALPUR. S/D RETURNED AT 18:35 HRS | LD09/1043
| 909066 | SHUJALPUR-NAGDA I 400kV | 2013-09-15 | 18:35 | 2013-09-16 | 06:53 | - |  |  | - |  |  | - |  |  | 0.5125 | 12 | 18 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD09/1060 | LD09/1076
| 909112 | SHUJALPUR-NAGDA I 400kV | 2013-09-23 | 01:17 | 2013-09-23 | 09:54 | - |  |  | - |  |  | - |  |  | 0.35903 | 8 | 36 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1684 | LD 09/1705
| 909125 | SHUJALPUR-NAGDA I 400kV | 2013-09-25 | 04:05 | 2013-09-27 | 09:42 | - |  |  | - |  |  | - |  |  | 1900-01-01 05:37 | 53 | 36 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD/09/1882 | LD 09/2086
|  | SUBTOTAL |  |  |  |  | 0.10625 | 2 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-02 02:32 | 73 | 90
|  | Element Availability= | [6 empty] | 2.5333 |  |  | 0 |  |  | 0 |  |  | 74.5 |  |  |  |  | 152.229 | 2 | 2.5333 | 771.2936 | 720 | 304.458 | 219209.76 | 0.0035185 | 99.65%
55 | 909069 | SHUJALPUR-NAGDA II 400kV | 2013-09-16 | 16:13 | 2013-09-16 | 18:50 | 0.10903 | 2 | 36 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC Approved S/D for modification in A/R logic at Shujalpur end. | LD09/1129 | LD09/1145
| 909118 | SHUJALPUR-NAGDA II 400kV | 2013-09-24 | 00:49 | 2013-09-24 | 09:10 | - |  |  | - |  |  | - |  |  | 0.34792 | 8 | 20 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1770 | LD 09/1795
|  | SUBTOTAL |  |  |  |  | 0.10903 | 2 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34792 | 8 | 20
|  | Element Availability= | [6 empty] | 2.6 |  |  | 0 |  |  | 0 |  |  | 8.3333 |  |  |  |  | 152.229 | 2 | 2.6 | 791.5908 | 720 | 304.458 | 219209.76 | 0.0036111 | 99.64%
56 | 909011 | NAGDA-DEHGAM II 400kV | 2013-09-03 | 12:07 | 2013-09-03 | 13:00 | - |  |  | 0.036806 | 0 | 52 | - |  |  | - |  |  | OMSU | A/T due to receipt of D/T from Nagda MPPTCL end. |  | LD09/182
| 909105 | NAGDA-DEHGAM II 400kV | 2013-09-21 | 18:42 | 2013-09-21 | 18:42 | 0 | 0 | 0 | - |  |  | - |  |  | - |  |  | LART | A/R successfully on R-ph to E/F, F/L - 61km from dehgam only but A/T at Nagda (MPPTCL) end.
| 909106 | NAGDA-DEHGAM II 400kV | 2013-09-21 | 18:42 | 2013-09-21 | 19:07 | - |  |  | 0.017361 | 0 | 24 | - |  |  | - |  |  | OMSU | A/R unsuccessful at Nagda (MPPTCL) end only on R ph to Earth fault. |  | LD 09/1594
| 909115 | NAGDA-DEHGAM II 400kV | 2013-09-23 | 23:37 | 2013-09-24 | 08:05 | - |  |  | - |  |  | - |  |  | 0.35278 | 8 | 28 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1766 | LD 09/1786
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.054167 | 0 | 76 | 0 | 0 | 0 | 0.35278 | 8 | 28
|  | Element Availability= | [6 empty] | 0 |  |  | 1.2667 |  |  | 0 |  |  | 8.4667 |  |  |  |  | 331.442 | 2 | 0 | 0 | 718.7333 | 662.884 | 476436.8269 | 0 | 100%
57 | 909110 | NAGDA-DEHGAM I 400KV | 2013-09-23 | 00:13 | 2013-09-23 | 10:53 | - |  |  | - |  |  | - |  |  | 0.44444 | 10 | 40 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1679 | LD 09/1626
| 909122 | NAGDA-DEHGAM I 400KV | 2013-09-25 | 00:15 | 2013-09-25 | 09:26 | - |  |  | - |  |  | - |  |  | 0.38264 | 9 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1877 | LD 09/1897
| 909132 | NAGDA-DEHGAM I 400KV | 2013-09-26 | 02:52 | 2013-09-26 | 09:38 | - |  |  | - |  |  | - |  |  | 0.28194 | 6 | 46 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1993 | LD09/2006
| 909156 | NAGDA-DEHGAM I 400KV | 2013-09-30 | 03:50 | 2013-09-30 | 06:08 | - |  |  | - |  |  | - |  |  | 0.095833 | 2 | 18 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2267 | LD09/2270
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 04:55 | 27 | 115
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 28.9167 |  |  |  |  | 331.442 | 2 | 0 | 0 | 720 | 662.884 | 477276.48 | 0 | 100%
58 | 909102 | SEONI-KHANDWA I 400kV | 2013-09-21 | 13:03 | 2013-09-21 | 19:14 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | 0.25069 | 6 | 1 | GOVC | A/T on operation of O/V protection at Khandwa end. |  | LD 09/1595
| 909111 | SEONI-KHANDWA I 400kV | 2013-09-23 | 01:17 | 2013-09-23 | 10:09 | - |  |  | - |  |  | - |  |  | 0.36944 | 8 | 52 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1683 | LD 09/1701
| 909131 | SEONI-KHANDWA I 400kV | 2013-09-25 | 23:59 | 2013-09-26 | 09:37 | - |  |  | - |  |  | - |  |  | 0.40139 | 9 | 37 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1985 | LD09/2007
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069444 | 0 | 10 | 1899-12-31 00:31 | 23 | 90
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 24.5 |  |  |  |  | 351.729 | 4 | 0 | 0 | 719.8333 | 1406.916 | 1012745.034 | 0 | 100%
59 | 909117 | SEONI-KHANDWA II 400kV | 2013-09-24 | 00:45 | 2013-09-24 | 08:12 | - |  |  | - |  |  | - |  |  | 0.31042 | 7 | 27 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1771 | LD 09/1789
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31042 | 7 | 27
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.45 |  |  |  |  | 351.729 | 4 | 0 | 0 | 720 | 1406.916 | 1012979.52 | 0 | 100%
60 | 908122 | KHANDWA-RAJGARH II 400kV | 2013-08-31 | 00:54 | 2013-09-02 | 12:45 | - |  |  | - |  |  | - |  |  | 1899-12-31 12:45 | 36 | 45 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 08/2226 | LD 09/99
| 909007 | KHANDWA-RAJGARH II 400kV | 2013-09-02 | 17:34 | 2013-09-07 | 0.43194 | - |  |  | - |  |  | - |  |  | 1900-01-03 16:48 | 112 | 47 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/120 | LD 09/474
| 909036 | KHANDWA-RAJGARH II 400kV | 2013-09-11 | 00:23 | 2013-09-13 | 13:45 | - |  |  | - |  |  | - |  |  | 1900-01-01 13:22 | 61 | 21 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/720 | LD09/925
| 909067 | KHANDWA-RAJGARH II 400kV | 2013-09-16 | 02:05 | 2013-09-20 | 07:17 | - |  |  | - |  |  | - |  |  | 1900-01-03 05:12 | 101 | 12 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD09/1073 | LD 09/1433
| 909103 | KHANDWA-RAJGARH II 400kV | 2013-09-21 | 13:08 | 2013-09-27 | 09:55 | - |  |  | - |  |  | - |  |  | 1900-01-04 20:47 | 140 | 46 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1563 | LD 09/2083
| 909147 | KHANDWA-RAJGARH II 400kV | 2013-09-27 | 21:42 | 2013-09-30 | 06:25 | - |  |  | - |  |  | - |  |  | 1900-01-01 08:43 | 56 | 42 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2129 | LD 09/2271
| 909158 | KHANDWA-RAJGARH II 400kV | 2013-09-30 | 12:16 |  |  | - |  |  | - |  |  | - |  |  | 0.48889 | 11 | 44 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/2296
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-20 17:21 | 517 | 257
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 521.2833 |  |  |  |  | 220.588 | 2 | 0 | 0 | 720 | 441.176 | 317646.72 | 0 | 100%
61 | 908110 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-08-27 | 19:05 | 2013-09-13 | 08:51 | - |  |  | - |  |  | - |  |  | 1900-01-11 08:51 | 296 | 51 | LVRD | After completion of work by Powergrid Line kept out for voltage regulation on WRLDC instruction. | LD08/1987 | LD09/899
| 909053 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-09-13 | 18:04 | 2013-09-16 | 13:44 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | 1900-01-01 19:30 | 67 | 30 | GOVC | Line A/T on O/V stage-I operated at Rajgarh end. |  | LD 09/1123
| 909070 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-09-17 | 08:35 | 2013-09-17 | 08:35 | - |  |  | 0 | 0 | 0 | - |  |  | - |  |  | OMSU | Line A/R successfully on Bph to E/F (FL-82.9km from SSP & 84 km from Rajgarh). Fault section lies beyong the Jourisdiction of POWERGRID.
| 909074 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-09-17 | 20:42 | 2013-09-20 | 14:37 | - |  |  | 1900-01-01 17:55 | 65 | 54 | - |  |  | - |  |  | OMSU | Line A/T on R Ph to E/F (F/L-116km from Rajgarh and 43km from SSP). Fault lies beyond the jurisdiction of POWERGRID. |  | LD 09/1469
| 909098 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-09-20 | 23:04 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-09 00:56 | 240 | 56 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD09/1514
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 17:55 | 65 | 54 | 0.0069444 | 0 | 10 | 1900-01-24 05:17 | 603 | 137
|  | Element Availability= | [6 empty] | 0 |  |  | 65.9 |  |  | 0.16667 |  |  | 605.2833 |  |  |  |  | 4.01 | 2 | 0 | 0 | 653.9333 | 8.02 | 5244.5453 | 0 | 100%
62 | 909034 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-09-10 | 16:38 | 2013-09-10 | 16:38 | - |  |  | 0 |  |  | - |  |  | - |  |  | OMSU | Line A/R successfully at both ends on Y ph to E/F.(F/L:117km from SSP)
| 909064 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-09-15 | 18:02 | 2013-09-18 | 10:06 | - |  |  | - |  |  | 1900-01-01 16:04 | 64 | 3 | - |  |  | GOVC | Line A/T on O/V stage-I operated at Rajgarh end. |  | LD 09/1252
| 909075 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-09-18 | 10:10 | 2013-09-19 | 00:11 | - |  |  | 0.58403 | 14 | 1 | - |  |  | - |  |  | OMSU | Line A/T on Y Ph to E/F (F/L-120km from Rajgarh,44.9km from SSP). Fault lies beyond the jurisdiction of POWERGRID |  | LD09/1309
| 909081 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-09-19 | 04:35 | 2013-09-19 | 04:35 | - |  |  | 0 |  |  | - |  |  | - |  |  | OMSU | Line A/R successfully from both ends on B ph to E/F,76km from rajgarh,75.2km from SSP,F/C:2.9kA(Raj),F/C:3.372kA(SSP)
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.58403 | 14 | 1 | 1900-01-01 16:04 | 64 | 3 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 14.0167 |  |  | 64.05 |  |  | 0 |  |  |  |  | 4.01 | 2 | 0 | 0 | 641.9333 | 8.02 | 5148.3053 | 0 | 100%
63 | 908120 | RAJGARH-NAGDA I 400kV (LILO) | 2013-08-30 | 18:09 | 2013-09-26 | 10:37 | - |  |  | - |  |  | - |  |  | 1900-01-24 10:37 | 610 | 37 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 08/2207 | LD 09/2015
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-24 10:37 | 610 | 37
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 610.6167 |  |  |  |  | 4.12 | 2 | 0 | 0 | 720 | 8.24 | 5932.8 | 0 | 100%
64 | 909136 | RAJGARH-NAGDA II 400kV (LILO) | 2013-09-26 | 12:22 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-03 11:38 | 107 | 38 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2035
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 11:38 | 107 | 38
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 107.6333 |  |  |  |  | 4.12 | 2 | 0 | 0 | 720 | 8.24 | 5932.8 | 0 | 100%
65 | 908118 | KHANDWA-RAJGARH I 400kV | 2013-08-30 | 13:07 | 2013-09-02 | 11:29 | - |  |  | - |  |  | - |  |  | 1899-12-31 11:29 | 35 | 29 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 08/2187 | LD 09/93
| 909006 | KHANDWA-RAJGARH I 400kV | 2013-09-02 | 16:04 | 2013-09-04 | 0.44444 | - |  |  | - |  |  | - |  |  | 1899-12-31 18:36 | 42 | 36 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/113 | LD 09/249
| 909022 | KHANDWA-RAJGARH I 400kV | 2013-09-04 | 21:48 | 2013-09-11 | 07:16 | - |  |  | - |  |  | - |  |  | 1900-01-05 09:28 | 153 | 27 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/304 | LD 09/731
| 909044 | KHANDWA-RAJGARH I 400kV | 2013-09-12 | 00:40 | 2013-09-12 | 13:12 | - |  |  | - |  |  | - |  |  | 0.52222 | 12 | 31 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/800 | LD09/840
| 909055 | KHANDWA-RAJGARH I 400kV | 2013-09-14 | 01:40 | 2013-09-14 | 08:49 | - |  |  | - |  |  | - |  |  | 0.29792 | 7 | 8 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/958 | LD 09/964
| 909065 | KHANDWA-RAJGARH I 400kV | 2013-09-15 | 18:10 | 2013-09-16 | 09:57 | - |  |  | - |  |  | - |  |  | 0.65764 | 15 | 46 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1051 | LD 09/1093
| 909087 | KHANDWA-RAJGARH I 400kV | 2013-09-19 | 21:44 | 2013-09-27 | 09:51 | - |  |  | - |  |  | - |  |  | 1900-01-06 12:07 | 180 | 7 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD09/1411 | LD 09/2083
| 909142 | KHANDWA-RAJGARH I 400kV | 2013-09-27 | 12:03 | 2013-09-29 | 09:55 | - |  |  | - |  |  | - |  |  | 1899-12-31 21:52 | 45 | 52 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2100 | LD 09/2234
| 909154 | KHANDWA-RAJGARH I 400kV | 2013-09-29 | 21:29 |  |  | - |  |  | - |  |  | - |  |  | 1899-12-31 02:31 | 26 | 31 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2254
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-20 15:31 | 515 | 267
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 519.45 |  |  |  |  | 220.588 | 2 | 0 | 0 | 720 | 441.176 | 317646.72 | 0 | 100%
66 |  | VAPI-MAGARWADA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 720 | 25.71 | 18511.2 | 0 | 100%
67 |  | VAPI-MAGARWADA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 720 | 25.71 | 18511.2 | 0 | 100%
68 |  | VAPI-KHARADPARA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 720 | 29.66 | 21355.2 | 0 | 100%
69 |  | VAPI-KHARADPARA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 720 | 29.66 | 21355.2 | 0 | 100%
70 |  | GWALIOR-BINA II 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 233.652 | 4 | 0 | 0 | 720 | 934.608 | 672917.76 | 0 | 100%
71 | 909029 | SEONI-BINA 765kV | 2013-09-07 | 10:35 | 2013-09-07 | 11:27 | 0.036111 | 0 | 52 | - |  |  | - |  |  | - |  |  | OSFT | H/T to avail emergency S/D by WRTS # 1 for attending hot spot at Seoni SS. | WRLD09/476NLDC/42 | LD 09/481 LD09/43
| 909056 | SEONI-BINA 765kV | 2013-09-14 | 09:35 | 2013-09-14 | 21:12 | - |  |  | 0.48403 | 11 | 36 | - |  |  | - |  |  | OMSU | H/T to avail S/D by WRTS # 1 for isolator alignment at Seoni (WR-I). | LD 09/965 LD 09/90 | LD 09/1006
| 909153 | SEONI-BINA 765kV | 2013-09-29 | 12:14 | 2013-09-29 | 18:38 | - |  |  | 0.26667 | 6 | 23 | - |  |  | - |  |  | OMSU | Line H/T to Avail Emergency S/D by WRTS - I for attending Hot Spot at Seoni end. | WR 09/2240 NLD 09/233 | WR 09/2250 NLD 09/238
|  | SUBTOTAL |  |  |  |  | 0.036111 | 0 | 52 | 0.75069 | 17 | 59 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.86667 |  |  | 17.9833 |  |  | 0 |  |  | 0 |  |  |  |  | 292.45 | 4 | 0.86667 | 1013.8267 | 702.0167 | 1169.8 | 821219.0967 | 0.0012345 | 99.88%
72 | 909104 | DAMOH-BHOPAL I 400KV | 2013-09-21 | 13:30 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-08 10:30 | 226 | 30 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1564
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 10:30 | 226 | 30
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 226.5 |  |  |  |  | 241.471 | 2 | 0 | 0 | 720 | 482.942 | 347718.24 | 0 | 100%
73 | 908115 | DAMOH-BHOPAL II 400KV | 2013-08-29 | 11:02 | 2013-09-20 | 12:19 | - |  |  | - |  |  | - |  |  | 1900-01-18 12:19 | 468 | 19 | LVRD | Line kept out on V/R on WRLDC instruction | LD 08/2099 | LD 09/1457
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-18 12:19 | 468 | 19
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 468.3167 |  |  |  |  | 213.8 | 2 | 0 | 0 | 720 | 427.6 | 307872 | 0 | 100%
74 |  | VAPI-KHADOLI I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.549 | 1 | 0 | 0 | 720 | 28.549 | 20555.28 | 0 | 100%
75 |  | VAPI-SAYALI 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 18.3 | 1 | 0 | 0 | 720 | 18.3 | 13176 | 0 | 100%
76 |  | SAYALI-KHADOLI 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 12.235 | 1 | 0 | 0 | 720 | 12.235 | 8809.2 | 0 | 100%
77 | 909063 | DAMOH-BIRSINGHPUR I 400kV | 2013-09-15 | 16:22 | 2013-09-15 | 16:59 | 0.025694 | 0 | 37 | - |  |  | - |  |  | - |  |  | LEFT | LINE A/T DUE TO Y PH TO E/F(FL-69.5KM FROM DAMOH) |  | LD09/1046
|  | SUBTOTAL |  |  |  |  | 0.025694 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.61667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 228.474 | 2 | 0.61667 | 281.7846 | 720 | 456.948 | 329002.56 | 0.00085648 | 99.91%
78 | 909032 | DAMOH-BIRSINGHPUR II 400kV | 2013-09-10 | 11:56 | 2013-09-10 | 13:33 | 0.067361 | 1 | 37 | - |  |  | - |  |  | - |  |  | OMST | Line H/T to take out L/R at Damoh end because of High moisture content.Line was ready for charging without L/R at damoh at 13:33Hrs/10.09.13 | LD09/665 | LD09/671
| 909033 | DAMOH-BIRSINGHPUR II 400kV | 2013-09-10 | 13:33 | 2013-09-20 | 01:35 | - |  |  | - |  |  | - |  |  | 1900-01-08 12:02 | 228 | 1 | LVRD | Line test charged from Birsingpur end at 13:33 but the line A/T on O/V at Damoh.subsequently the line was kept out on V/R vide code LD/09/676 |  | LD 09/422
|  | SUBTOTAL |  |  |  |  | 0.067361 | 1 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 12:02 | 228 | 1
|  | Element Availability= | [6 empty] | 1.6167 |  |  | 0 |  |  | 0 |  |  | 228.0167 |  |  |  |  | 228.474 | 2 | 1.6167 | 738.7326 | 720 | 456.948 | 329002.56 | 0.0022454 | 99.78%
79 | 909076 | DEHGAM PIRANA I 400kV | 2013-09-18 | 11:22 | 2013-09-18 | 14:44 | 0.14028 | 3 | 21 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC S/D for modification in A/R logic in BCU at Pirana | LD09/1261 | LD09/1271
|  | SUBTOTAL |  |  |  |  | 0.14028 | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.35 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 3.35 | 312.689 | 720 | 93.34 | 67204.8 | 0.0046528 | 99.53%
80 | 909083 | DEHGAM PIRANA II 400kV | 2013-09-19 | 09:33 | 2013-09-19 | 11:38 | 0.086806 | 2 | 4 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC S/D for modification in A/R logic in BCU at Pirana | LD09/1337 | LD09/1356
|  | SUBTOTAL |  |  |  |  | 0.086806 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 2.0667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 2.0667 | 192.9027 | 720 | 93.34 | 67204.8 | 0.0028704 | 99.71%
81 | 909068 | MUNDRA-BHACHAU I 400kV | 2013-09-16 | 12:11 | 2013-09-16 | 19:11 | - |  |  | - |  |  | - |  |  | 0.29167 | 6 | 59 | OSFD | Line H/T to avail Emergency S/D by CGPL for attending Hot Spot in Line Isolator at CGPL S/Y | LD09/1110 | LD09/1147
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29167 | 6 | 59
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.9833 |  |  |  |  | 99.468 | 3 | 0 | 0 | 720 | 298.404 | 214850.88 | 0 | 100%
82 | 909077 | MUNDRA-BHACHAU II 400kV | 2013-09-18 | 14:00 | 2013-09-18 | 20:54 | - |  |  | - |  |  | - |  |  | 0.2875 | 6 | 53 | OSFD | Line H/T to avail emergency S/D to attend hot spot in B ph line ISOL by CGPL | LD09/1268 | LD09/1300
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2875 | 6 | 53
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.8833 |  |  |  |  | 99.468 | 3 | 0 | 0 | 720 | 298.404 | 214850.88 | 0 | 100%
83 | 909084 | BHACHAU-RANCHODPURA I 400kV | 2013-09-19 | 11:19 | 2013-09-19 | 11:40 | - |  |  | 0.014583 | 0 | 20 | - |  |  | - |  |  | OMSU | To avail OCC approved S/D for collection of oil sample of Line Reactor Bushing at Ranchodpura (GETCO) end. | LD09/1350
| 909090 | BHACHAU-RANCHODPURA I 400kV | 2013-09-20 | 10:41 | 2013-09-20 | 10:49 | - |  |  | 0.0055556 | 0 | 7 | - |  |  | - |  |  | OMSU | Line H/T to take Line Reactor into service. | LD09/1453 | LD09/1455
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.020139 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.45 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0 | 0 | 719.55 | 848.568 | 610587.1044 | 0 | 100%
84 | 909091 | BHACHAU-RANCHODPURA II 400kV | 2013-09-20 | 10:41 | 2013-09-20 | 11:52 | - |  |  | 0.049306 | 1 | 10 | - |  |  | - |  |  | OMSU | Line H/T to take Line Reactor Bushing oil sample. | LD09/1456 | LD09/1461
| 909096 | BHACHAU-RANCHODPURA II 400kV | 2013-09-20 | 19:41 | 2013-09-20 | 20:00 | - |  |  | 0.013194 | 0 | 18 | - |  |  | - |  |  | OMSU | Line H/T to take Line Reactor into service at Ranchodpura end. | LD09/1502 | LD09/1508
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.0625 | 1 | 28 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 1.1667 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0 | 0 | 718.8333 | 848.568 | 609978.964 | 0 | 100%
85 | 909145 | MUNDRA-LIMBDI I 400kV | 2013-09-27 | 16:25 | 2013-09-27 | 19:12 | - |  |  | - |  |  | - |  |  | 0.11597 | 2 | 46 | OSFD | Line H/T to avail S/D by GETCO for attending hot spot at Limbdi (GETCO) end. | LD09/2109 | LD09/2125
| 909151 | MUNDRA-LIMBDI I 400kV | 2013-09-28 | 17:10 | 2013-09-29 | 01:05 | - |  |  | - |  |  | - |  |  | 0.32986 | 7 | 54 | OSFD | Line H/T to avail S/D by Getco for attending Hot Spot in Bus#2 Isolator at Limbdi (GETCO) S/S. | LD09/2189
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44583 | 9 | 100
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.6667 |  |  |  |  | 314.053 | 3 | 0 | 0 | 720 | 942.159 | 678354.48 | 0 | 100%
86 | 909133 | MUNDRA-LIMBDI II 400kV | 2013-09-26 | 08:17 | 2013-09-26 | 12:06 | - |  |  | 0.15903 | 3 | 49 | - |  |  | - |  |  | SBBU | Line Auto tripped due to Bus fault at Limbdi S/S( GETCO ). |  | LD09/2029
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.15903 | 3 | 49 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 3.8167 |  |  | 0 |  |  | 0 |  |  |  |  | 314.053 | 3 | 0 | 0 | 716.1833 | 942.159 | 674758.5731 | 0 | 100%
87 | 909041 | SATNA-BINA(PG ) I 765kV | 2013-09-11 | 16:13 | 2013-09-23 | 13:24 | - |  |  | - |  |  | - |  |  | 1900-01-10 21:11 | 285 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/768 | WR 09/1723 NLD 09/164
| 909144 | SATNA-BINA(PG ) I 765kV | 2013-09-27 | 15:07 | 2013-09-29 | 11:36 | - |  |  | - |  |  | - |  |  | 1899-12-31 20:29 | 44 | 28 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 09/2108 NLD 09/208 | WR 09/2232 NLD 09/231
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-12 17:40 | 329 | 39
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 329.65 |  |  |  |  | 274.164 | 4 | 0 | 0 | 720 | 1096.656 | 789592.32 | 0 | 100%
88 | 907142 | SATNA-BINA(PG ) II 765kV | 2013-07-30 | 13:37 | 2013-09-11 | 15:57 | - |  |  | - |  |  | - |  |  | 1900-01-09 15:57 | 255 | 57 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 07/2131 ,213 | WR 09/754 NLD 09/67
| 909114 | SATNA-BINA(PG ) II 765kV | 2013-09-23 | 13:36 | 2013-09-27 | 14:34 | - |  |  | - |  |  | - |  |  | 1900-01-03 00:58 | 96 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 09/1732 NLD 09/165 | WR 09/2105 NLD 09/207
| 909155 | SATNA-BINA(PG ) II 765kV | 2013-09-30 | 01:05 |  |  | - |  |  | - |  |  | - |  |  | 0.95486 | 22 | 55 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 09/2262 NLD 09/241
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-14 15:50 | 373 | 170
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 375.8333 |  |  |  |  | 275.635 | 4 | 0 | 0 | 720 | 1102.54 | 793828.8 | 0 | 100%
89 | 909001 | BINA-INDORE 765 KV | 2013-09-01 | 00:52 | 2013-09-03 | 11:48 | - |  |  | - |  |  | - |  |  | 1900-01-01 10:56 | 58 | 56 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 08/2299 | WR09/171 NLD 09/111
| 909017 | BINA-INDORE 765 KV | 2013-09-04 | 03:20 | 2013-09-04 | 11:20 | - |  |  | - |  |  | - |  |  | 0.33333 | 7 | 59 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/226 NLDC-17 | WR 09/247 NLD 09/19
| 909019 | BINA-INDORE 765 KV | 2013-09-04 | 12:59 | 2013-09-04 | 13:09 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V stage - I at Indore. | LD09/265
| 909020 | BINA-INDORE 765 KV | 2013-09-04 | 13:09 | 2013-09-11 | 10:34 | - |  |  | - |  |  | - |  |  | 1900-01-05 21:25 | 165 | 24 | LVRD | Line kept out on Voltage Regulation on WRLDC instruction. |  | LD09/739
| 909042 | BINA-INDORE 765 KV | 2013-09-11 | 16:51 | 2013-09-16 | 11:58 | - |  |  | - |  |  | - |  |  | 1900-01-03 19:07 | 115 | 7 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/772 | WR 09/1103 NLD 09/102
| 909072 | BINA-INDORE 765 KV | 2013-09-17 | 17:58 | 2013-09-17 | 19:44 | - |  |  | - |  |  | - |  |  | 0.073611 | 1 | 45 | LPRD | Line H/T on power regulation to facilitate S/D on 765/400kV ICT #2 at Indore. | LD09/1214 | LD09/1219
| 909080 | BINA-INDORE 765 KV | 2013-09-18 | 18:21 | 2013-09-19 | 15:05 | - |  |  | - |  |  | - |  |  | 0.86389 | 20 | 44 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1292 | WR 09/1371 NLD 09/138
| 909092 | BINA-INDORE 765 KV | 2013-09-20 | 13:02 | 2013-09-20 | 13:32 | - |  |  | - |  |  | 0.020833 | 0 | 29 | - |  |  | GOVC | Line A/T on operation of O/V stage-I |  | WR 09/1472 NLD 09/143
| 909097 | BINA-INDORE 765 KV | 2013-09-20 | 22:06 | 2013-09-21 | 10:49 | - |  |  | - |  |  | - |  |  | 0.52986 | 12 | 43 | LVRD | Line kept out on V/R as per WRLDC Instruction. | WR 09/1512 NLD 09/146 | WR 09/1550 NLD 09/151
| 909099 | BINA-INDORE 765 KV | 2013-09-21 | 12:02 | 2013-09-21 | 12:12 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | A/T on operation of O/V protection at Indore end.
| 909101 | BINA-INDORE 765 KV | 2013-09-21 | 12:12 | 2013-09-23 | 22:32 | - |  |  | - |  |  | - |  |  | 1900-01-01 10:20 | 58 | 19 | LVRD | Line kept out on V/R as per WRLDC Instruction. |  | WR 09/1762 NLD 09/170
| 909119 | BINA-INDORE 765 KV | 2013-09-24 | 02:32 | 2013-09-24 | 09:45 | - |  |  | - |  |  | 0.30069 | 7 | 12 | - |  |  | GOVC | Line A/T on O/V and subsequently kept out on V/R as per WRLDC Instruction. |  | LD 09/1796
| 909124 | BINA-INDORE 765 KV | 2013-09-25 | 04:02 | 2013-09-25 | 04:12 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V protection at Indore.
| 909126 | BINA-INDORE 765 KV | 2013-09-25 | 04:12 | 2013-09-25 | 08:59 | - |  |  | - |  |  | - |  |  | 0.19931 | 4 | 46 | LVRD | After Tripping on O/V line kept out for volatge regulation on WRLDC Instruction | LD 09/1885 | LD09/1891
| 909128 | BINA-INDORE 765 KV | 2013-09-25 | 12:59 | 2013-09-25 | 13:04 | - |  |  | - |  |  | 0.0034722 | 0 | 4 | - |  |  | GOVC | Line A/T on Operation of Operation of O/V stage - I at Indore end.
| 909129 | BINA-INDORE 765 KV | 2013-09-25 | 13:04 | 2013-09-28 | 15:01 | - |  |  | - |  |  | - |  |  | 1900-01-02 01:57 | 73 | 57 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1928 | LD 09/2171
| 909149 | BINA-INDORE 765 KV | 2013-09-28 | 17:02 | 2013-09-28 | 17:12 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V Stage-I at Indore and kept out on V/R as per WRLDC instructions | LD09/2203
| 909152 | BINA-INDORE 765 KV | 2013-09-29 | 17:12 |  |  | - |  |  | - |  |  | - |  |  | 1899-12-31 06:48 | 30 | 48 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2203
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.35278 | 7 | 85 | 1900-01-21 22:33 | 543 | 448
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 8.4167 |  |  | 550.4667 |  |  |  |  | 311 | 4 | 0 | 0 | 711.5833 | 1244 | 885209.6667 | 0 | 100%
90 |  | GANDHAR-NAVSARI (PG) II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 102.152 | 2 | 0 | 0 | 720 | 204.304 | 147098.88 | 0 | 100%
91 |  | GANDHAR-NAVSARI (PG) I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 102.152 | 2 | 0 | 0 | 720 | 204.304 | 147098.88 | 0 | 100%
92 |  | MUNDRA-JETPUR II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337 | 3 | 0 | 0 | 720 | 1011 | 727920 | 0 | 100%
93 | 908126 | MUNDRA-JETPUR II 400kV | 2013-08-31 | 18:15 | 2013-09-01 | 00:21 | - |  |  | - |  |  | - |  |  | 0.014583 | 0 | 21 | LPRD | Line kept out on power regulation due to over load in ICT at jetpur end | - | LD 08/2294
| 909002 | MUNDRA-JETPUR II 400kV | 2013-09-01 | 10:18 | 2013-09-01 | 17:38 | - |  |  | - |  |  | - |  |  | 0.30556 | 7 | 19 | LCSD | Line H/T to avail emergency S/d for replacement of insulators | LD09/21 | LD09/37
| 909100 | MUNDRA-JETPUR II 400kV | 2013-09-21 | 12:02 | 2013-09-21 | 12:17 | - |  |  | 0.010417 | 0 | 15 | - |  |  | - |  |  | SRMU | A/T due relay mal-operation at Mundra (CGPL) end. |  | LD 09/1559
| 909139 | MUNDRA-JETPUR II 400kV | 2013-09-27 | 03:11 | 2013-09-27 | 07:33 | - |  |  | - |  |  | - |  |  | 0.18194 | 4 | 21 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2075 | LD09/2077
| 909140 | MUNDRA-JETPUR II 400kV | 2013-09-27 | 07:36 | 2013-09-27 | 11:11 | - |  |  | - |  |  | 0.14931 | 3 | 34 | - |  |  | LNCC | Line A/T on Y ph to E during severe rains and thunderstrome.Charging delayed by Mundra end. |  | LD09/2096
| 909150 | MUNDRA-JETPUR II 400kV | 2013-09-28 | 16:29 | 2013-09-28 | 16:39 | - |  |  | - |  |  | - |  |  | 0.0069444 | 0 | 10 | OSFD | Line H/T to avail S/D by CGPL for charging of Main Bay | LD09/2184 | LD09/2187
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.010417 | 0 | 15 | 0.14931 | 3 | 34 | 0.50903 | 11 | 71
|  | Element Availability= | [6 empty] | 0 |  |  | 0.25 |  |  | 3.5667 |  |  | 12.1833 |  |  |  |  | 337 | 3 | 0 | 0 | 716.1833 | 1011 | 724061.35 | 0 | 100%
94 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 720 | 114.2 | 82224 | 0 | 100%
95 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 720 | 114.2 | 82224 | 0 | 100%
96 |  | VINDHYACHAL (NTPC) -SASAN (RELIANCE) I 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 720 | 10.886 | 7837.92 | 0 | 100%
97 |  | VINDHYACHAL (NTPC) -SASAN (RELIANCE) II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 720 | 10.886 | 7837.92 | 0 | 100%
98 | 908112 | SASAN-SATNA I 765kV | 2013-08-28 | 18:41 | 2013-09-06 | 22:18 | - |  |  | - |  |  | - |  |  | 1900-01-04 22:18 | 142 | 18 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WRLD08/2055NLDC/242 | WR 09/449 NLD 09/38
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-04 22:18 | 142 | 18
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 142.3 |  |  |  |  | 245.7 | 4 | 0 | 0 | 720 | 982.8 | 707616 | 0 | 100%
99 |  | BINA(PG)-BINA(MPEB) III 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.8 | 2 | 0 | 0 | 720 | 1.6 | 1152 | 0 | 100%
100 |  | VAPI - NAVASARI (GIS) I 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 720 | 233.7 | 168264 | 0 | 100%
101 |  | VAPI - NAVASARI (GIS) II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 720 | 233.7 | 168264 | 0 | 100%
102 | 909028 | SASAN-SATNA II 765kV | 2013-09-06 | 22:27 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-23 01:33 | 142 | 33 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/452 LD 09/39
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-23 01:33 | 142 | 33
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 142.55 |  |  |  |  | 245.7 | 4 | 0 | 0 | 720 | 982.8 | 707616 | 0 | 100%
103 |  | BINA(PG)-BINA(MPEB) IV 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.8 | 2 | 0 | 0 | 720 | 1.6 | 1152 | 0 | 100%
104 | 909109 | INDORE (PG) - INDORE ( MPPTCL) I 400kV | 2013-09-22 | 19:16 | 2013-09-22 | 23:55 | 0.19375 | 4 | 39 | - |  |  | - |  |  | - |  |  | SBBT | Line A/T due E/S closed of R and B ph in charged condition at Indore (PG ) end. |  | LD 09/1678
| 909116 | INDORE (PG) - INDORE ( MPPTCL) I 400kV | 2013-09-24 | 00:25 | 2013-09-24 | 11:40 | - |  |  | - |  |  | - |  |  | 0.46875 | 11 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1769 | LD 09/1815
| 909121 | INDORE (PG) - INDORE ( MPPTCL) I 400kV | 2013-09-25 | 00:05 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-04 23:55 | 143 | 55 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1876
|  | SUBTOTAL |  |  |  |  | 0.19375 | 4 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-05 11:10 | 154 | 70
|  | Element Availability= | [6 empty] | 4.65 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 49.7 | 4 | 4.65 | 924.42 | 720 | 198.8 | 143136 | 0.0064583 | 99.35%
105 | 909120 | Indore (PG) - Indore ( MPPTCL) - II 400kV | 2013-09-24 | 11:22 | 2013-09-24 | 12:04 | 0.029167 | 0 | 42 | - |  |  | - |  |  | - |  |  | LEFT | Line A/T on R ph to E/F. |  | LD09/1818
|  | SUBTOTAL |  |  |  |  | 0.029167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.7 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 49.7 | 4 | 0.7 | 139.16 | 720 | 198.8 | 143136 | 0.00097222 | 99.9%
[20 empty] | TRANSMISSION LINE AVAILABILITY | [5 empty] | 15558.5333 |  |  | 28651611.3812
0.00054302
99.95%
106 | 909018 | AGRA-GWALIOR I 765 KV | 2013-09-04 | 07:31 | 2013-09-04 | 19:03 | - |  |  | - |  |  | - |  |  | 0.48056 | 11 | 31 | LCSD | Line H/T to avail S/D by NRTS - I for Construction work | WR 09/230 NLD 09/18 NR 08/156
| 909023 | AGRA-GWALIOR I 765 KV | 2013-09-05 | 07:24 | 2013-09-05 | 18:52 | - |  |  | - |  |  | - |  |  | 0.47778 | 11 | 28 | LCSD | Line H/T to avail S/D by NRTS - I for Construction work.( for erection of main bay equipments of Fatehpur#2 at agra)) | WR 09/316 NR 09/198 NLD 09/25 | WR 09/365 NR 09/233 NLD 09/31
| 909026 | AGRA-GWALIOR I 765 KV | 2013-09-06 | 07:44 | 2013-09-06 | 18:33 | - |  |  | - |  |  | - |  |  | 0.45069 | 10 | 48 | LCSD | Line H/T to avail S/D by NRTS - I for Construction work( for erection of main bay equipments of Fatehpur#2 at agra) | WR 09/390 NR 09/248 NLD 09/33 | WR 09/435 NR 09/281 NLD 09/34
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 09:49 | 32 | 107
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.5167 |  |  |  |  | 129.435 | 4 | 0 | 0 | 720 | 517.74 | 372772.8 | 0 | 100%
107 | 909082 | AGRA-GWALIOR II 765KV | 2013-09-19 | 07:23 | 2013-09-19 | 19:01 | - |  |  | - |  |  | - |  |  | 0.48472 | 11 | 38 | LCSD | Line H/T to avail OCC Approved S/D by NRTS-I for Stringing of Agra - Fatehpur Line | WR 09/1326 NLD 09/136 NR 09/1091 | WR 09/1400 NLD 09/141 NR 09/1132
| 909089 | AGRA-GWALIOR II 765KV | 2013-09-20 | 07:35 | 2013-09-20 | 18:57 | - |  |  | - |  |  | - |  |  | 0.47361 | 11 | 22 | LCSD | Line H/T to avail OCC Approved S/D by NRTS-I for Stringing of Agra - Fatehpur Line. | WR 09/1436 NLD 09/142 NR 09/1148 | WR 09/1499 NLD 09/144 NR 09/1197
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95833 | 22 | 60
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.6333 |  |  |  |  | 127.934 | 4 | 0 | 0 | 720 | 511.736 | 368449.92 | 0 | 100%
ICTs
1 |  | ICT1 JABALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
2 |  | ICT2 JABALPUR 400/220/33kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
3 |  | ICT1 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
4 |  | ICT2 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
5 |  | ICT1 SATNA 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
6 | 909049 | ICT2 SATNA 400/220KV | 2013-09-13 | 10:21 | 2013-09-13 | 11:45 | 0.058333 | 1 | 24 | - |  |  | - |  |  | - |  |  | OSPT | To avail OCC approved S/D For AMP works | LD09/909 | LD09/917
|  | SUBTOTAL |  |  |  |  | 0.058333 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.4 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 1.4 | 1102.5 | 720 | 787.5 | 567000 | 0.0019444 | 99.81%
7 | 909093 | ICT1 KHANDWA 400/220kV | 2013-09-20 | 13:05 | 2013-09-20 | 14:01 | - |  |  | - |  |  | 0.038889 | 0 | 55 | - |  |  | GOLC | ICT auto tripped due to operation of B/U over current Relay. |  | LD09/1477
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.038889 | 0 | 55 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.91667 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 719.0833 | 787.5 | 566278.125 | 0 | 100%
8 | 909094 | ICT2 KHANDWA 400/220kV | 2013-09-20 | 13:05 | 2013-09-20 | 14:10 | - |  |  | - |  |  | 0.045139 | 1 | 5 | - |  |  | GOLC | ICT auto tripped due to operation of over loading Relay. |  | LD09/1479
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.045139 | 1 | 5 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 1.0833 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 718.9167 | 787.5 | 566146.875 | 0 | 100%
9 |  | ICT1 VAPI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
10 |  | ICT2 VAPI 400/220/33kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
11 |  | ICT1 GWALIOR 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
12 |  | ICT1 RAJGARH 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
13 |  | ICT2 GWALIOR 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
14 |  | ICT ITARSI 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
15 | 909141 | ICT1 DAMOH 400/220kV | 2013-09-27 | 11:57 | 2013-09-27 | 12:55 | 0.040278 | 0 | 58 | - |  |  | - |  |  | - |  |  | OSFT | ICT# I H/T to attend Bushing oil leakage and for taking Oil sample of Bushing. | LD09/2094 | LD09/2102
|  | SUBTOTAL |  |  |  |  | 0.040278 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.96667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0.96667 | 761.25 | 720 | 787.5 | 567000 | 0.0013426 | 99.87%
16 | 909148 | ICT2 DAMOH 400/220kV | 2013-09-28 | 13:00 | 2013-09-28 | 14:05 | 0.045139 | 1 | 5 | - |  |  | - |  |  | - |  |  | OSFT | ICT H/T to avail S/D for collection of oil sample of Bushing | LD09/2168 | LD09/2176
|  | SUBTOTAL |  |  |  |  | 0.045139 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.0833 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 1.0833 | 853.125 | 720 | 787.5 | 567000 | 0.0015046 | 99.85%
17 | 909027 | ICT2 RAJGARH 400/220KV | 2013-09-06 | 13:21 | 2013-09-06 | 14:35 | 0.051389 | 1 | 14 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail S/D for taking oil sample of Bushings. | LD 09/411 | LD09/414
|  | SUBTOTAL |  |  |  |  | 0.051389 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.2333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 1.2333 | 971.25 | 720 | 787.5 | 567000 | 0.001713 | 99.83%
18 |  | ICT1 BINA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
19 |  | ICT1 PIRANA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
20 |  | ICT2 PIRANA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
21 |  | ICT3 GWALIOR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
22 | 909085 | ICT1 SHUJALPUR 400/220/33kV | 2013-09-19 | 12:21 | 2013-09-19 | 13:34 | 0.050694 | 1 | 13 | - |  |  | - |  |  | - |  |  | OSPT | To avail OCC approved S/D for AMP works at Shujalpur end. | LD09/1360 | LD09/1370
|  | SUBTOTAL |  |  |  |  | 0.050694 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.2167 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 1.2167 | 958.125 | 720 | 787.5 | 567000 | 0.0016898 | 99.83%
23 |  | ICT1 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
24 |  | ICT2 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
25 |  | ICT2 SHUJALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
26 | 909078 | ICT1 SATNA 765/400KV | 2013-09-18 | 14:44 | 2013-09-18 | 16:03 | - |  |  | 0.054861 | 1 | 18 | - |  |  | - |  |  | OMSU | ICT hand tripped to change Tap position of ICT from 1 to 12 on WRLDC instruction | LD09/1267 | LD09/1276
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.054861 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 1.3 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 718.7 | 2500 | 1796750 | 0 | 100%
27 |  | ICT2 NAVSARI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
28 |  | ICT1 NAVSARI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
29 | 909079 | ICT2 SATNA 765/400KV | 2013-09-18 | 16:05 | 2013-09-18 | 17:01 | - |  |  | 0.038889 | 0 | 55 | - |  |  | - |  |  | OMSU | ICT hand tripped to change Tap position of ICT from 1 to 12 on WRLDC instruction | LD09/1278 | LD09/1281
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.038889 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0.91667 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 719.0833 | 2500 | 1797708.3333 | 0 | 100%
30 |  | ICT1 BINA 765/400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 720 | 2500 | 1800000 | 0 | 100%
31 |  | ICT3 VAPI 400/220/33kV | [17 empty] | H/T to avail S/D by Powergrid for taking oil sample of 220kV side CTs. | LD 08/1041
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 720 | 787.5 | 567000 | 0 | 100%
32 | 908119 | ICT2 BINA 765/400KV | 2013-08-29 | 16:00 | 2013-09-10 | 11:12 | - |  |  | - |  |  | - |  |  | 1900-01-08 11:12 | 227 | 12 | LCSD | ICT H/T for commissioing of ICT spare unit at Bina S/S.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 11:12 | 227 | 12
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 227.2 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 720 | 2500 | 1800000 | 0 | 100%
33 |  | ICT1 GWALIOR 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
34 |  | ICT2 GWALIOR 765/400KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 720 | 3750 | 2700000 | 0 | 100%
35 | 909073 | ICT2 INDORE 765/400KV | 2013-09-17 | 17:58 | 2013-09-17 | 19:42 | 0.072222 | 1 | 43 | - |  |  | - |  |  | - |  |  | OSFT | ICT H/T to avail emergency S/D due to oil leakage from R ph unit. | LD09/1215 | LD09/1218
|  | SUBTOTAL |  |  |  |  | 0.072222 | 1 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.7167 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 1.7167 | 6437.5 | 720 | 3750 | 2700000 | 0.0023843 | 99.76%
[20 empty] | ICT AVAILABILITY | [5 empty] | 11083.75 |  |  | 31910106.0533
0.00034734
99.97%
Bus Reactors
1 |  | BUS REACTOR DEHGAM I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
2 |  | BUS REACTOR JABALPUR I 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 720 | 100 | 72000 | 0 | 100%
3 |  | BUS REACTOR JABALPUR II 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 720 | 100 | 72000 | 0 | 100%
4 |  | BUS REACTOR ITARSI I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
5 |  | BUS REACTOR ITARSI II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
6 |  | BUS REACTOR ITARSI III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
7 |  | BUS REACTOR JABALPUR III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
8 |  | BUS REACTOR DHULE 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 80 | 4 | 0 | 0 | 720 | 320 | 230400 | 0 | 100%
9 |  | BUS REACTOR SATNA 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
10 |  | Bus Reactor # 1 / Bina |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
11 |  | Bus Reactor / Damoh |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
12 |  | Bus Reactor / Gwalior |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 720 | 200 | 144000 | 0 | 100%
13 |  | BUS REACTOR KHANDWA 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 720 | 500 | 360000 | 0 | 100%
14 | 909012 | BUS REACTOR DEHGAM II 400kV | 2013-09-03 | 12:14 | 2013-09-25 | 23:46 | - |  |  | - |  |  | - |  |  | 1900-01-21 11:32 | 539 | 31 | SVRD | Reactor H/T on Voltage regulation as per instruction of WRLDC. | LD 09/176 | LD 09/1979
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-21 11:32 | 539 | 31
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 539.5167 |  |  |  |  | 125 | 4 | 0 | 0 | 720 | 500 | 360000 | 0 | 100%
15 | 909010 | BUS REACTOR BHACHAU 400kV | 2013-09-03 | 11:46 | 2013-09-18 | 13:48 | - |  |  | - |  |  | - |  |  | 1900-01-14 02:02 | 362 | 1 | SVRD | Reactor H/T on Voltage regulation as per instruction of WRLDC. | LD 09/178 | LD 09/1266
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-14 02:02 | 362 | 1
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 362.0167 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
16 |  | Bus Reactor / Shujalpur |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
17 | 909143 | BUS REACTOR RAJGARH 400kV | 2013-09-27 | 12:21 | 2013-09-27 | 18:55 | - |  |  | - |  |  | - |  |  | 0.27361 | 6 | 34 | SCSD | Reactor H/T to avail S/D for commissioning of Controlled Switching Device. | LD09/2101 | LD09/2123
| 909157 | BUS REACTOR RAJGARH 400kV | 2013-09-30 | 11:17 | 2013-09-30 | 13:06 | - |  |  | - |  |  | - |  |  | 0.075694 | 1 | 48 | SCSD | Reactor H/T to avail OCC Approved S/D for commissioning of Controlled Switching Device(CSD) | LD 09/2289 | LD 09/2300
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34931 | 7 | 82
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.5667 |  |  |  |  | 125 | 4 | 0 | 0 | 720 | 500 | 360000 | 0 | 100%
18 | 909030 | BUS REACTOR SATNA 765kV | 2013-09-09 | 19:28 | 2013-09-11 | 14:11 | - |  |  | - |  |  | - |  |  | 1899-12-31 18:43 | 42 | 42 | SVRD | Reactor H/T for voltage regulation on WRLDC instruction | LD 09/628 LD 09/56 | LD09/759
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 18:43 | 42 | 42
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 42.7 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
19 |  | Bus Reactor / Navsari |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
20 |  | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
21 |  | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
22 |  | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
23 |  | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
24 |  | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 720 | 960 | 691200 | 0 | 100%
25 |  | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
26 |  | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 720 | 252 | 181440 | 0 | 100%
[20 empty] | BUS REACTOR AVAILABILITY | [5 empty] | 0 |  |  | 7444800
0
100%
[20 empty] | SYSTEM AVAILABILITY | [5 empty] | 26642.2833 |  |  | 68006517.4345
0.00039176
99.96%
Formulas:
OUTAGE HOURS ATTRIBUTED TO = SUM([OUTAGE HOURS ATTRIBUTED TO, row above]:[OUTAGE HOURS ATTRIBUTED TO, row above])
OUTAGE HOURS ATTRIBUTED TO = SUM(H21:[OUTAGE HOURS ATTRIBUTED TO, row above])
OTHERS = SUM([OTHERS, row above]:[OTHERS, row above])
OTHERS = IF((RIGHT([Outage Category],1)="U"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
SYSTEM CONSTR. = SUM([SYSTEM CONSTR., row above]:[SYSTEM CONSTR., row above])
SYSTEM CONSTR. = SUM(N21:[SYSTEM CONSTR., row above])
OUTAGE DEEMED AVAILABLE = SUM([OUTAGE DEEMED AVAILABLE, row above]:[OUTAGE DEEMED AVAILABLE, row above])
OUTAGE DEEMED AVAILABLE = IF((RIGHT([Outage Category],1)="D"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")

## availability sheet
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR SEPTEMBER-2013
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =30*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 720 | 79 | 2 | 0 | 158 | 113760 | 0 | 100 | 100%
2 | 400kV Itarsi-Indore # 1 | 2 | 4 |  |  | 2.0667 | 0 | 720 | 207 | 2 | 855.6 | 414 | 298080 | 0.0028704 | 99.713 | 99.71%
3 | 400kV Itarsi-Indore # 2 |  |  | 0 | 48 | 0 | 0.8 | 719.2 | 214 | 2 | 0 | 428 | 307817.6 | 0 | 100 | 100%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 720 | 289 | 2 | 0 | 578 | 416160 | 0 | 100 | 100%
5 | 400kV Indore-Asoj # 2 |  |  | 1 | 57 | 0 | 1.95 | 718.05 | 273 | 2 | 0 | 546 | 392055.3 | 0 | 100 | 100%
6 | 400 KV V'chal - Jabalpur # 1 | 0 | 10 | 1 | 24 | 0.16667 | 1.4 | 718.6 | 360 | 2 | 120 | 720 | 517392 | 0.00023193 | 99.9768 | 99.98%
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 720 | 360 | 2 | 0 | 720 | 518400 | 0 | 100 | 100%
8 | 400 KV Jabalpur - Itarsi # 1 | 0 | 59 |  |  | 0.98333 | 0 | 720 | 232 | 2 | 456.2667 | 464 | 334080 | 0.0013657 | 99.8634 | 99.86%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 720 | 232 | 2 | 0 | 464 | 334080 | 0 | 100 | 100%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 720 | 157 | 2 | 0 | 314 | 226080 | 0 | 100 | 100%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 720 | 157 | 2 | 0 | 314 | 226080 | 0 | 100 | 100%
12 | 400 KV Jabalpur-Sasan | 3 | 20 |  |  | 3.3333 | 0 | 720 | 376 | 2 | 2506.6667 | 752 | 541440 | 0.0046296 | 99.537 | 99.54%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 720 | 21 | 2 | 0 | 42 | 30240 | 0 | 100 | 100%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 720 | 389 | 2 | 0 | 778 | 560160 | 0 | 100 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 720 | 234 | 2 | 0 | 468 | 336960 | 0 | 100 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 |  |  |  |  | 0 | 0 | 720 | 234 | 2 | 0 | 468 | 336960 | 0 | 100 | 100%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 720 | 196.64 | 2 | 0 | 393.28 | 283161.6 | 0 | 100 | 100%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 720 | 196.64 | 2 | 0 | 393.28 | 283161.6 | 0 | 100 | 100%
19 | 400 KV Khandwa - Dhule # 1 | 5 | 36 |  |  | 5.6 | 0 | 720 | 261.78 | 2 | 2931.936 | 523.56 | 376963.2 | 0.0077778 | 99.2222 | 99.22%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 720 | 261.78 | 2 | 0 | 523.56 | 376963.2 | 0 | 100 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 720 | 57 | 2 | 0 | 114 | 82080 | 0 | 100 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  |  |  | 0 | 0 | 720 | 110 | 2 | 0 | 220 | 158400 | 0 | 100 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 720 | 13 | 2 | 0 | 26 | 18720 | 0 | 100 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 720 | 13 | 1 | 0 | 13 | 9360 | 0 | 100 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 720 | 13 | 1 | 0 | 13 | 9360 | 0 | 100 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 | 3 | 11 | 1 | 35 | 3.1833 | 1.5833 | 718.4167 | 58.149 | 1 | 185.1077 | 58.149 | 41775.2107 | 0.004431 | 99.5569 | 99.56%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  | 0 | 38 | 0 | 0.63333 | 719.3667 | 58.149 | 1 | 0 | 58.149 | 41830.4523 | 0 | 100 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 720 | 31.334 | 1 | 0 | 31.334 | 22560.48 | 0 | 100 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 48 | 29 |  |  | 48.4833 | 0 | 720 | 31.334 | 1 | 1519.1768 | 31.334 | 22560.48 | 0.067338 | 93.2662 | 93.27%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 720 | 37 | 1 | 0 | 37 | 26640 | 0 | 100 | 100%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 720 | 37 | 1 | 0 | 37 | 26640 | 0 | 100 | 100%
32 | 220kV Kawas - Haldarwa # 1 |  |  | 25 | 56 | 0 | 25.9333 | 694.0667 | 81 | 1 | 0 | 81 | 56219.4 | 0 | 100 | 100%
33 | 220kV Kawas-Haldarwa # 2 |  |  | 1 | 8 | 0 | 1.1333 | 718.8667 | 81 | 1 | 0 | 81 | 58228.2 | 0 | 100 | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 720 | 74 | 1 | 0 | 74 | 53280 | 0 | 100 | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 720 | 74 | 1 | 0 | 74 | 53280 | 0 | 100 | 100%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 720 | 43 | 1 | 0 | 43 | 30960 | 0 | 100 | 100%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 720 | 43 | 1 | 0 | 43 | 30960 | 0 | 100 | 100%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  | 0 | 47 | 0 | 0.78333 | 719.2167 | 117 | 1 | 0 | 117 | 84148.35 | 0 | 100 | 100%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 720 | 117 | 1 | 0 | 117 | 84240 | 0 | 100 | 100%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 720 | 267 | 2 | 0 | 534 | 384480 | 0 | 100 | 100%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 720 | 267 | 2 | 0 | 534 | 384480 | 0 | 100 | 100%
42 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 720 | 258.31 | 2 | 0 | 516.62 | 371966.4 | 0 | 100 | 100%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 720 | 100.32 | 2 | 0 | 200.64 | 144460.8 | 0 | 100 | 100%
44 | 400kV Nigrie-Satna |  |  |  |  | 0 | 0 | 720 | 161.11 | 2 | 0 | 322.22 | 231998.4 | 0 | 100 | 100%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 720 | 276 | 2 | 0 | 552 | 397440 | 0 | 100 | 100%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 720 | 276 | 2 | 0 | 552 | 397440 | 0 | 100 | 100%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 720 | 0.742 | 2 | 0 | 1.484 | 1068.48 | 0 | 100 | 100%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 720 | 0.742 | 2 | 0 | 1.484 | 1068.48 | 0 | 100 | 100%
49 | 765 kV Gwalior-Bina # 1 |  |  |  |  | 0 | 0 | 720 | 234.931 | 4 | 0 | 939.724 | 676601.28 | 0 | 100 | 100%
50 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 720 | 272.586 | 2 | 0 | 545.172 | 392523.84 | 0 | 100 | 100%
51 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 720 | 272.586 | 2 | 0 | 545.172 | 392523.84 | 0 | 100 | 100%
52 | 400KV Bina - Sujalpur # 1 | 4 | 34 |  |  | 4.5667 | 0 | 720 | 199.936 | 2 | 1826.0821 | 399.872 | 287907.84 | 0.0063426 | 99.3657 | 99.37%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 720 | 199.936 | 2 | 0 | 399.872 | 287907.84 | 0 | 100 | 100%
54 | 400KV Sujalpur - Nagda # 1 | 2 | 33 |  |  | 2.55 | 0 | 720 | 152.229 | 2 | 776.3679 | 304.458 | 219209.76 | 0.0035417 | 99.6458 | 99.65%
55 | 400KV Sujalpur - Nagda # 2 | 2 | 37 |  |  | 2.6167 | 0 | 720 | 152.229 | 2 | 796.6651 | 304.458 | 219209.76 | 0.0036343 | 99.6366 | 99.64%
56 | 400KV Nagda - Dehgam # 2 |  |  | 1 | 18 | 0 | 1.3 | 718.7 | 331.442 | 2 | 0 | 662.884 | 476414.7308 | 0 | 100 | 100%
57 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 720 | 331.442 | 2 | 0 | 662.884 | 477276.48 | 0 | 100 | 100%
58 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 719.8333 | 351.729 | 4 | 0 | 1406.916 | 1012745.034 | 0 | 100 | 100%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 720 | 351.729 | 4 | 0 | 1406.916 | 1012979.52 | 0 | 100 | 100%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 720 | 220.588 | 2 | 0 | 441.176 | 317646.72 | 0 | 100 | 100%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 65 | 65 | 0 | 66.0833 | 653.9167 | 4.01 | 2 | 0 | 8.02 | 5244.4117 | 0 | 100 | 100%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 78 | 5 | 0 | 78.0833 | 641.9167 | 4.01 | 2 | 0 | 8.02 | 5148.1717 | 0 | 100 | 100%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 720 | 4.12 | 2 | 0 | 8.24 | 5932.8 | 0 | 100 | 100%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 720 | 4.12 | 2 | 0 | 8.24 | 5932.8 | 0 | 100 | 100%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 720 | 220.588 | 2 | 0 | 441.176 | 317646.72 | 0 | 100 | 100%
66 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 720 | 25.71 | 1 | 0 | 25.71 | 18511.2 | 0 | 100 | 100%
67 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 720 | 25.71 | 1 | 0 | 25.71 | 18511.2 | 0 | 100 | 100%
68 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 720 | 29.66 | 1 | 0 | 29.66 | 21355.2 | 0 | 100 | 100%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 720 | 29.66 | 1 | 0 | 29.66 | 21355.2 | 0 | 100 | 100%
70 | 765 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 720 | 233.652 | 4 | 0 | 934.608 | 672917.76 | 0 | 100 | 100%
71 | 765 kV Seoni - Bina | 0 | 52 | 18 | 1 | 0.86667 | 18.0167 | 701.9833 | 292.45 | 4 | 1013.8267 | 1169.8 | 821180.1033 | 0.0012346 | 99.8765 | 99.88%
72 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 720 | 214.471 | 2 | 0 | 428.942 | 308838.24 | 0 | 100 | 100%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 720 | 213.8 | 2 | 0 | 427.6 | 307872 | 0 | 100 | 100%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 720 | 28.549 | 1 | 0 | 28.549 | 20555.28 | 0 | 100 | 100%
75 | 220 KV Vapi - Sayali |  |  |  |  | 0 | 0 | 720 | 18.3 | 1 | 0 | 18.3 | 13176 | 0 | 100 | 100%
76 | 220kV Sayali-Khadoli |  |  |  |  | 0 | 0 | 720 | 12.235 | 1 | 0 | 12.235 | 8809.2 | 0 | 100 | 100%
77 | 400kV Damoh-Birsinghpur#1 | 0 | 37 |  |  | 0.61667 | 0 | 720 | 228.474 | 2 | 281.7846 | 456.948 | 329002.56 | 0.00085648 | 99.9144 | 99.91%
78 | 400kV Damoh-Birsinghpur#2 | 1 | 37 |  |  | 1.6167 | 0 | 720 | 228.474 | 2 | 738.7326 | 456.948 | 329002.56 | 0.0022454 | 99.7755 | 99.78%
79 | 400kV Dehgam-Pirana#1 | 3 | 22 |  |  | 3.3667 | 0 | 720 | 46.67 | 2 | 314.2447 | 93.34 | 67204.8 | 0.0046759 | 99.5324 | 99.53%
80 | 400kV Dehgam-Pirana#2 | 2 | 5 |  |  | 2.0833 | 0 | 720 | 46.67 | 2 | 194.4583 | 93.34 | 67204.8 | 0.0028935 | 99.7106 | 99.71%
81 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 720 | 99.468 | 3 | 0 | 298.404 | 214850.88 | 0 | 100 | 100%
82 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 720 | 99.468 | 3 | 0 | 298.404 | 214850.88 | 0 | 100 | 100%
83 | 400kV Bhachau - Ranchodpura # 1 |  |  | 0 | 29 | 0 | 0.48333 | 719.5167 | 282.856 | 3 | 0 | 848.568 | 610558.8188 | 0 | 100 | 100%
84 | 400kV Bhachau - Ranchodpura # 2 |  |  | 1 | 30 | 0 | 1.5 | 718.5 | 282.856 | 3 | 0 | 848.568 | 609696.108 | 0 | 100 | 100%
85 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 720 | 314.053 | 3 | 0 | 942.159 | 678354.48 | 0 | 100 | 100%
86 | 400kV Mundra - Limbdi # 2 |  |  | 3 | 49 | 0 | 3.8167 | 716.1833 | 314.053 | 3 | 0 | 942.159 | 674758.5731 | 0 | 100 | 100%
87 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 720 | 274.164 | 4 | 0 | 1096.656 | 789592.32 | 0 | 100 | 100%
88 | 765kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 720 | 275.635 | 4 | 0 | 1102.54 | 793828.8 | 0 | 100 | 100%
89 | 765kV Bina - Indore |  |  | 8 | 28 | 0 | 8.4667 | 711.5333 | 311 | 4 | 0 | 1244 | 885147.4667 | 0 | 100 | 100%
90 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 720 | 102.152 | 2 | 0 | 204.304 | 147098.88 | 0 | 100 | 100%
91 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 720 | 102.152 | 2 | 0 | 204.304 | 147098.88 | 0 | 100 | 100%
92 | 400kV Mundra-Jetpur#1 |  |  |  |  | 0 | 0 | 720 | 337 | 3 | 0 | 1011 | 727920 | 0 | 100 | 100%
93 | 400kV Mundra-Jetpur#2 |  |  | 3 | 49 | 0 | 3.8167 | 716.1833 | 337 | 3 | 0 | 1011 | 724061.35 | 0 | 100 | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 720 | 28.55 | 4 | 0 | 114.2 | 82224 | 0 | 100 | 100%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 720 | 28.55 | 4 | 0 | 114.2 | 82224 | 0 | 100 | 100%
96 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 720 | 5.443 | 2 | 0 | 10.886 | 7837.92 | 0 | 100 | 100%
97 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 720 | 5.443 | 2 | 0 | 10.886 | 7837.92 | 0 | 100 | 100%
98 | 765kV Sasan - Satna # 1 |  |  |  |  | 0 | 0 | 720 | 245.7 | 4 | 0 | 982.8 | 707616 | 0 | 100 | 100%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 720 | 0.8 | 2 | 0 | 1.6 | 1152 | 0 | 100 | 100%
100 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 720 | 116.85 | 2 | 0 | 233.7 | 168264 | 0 | 100 | 100%
101 | 400kV Vapi-Navsari#2 |  |  |  |  | 0 | 0 | 720 | 116.85 | 2 | 0 | 233.7 | 168264 | 0 | 100 | 100%
102 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 720 | 245.7 | 4 | 0 | 982.8 | 707616 | 0 | 100 | 100%
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 720 | 0.8 | 2 | 0 | 1.6 | 1152 | 0 | 100 | 100%
104 | 400kV Indore (MP)-Indore (PG)#1 | 4 | 39 |  |  | 4.65 | 0 | 720 | 49.7 | 4 | 924.42 | 198.8 | 143136 | 0.0064583 | 99.3542 | 99.35%
105 | 400kV Indore (MP)-Indore (PG)#2 | 0 | 42 |  |  | 0.7 | 0 | 720 | 49.7 | 4 | 139.16 | 198.8 | 143136 | 0.00097222 | 99.9028 | 99.9%
| Total Sr.No. 1 to 105 | 79 | 507 | 206 | 597 |  |  |  | 16435.669 |  | 15580.4958 |  | 28612264.5611
* | Lines charged with 400kV level
|  | 87.45 |  | 215.95
[10 empty] | NAFM | 0.00054454
Availability of ( Sl no 1 to 105) transmission lines during SEPTEMBER-2013 = | [9 empty] | TAFM | 99.9455
106 | 765 kV Gwalior -Agra # 1 |  |  | 0 | 0 | 0 | 0 | 720 | 129.435 | 4 | 0 | 517.74 | 372772.8 | 0 | 100 | 100%
107 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 127.934 | 4 | 0 | 511.736 | 368449.92 | 0 | 100 | 100%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =30*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
6 | 400/220kV ICT # 2 / Satna | 1 | 24 |  |  | 1.4 | 0 | 720 | 315 | 2.5 | 1102.5 | 787.5 | 567000 | 0.0019444 | 99.8056 | 99.81%
7 | 400/220kV ICT # 1 / Khandwa |  |  | 0 | 56 | 0 | 0.93333 | 719.0667 | 315 | 2.5 | 0 | 787.5 | 566265 | 0 | 100 | 100%
8 | 400/220kV ICT # 2 / Khandwa |  |  | 1 | 5 | 0 | 1.0833 | 718.9167 | 315 | 2.5 | 0 | 787.5 | 566146.875 | 0 | 100 | 100%
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
10 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
14 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
15 | 400/220kV ICT # 1 / Damoh | 0 | 58 |  |  | 0.96667 | 0 | 720 | 315 | 2.5 | 761.25 | 787.5 | 567000 | 0.0013426 | 99.8657 | 99.87%
16 | 400/220kV ICT # 2 / Damoh | 1 | 5 |  |  | 1.0833 | 0 | 720 | 315 | 2.5 | 853.125 | 787.5 | 567000 | 0.0015046 | 99.8495 | 99.85%
17 | 400/220 KV ICT # 2 / Rajgarh | 1 | 14 |  |  | 1.2333 | 0 | 720 | 315 | 2.5 | 971.25 | 787.5 | 567000 | 0.001713 | 99.8287 | 99.83%
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
20 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
21 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
22 | 400/220 KV ICT # 1 / Shujalpur | 1 | 13 |  |  | 1.2167 | 0 | 720 | 315 | 2.5 | 958.125 | 787.5 | 567000 | 0.0016898 | 99.831 | 99.83%
23 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
24 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
25 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
26 | 765/400KV ICT# 1 / Satna |  |  | 1 | 19 | 0 | 1.3167 | 718.6833 | 1000 | 2.5 | 0 | 2500 | 1796708.3333 | 0 | 100 | 100%
27 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
28 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
29 | 765/400KV ICT# 2 / Satna |  |  | 0 | 56 | 0 | 0.93333 | 719.0667 | 1000 | 2.5 | 0 | 2500 | 1797666.6667 | 0 | 100 | 100%
30 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 720 | 1000 | 2.5 | 0 | 2500 | 1800000 | 0 | 100 | 100%
31 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 720 | 315 | 2.5 | 0 | 787.5 | 567000 | 0 | 100 | 100%
32 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 720 | 1000 | 2.5 | 0 | 2500 | 1800000 | 0 | 100 | 100%
33 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100%
34 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 720 | 1500 | 2.5 | 0 | 3750 | 2700000 | 0 | 100 | 100%
35 | 765/400KV ICT# 2 / INDORE | 1 | 44 |  |  | 1.7333 | 0 | 720 | 1500 | 2.5 | 6500 | 3750 | 2700000 | 0.0024074 | 99.7593 | 99.76%
| Total Sr.No. 1 to 35 | 5 | 158 | 2 | 136 |  |  |  | 17320 |  | 11146.25 |  | 31168786.875
|  | 7.6333 |  | 4.2667 | [5 empty] | NAFM | 0.00035761
Availability of 35 ( Sl no 1 to 35) ICTs in SEPTEMBER-2013 = | [9 empty] | TAFM | 99.9642
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =30*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 720 | 25 | 4 | 0 | 100 | 72000 | 0 | 100 | 100%
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 720 | 25 | 4 | 0 | 100 | 72000 | 0 | 100 | 100%
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100%
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100%
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100%
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 720 | 80 | 4 | 0 | 320 | 230400 | 0 | 100 | 100%
9 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100%
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 720 | 50 | 4 | 0 | 200 | 144000 | 0 | 100 | 100%
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 720 | 125 | 4 | 0 | 500 | 360000 | 0 | 100 | 100%
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 720 | 125 | 4 | 0 | 500 | 360000 | 0 | 100 | 100%
15 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
16 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
17 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 720 | 125 | 4 | 0 | 500 | 360000 | 0 | 100 | 100%
18 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100%
19 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
20 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100%
21 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100%
22 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
23 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100%
24 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 720 | 240 | 4 | 0 | 960 | 691200 | 0 | 100 | 100%
25 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
26 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 720 | 63 | 4 | 0 | 252 | 181440 | 0 | 100 | 100%
| Total of sl no 1 to 26 | 0 | 0 | 0 | 0 |  |  |  | 2585 |  | 0 |  | 7444800
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 26 ( Sl no 1 to 26) Bus Reactors in SEPTEMBER-2013 = | [7 empty] | TAFM | 100
[11 empty] | 26726.7457 |  | 67225851.4361
[8 empty] | NAFM = | 0.00039757
% System Availability for SEPTEMBER-2013 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9602
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B136: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B137: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## ANX-II
MONTH : SEPTEMBER-2013
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : SEPTEMBER-2013
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
SEPTEMBER 2013
Sl. No. | Name of Elements | Type of failures | Restoration Time (Days) |  |  | Remarks
A |  | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 |  | Insualtor Failure | Terrain Type
|  |  | Plain | River bed | Hilly
i | KHANDWA-DHULE I 400kV | Insualtor Failure in single phase | Less than 1 day
ii |  | Insualtor Failure in two phases | NIL
ii |  | Insualtor Failure in three phases
2 |  | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 |  | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 |  | Tower Damage ( not collapse)
i |  | One arm damage
ii |  | Two arm damage
5 |  | Snapping of phase conductor
i |  | Conductor snapping in single phase
ii |  | Conductor snapping in two phases
iii |  | Conductor snapping in three phases
6 |  | Failure of Earth wire
7 |  | Insulator failure with conductor snapping
8 |  | Any other combination of failures
B |  | Elements of sub-station for each KV class seperately
1 |  | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
|  | Other major failures in ICTs | Single phase Unit |  | Three phase Unit
|  | (i) Replacement of faulty bushings | NIL
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 |  | Failures of Reactors
Restoration of failed Reactors

## Supporting Annex V
Supporting Annex V
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF SEPTEMBER -2013
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | Outage Category | Details | WRLDC CODE FOR |  | Outage in Days |  |  | REMARKS
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING | Flashover | Snapping | Collapes of Tower
1 | 909051 | KHANDWA-DHULE I 400kV | 2013-09-13 | 14:31 | 2013-09-14 | 16:38 | 0.23333 | - | - | 0.75 | LHWT | Line A/T on R ph to E/F due to flashover at loc no: 878(WR-I portion). Line restoration got delayed due to continuous rains & poor visibility at site Hence outage from 1600hrs/13.09.2013 to 1000/14.09.2013 may not be attributable to POWERGRID(F/L- 195.1Km from Khandwa, WR-I jurisdiction). |  | LD 09/991 | 0.21042