## Tripping AC SYSTEM (hidden)
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR MARCH- 2011
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032
5 | 400kV Indore-Asoj # 2 | 8 | 38 |  |  | 8.6333 | 0 | 744 | 273 | 2 | 4713.8 | 546 | 406224
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
8 | 400 KV Jabalpur - Itarsi # 1 | 4 | 54 |  |  | 4.9 | 0 | 744 | 232 | 2 | 2273.6 | 464 | 345216
9 | 400 KV Jabalpur - Itarsi # 2 | 6 | 25 |  |  | 6.4167 | 0 | 744 | 232 | 2 | 2977.3333 | 464 | 345216
10 | 400kV Jhanor-Dehgam#1 | 0 | 0 |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616
11 | 400kV Jhanor-Dehgam#2 | 12 | 59 |  |  | 12.9833 | 0 | 744 | 157 | 2 | 4076.7667 | 314 | 233616
12 | 400 KV V'chal - Jabalpur # 3 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
13 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
14 | 400 KV Jabalpur - Itarsi # 3 | 4 | 45 |  |  | 4.75 | 0 | 744 | 234 | 2 | 2223 | 468 | 348192
15 | 400 KV Jabalpur - Itarsi # 4 | 5 | 52 |  |  | 5.8667 | 0 | 744 | 234 | 2 | 2745.6 | 468 | 348192
16 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
17 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
18 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
19 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
20 | 400 KV Jhanor - Sugen(PGCIL portion) | 13 | 31 | 0 | 51 | 13.5167 | 0.85 | 743.15 | 57 | 2 | 1540.9 | 114 | 84719.1
21 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 9 | 3 | 0 | 9.05 | 734.95 | 110 | 2 | 0 | 220 | 161689
22 | 400 KV Jhanor - Jhanor(GPEC) |  |  | 1 | 88 | 0 | 2.4667 | 741.5333 | 13 | 2 | 0 | 26 | 19279.8667
23 | 220kV Jhanor-Haldarwa ckI # 1 | 0 | 15 | 3 | 42 | 0.25 | 3.7 | 740.3 | 13 | 1 | 3.25 | 13 | 9623.9
24 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  | 71 | 0 | 1.1833 | 742.8167 | 13 | 1 | 0 | 13 | 9656.6167
25 | 220kV Kawas-Navsari ckt # 1 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 49 | 1 | 17.9667 | 49 | 36456
26 | 220kV Kawas-Navsari ckt # 2 | 0 | 13 | 0 | 52 | 0.21667 | 0.86667 | 743.1333 | 49 | 1 | 10.6167 | 49 | 36413.5333
27 | 220kV Kawas-Ichchapur |  |  |  |  | 0 | 0 | 744 | 3 | 1 | 0 | 3 | 2232
28 | 220kV Kawas-Vav |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528
29 | 220kV Kawas - Haldarwa # 1 | 0 | 80 | 8 | 25 | 1.3333 | 8.4167 | 735.5833 | 81 | 1 | 108 | 81 | 59582.25
30 | 220kV Kawas-Haldarwa # 2 |  |  | 0 | 33 | 0 | 0.55 | 743.45 | 81 | 1 | 0 | 81 | 60219.45
31 | 220 kV Kakrapar - Haldarwa # 1 | 5 | 20 |  | 74 | 5.3333 | 1.2333 | 742.7667 | 74 | 1 | 394.6667 | 74 | 54964.7333
32 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 74 | 1 | 0 | 74 | 55012.8333
33 | 220 KV Kakrapar - Vav # 1 |  |  | 1 | 18 | 0 | 1.3 | 742.7 | 43 | 1 | 0 | 43 | 31936.1
35 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992
35 | 220kV Kakrapar-Vapi ckt # 1 | 0 | 26 |  |  | 0.43333 | 0 | 744 | 117 | 1 | 50.7 | 117 | 87048
36 | 220kV Kakrapar-Vapi ckt # 2 | 0 | 53 | 7 | 82 | 0.88333 | 8.3667 | 735.6333 | 117 | 1 | 103.35 | 117 | 86069.1
37 | 220kV Ichchapur-Vav |  |  |  |  | 0 | 0 | 744 | 34 | 1 | 0 | 34 | 25296
38 | 400kV V'chal - Satna # 1 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 267 | 2 | 0 | 534 | 397171.4
39 | 400kV V'chal - Satna # 2 | 0 | 50 | 0 | 18 | 0.83333 | 0.3 | 743.7 | 267 | 2 | 445 | 534 | 397135.8
40 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
41 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
42 | 400kV Satna - Bina # 1 | 0 | 24 |  |  | 0.4 | 0 | 744 | 276 | 2 | 220.8 | 552 | 410688
43 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688
44 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  | 1 | 49 | 0 | 1.8167 | 742.1833 | 0.742 | 2 | 0 | 1.484 | 1101.4001
45 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  | 1 | 50 | 0 | 1.8333 | 742.1667 | 0.742 | 2 | 0 | 1.484 | 1101.3753
46 | 400 kV Gwalior-Bina # 1 | 5 | 38 |  |  | 5.6333 | 0 | 744 | 234.931 | 4 | 5293.7785 | 939.724 | 699154.656
47 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
48 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
49 | 400KV Bina - Nagda # 1 | 0 | 18 |  |  | 0.3 | 0 | 744 | 330.155 | 2 | 198.093 | 660.31 | 491270.64
50 | 400KV Bina - Nagda # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 330.155 | 2 | 0 | 660.31 | 491160.5883
51 | 400KV Nagda - Dehgam # 2 |  |  | 3 | 58 | 0 | 3.9667 | 740.0333 | 331.442 | 2 | 0 | 662.884 | 490556.2561
52 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696
53 | 400KV Seoni - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
54 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
55 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
56 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
57 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
58 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
59 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
60 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
61 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
62 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
63 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
64 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
65 | 400 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352
66 | 400 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2
67 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848
68 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4
69 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
70 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
71 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
72 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
73 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
74 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
| Total Sr.No. 1 to 74 | 73 | 705 | 34 | 773 | 73.05 |  |  | 12271.634 |  | 27397.2215 |  | 19691267.3032
|  |  | 84.75 |  | 46.8833 |  |  |  |  | NAFM | 0.0013913
| Availability of 74 ( Sl no 1 to 74) transmission lines during MARCH-2011 = | [8 empty] | TAFM | 99.8609
Sr.No. 71,72,73 & 74 lines are declared for commercial operation w.e.f. 01.03.11
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
0.63333
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0.83333
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
10 | 400/220kV ICT # 2 / Vapi | 11 | 51 |  |  | 11.85 | 0 | 744 | 315 | 2.5 | 9331.875 | 787.5 | 585900
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
14 | 400/220kV ICT # 1 / Itarsi | 2 | 48 |  |  | 2.8 | 0 | 744 | 315 | 2.5 | 2205 | 787.5 | 585900
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
| Total Sr.No. 1 to 19 | 13 | 99 | 0 | 0 | 14.65 |  |  | 5040 | 47.5 | 11536.875 |  | 11132100
|  | 14.65 |  | 0 | [5 empty] | NAFM | 0.0010364
[10 empty] | TAFM | 99.8964
Availability of 19 ( Sl no 1 to 19) ICTs in MARCH-2011 =
ICT # 1 at Pirana was declared for commercial operation w.e.f. 01.03.11
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
| Total of sl no 1 to 14 | 0 | 0 | 0 | 0 |  |  |  | 882 | 56 | 0 |  | 2624832
0
[8 empty] | NAFM | 0
| Availability of 14( Sl no 1 to 14) Bus Reactors in MARCH-2011 = | [6 empty] | TAFM | 100
[11 empty] | 38934.0965 |  | 33448199.3032
[8 empty] | NAFM = | 0.001164
| % System Availability for MARCH 2011 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.8836
3
Note on B43: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B45: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B47: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B49: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B187: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B189: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-II) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-II) Transmission System in Western Region for the month of October - 2013 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 400kV Satpura-Itarsi | 100% | 40 | 400kV V'chal - Satna # 1 | 100%
2 | 400kV Itarsi-Indore # 1 | 100% | 41 | 400kV V'chal - Satna # 2 | 100%
3 | 400kV Itarsi-Indore # 2 | 100% | 42 | 400kV V'chal - Satna # 3 | 99.97%
4 | 400kV Indore-Asoj # 1 | 100% | 43 | 400kV V'chal -Nigrie | 100%
5 | 400kV Indore-Asoj # 2 | 100% | 44 | 400kV Nigrie-Satna | 99.98%
6 | 400 KV V'chal - Jabalpur # 1 | 100% | 45 | 400kV Satna - Bina # 1 | 100%
7 | 400 KV V'chal - Jabalpur # 2 | 99.57% | 46 | 400kV Satna - Bina # 2 | 100%
8 | 400 KV Jabalpur - Itarsi # 1 | 100% | 47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 | 100%
9 | 400 KV Jabalpur - Itarsi # 2 | 100% | 48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 | 100%
10 | 400kV Jhanor-Dehgam#1 | 100% | 49 | 765 kV Gwalior-Bina # 1 | 100%
11 | 400kV Jhanor-Dehgam#2 | 100% | 50 | 400KV Satna-Bina # 4 | 100%
12 | 400 KV Jabalpur-Sasan | 100% | 51 | 400KV Satna-Bina # 3 | 99.99%
13 | 400kV Sasan-Vindhyachal | 100% | 52 | 400KV Bina - Sujalpur # 1 | 100%
14 | 400 KV V'chal - Jabalpur # 4 | 100% | 53 | 400KV Bina - Sujalpur # 2 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 | 100% | 54 | 400KV Sujalpur - Nagda # 1 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 | 99.58% | 55 | 400KV Sujalpur - Nagda # 2 | 100%
17 | 400 KV Itarsi - Khandwa # 1 | 100% | 56 | 400KV Nagda - Dehgam # 2 | 100%
18 | 400 KV Itarsi - Khandwa # 2 | 100% | 57 | 400KV Nagda - Dehgam # 1 | 100%
19 | 400 KV Khandwa - Dhule # 1 | 100% | 58 | 400KV Seoni - Khandwa # 1 | 100%
20 | 400 KV Khandwa - Dhule # 2 | 100% | 59 | 400KV Seoni - Khandwa # 2 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) | 100% | 60 | 400KV Khandwa - Rajgarh # 2 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) | 100% | 61 | 400KV Rajgarh - SSP (LILO portion) # 1 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) | 100% | 62 | 400KV Rajgarh - SSP (LILO portion) # 2 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 | 100% | 63 | 400KV Rajgarh - Nagda (LILO portion) # 1 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 | 100% | 64 | 400KV Rajgarh - Nagda (LILO portion) # 2 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 | 100% | 65 | 400KV Khandwa - Rajgarh # 1 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 | 100% | 66 | 220 KV Vapi - Magarwada # 1 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 100% | 67 | 220 KV Vapi - Magarwada # 2 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 92.54% | 68 | 220 KV Vapi - Karadpada # 1 | 100%
30 | 220kV Kawas-Vav#1 | 100% | 69 | 220 KV Vapi - Karadpada # 2 | 100%
31 | 220kV Kawas-Vav#2 | 100% | 70 | 765 kV Gwalior-Bina # 2 | 100%
32 | 220kV Kawas - Haldarwa # 1 | 100% | 71 | 765 kV Seoni - Bina | 100%
33 | 220kV Kawas-Haldarwa # 2 | 100% | 72 | 400kV Damoh - Bhopal # 1 | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 | 98.82% | 73 | 400kV Damoh - Bhopal # 2 | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 | 100% | 74 | 220 KV Vapi - Khadoli # 1 | 100%
36 | 220 KV Kakrapar - Vav # 1 | 100% | 75 | 220 KV Vapi - Sayali | 100%
37 | 220 KV Kakrapar - Vav # 2 | 100% | 76 | 220kV Sayali-Khadoli | 100%
38 | 220kV Kakrapar-Vapi ckt # 1 | 100% | 77 | 400kV Damoh-Birsinghpur#1 | 100%
39 | 220kV Kakrapar-Vapi ckt # 2 | 100% | 78 | 400kV Damoh-Birsinghpur#2 | 100%
79 | 400kV Dehgam-Pirana#1 | 99.68% | 127 | 400/220 KV ICT # 2 / Pirana | 100%
80 | 400kV Dehgam-Pirana#2 | 100% | 128 | 400/220 KV ICT # 3 / Gwalior | 100%
81 | 400kV Mundra - Bhachau # 1 | 100% | 129 | 400/220 KV ICT # 1 / Shujalpur | 100%
82 | 400kV Mundra - Bhachau # 2 | 100% | 130 | 400/220 KV ICT # 1 / Bhachau | 100%
83 | 400kV Bhachau - Ranchodpura # 1 | 100% | 131 | 400/220 KV ICT # 2 / Bhachau | 100%
84 | 400kV Bhachau - Ranchodpura # 2 | 100% | 132 | 400/220 KV ICT # 2 / Shujalpur | 100%
85 | 400kV Mundra - Limbdi # 1 | 100% | 133 | 765/400KV ICT# 1 / Satna | 100%
86 | 400kV Mundra - Limbdi # 2 | 100% | 134 | 400/220 KV ICT # 2 / Navsari | 100%
87 | 765kV Satna - Bina # 1 | 100% | 135 | 400/220 KV ICT # 1 / Navsari | 100%
88 | 765kV Satna - Bina # 2 | 100% | 136 | 765/400KV ICT# 2 / Satna | 100%
89 | 765kV Bina - Indore | 100% | 137 | 765/400KV ICT# 1 / Bina | 100%
90 | 400kV Gandhar - Navsari # 2 | 100% | 138 | 400kV ICT#3/Vapi | 100%
91 | 400kV Gandhar - Navsari # 1 | 100% | 139 | 765/400KV ICT# 2 / Bina | 100%
92 | 400kV Mundra-Jetpur#1 | 100% | 140 | 765/400KV ICT# 1 / Gwalior | 100%
93 | 400kV Mundra-Jetpur#2 | 100% | 141 | 765/400KV ICT# 2 / Gwalior | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 | 100% | 142 | 765/400KV ICT# 2 / INDORE | 100%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 | 100% | 143 | 765/400KV ICT# 1 / INDORE | 100%
96 | 400kV V'chal (Pooling) - Sasan #1 | 100% | 144 | Bus reactor / Dehgam | 100%
97 | 400k V'chal (Pooling) - Sasan # 2 | 100% | 145 | 25 MVAR reactor # 1 / Jabalpur | 100%
98 | 765kV Sasan - Satna # 1 | 100% | 146 | 25 MVAR reactor # 2 / Jabalpur | 100%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 | 100% | 147 | Bus reactor # 1 / Itarsi | 100%
100 | 400kV Vapi-Navsari#1 | 100% | 148 | Bus reactor # 2 / Itarsi | 100%
101 | 400kV Vapi-Navsari#2 | 99.42% | 149 | Bus Reactor # 3 / Itarsi | 100%
102 | 765kV Sasan - Satna # 2 | 100% | 150 | Bus Reactor # 3 / Jabalpur | 100%
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 | 100% | 151 | Bus Reactor / Dhule | 100%
104 | 400kV Indore (MP)-Indore (PG)#1 | 100% | 152 | Bus Reactor-I (50 MVAR) / Satna | 100%
105 | 400kV Indore (MP)-Indore (PG)#2 | 100% | 153 | Bus Reactor # 1 / Bina | 100%
106 | 765 kV Gwalior -Agra # 1 | 100% | 154 | Bus Reactor / Damoh | 100%
107 | 765 kV Gwalior -Agra # 2 | 100% | 155 | Bus Reactor / Gwalior | 100%
108 | 400/220kV ICT # 1 / Jabalpur. | 99.4% | 156 | Bus Reactor / Khandwa | 100%
109 | 400/220kV ICT # 2 /Jabalpur. | 99.57% | 157 | Bus Reactor / Dehgam | 100%
110 | 400/220 KV ICT # 1 / Dehgam | 100% | 158 | Bus Reactor / Bhachau | 100%
111 | 400/220 KV ICT # 2/ Dehgam | 100% | 159 | Bus Reactor / Shujalpur | 100%
112 | 400/220kV ICT # 1 / Satna | 100% | 160 | Bus Reactor/ Rajgarh | 100%
113 | 400/220kV ICT # 2 / Satna | 100% | 161 | Bus Reactor / Satna 765KV | 100%
114 | 400/220kV ICT # 1 / Khandwa | 100% | 162 | Bus Reactor / Navsari | 100%
115 | 400/220kV ICT # 2 / Khandwa | 100% | 163 | Switchable Bina-I Line Reactor / Satna 765KV | 100%
116 | 400/220kV ICT # 1 / Vapi | 100% | 164 | Switchable Bina-II Line Reactor / Satna 765KV | 100%
117 | 400/220kV ICT # 2 / Vapi | 100% | 165 | Bus Reactor-II (63 MVAR)/Satna | 100%
118 | 400/220kV ICT # 1 / Gwalior | 100% | 166 | Switchable Bina-I Line Reactor / Gwalior 765KV | 100%
119 | 400/220 KV ICT # 1 / Rajgarh | 100% | 167 | Switchable Bina-II Line Reactor / Gwalior 765KV | 100%
120 | 400/220kV ICT # 2 / Gwalior | 100% | 168 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV | 100%
121 | 400/220kV ICT # 1 / Itarsi | 99.61% | 169 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV | 100%
122 | 400/220kV ICT # 1 / Damoh | 100% | 170 | Bus Reactor-II/Gwalior | 100%
123 | 400/220kV ICT # 2 / Damoh | 100% | 171 | Bus Reactor-III/Gwalior | 100%
124 | 400/220 KV ICT # 2 / Rajgarh | 99.6% | 172 | Bus Reactor-I/Indore | 100%
125 | 400/220 KV ICT / Bina | 100% | 173 | Switchable Indore - Line Reactor / Bina 765KV | 100%
126 | 400/220 KV ICT # 1 / Pirana | 100% | 174 | Switchable Shujalpur-II Line Reactor / Bina 400kV | 100%
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
Availability Bus Reactors =
System Availability :-
Note on B23: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B24: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B25: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B80: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B81: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## INDEX
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR OCTOBER-2013
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 0 | 100 | 100% | 90%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 0 | 100 | 100% | 90%
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432 | 0 | 100 | 100% | 90%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 0 | 100 | 100% | 90%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 0 | 100 | 100% | 90%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 0 | 100 | 100% | 90%
7 | 400 KV V'chal - Jabalpur # 2 | 3 | 13 |  |  | 3.2167 | 0 | 744 | 360 | 2 | 2316 | 720 | 535680 | 0.0043235 | 99.5677 | 99.57% | 90%
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100% | 90%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100% | 90%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100% | 90%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100% | 90%
12 | 400 KV Jabalpur-Sasan |  |  |  |  | 0 | 0 | 744 | 376 | 2 | 0 | 752 | 559488 | 0 | 100 | 100% | 90%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 744 | 21 | 2 | 0 | 42 | 31248 | 0 | 100 | 100% | 90%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 0 | 100 | 100% | 90%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 0 | 100 | 100% | 90%
16 | 400 KV Jabalpur - Itarsi # 4 | 3 | 8 |  |  | 3.1333 | 0 | 744 | 234 | 2 | 1466.4 | 468 | 348192 | 0.0042115 | 99.5789 | 99.58% | 90%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100% | 90%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100% | 90%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100% | 90%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100% | 90%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 0 | 100 | 100% | 90%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 110 | 2 | 0 | 220 | 163680 | 0 | 100 | 100% | 90%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 0 | 100 | 100% | 90%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100% | 90%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100% | 90%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 0 | 100 | 100% | 90%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 0 | 100 | 100% | 90%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 744 | 31.334 | 1 | 0 | 31.334 | 23312.496 | 0 | 100 | 100% | 90%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 55 | 30 |  |  | 55.5 | 0 | 744 | 31.334 | 1 | 1739.037 | 31.334 | 23312.496 | 0.074597 | 92.5403 | 92.54% | 90%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100% | 90%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100% | 90%
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 0 | 100 | 100% | 90%
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 0 | 100 | 100% | 90%
34 | 220 kV Kakrapar - Haldarwa # 1 | 8 | 36 | 14 | 0 | 8.6 | 14 | 730 | 74 | 1 | 636.4 | 74 | 54020 | 0.011781 | 98.8219 | 98.82% | 90%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 1 | 32 | 0 | 1.5333 | 742.4667 | 74 | 1 | 0 | 74 | 54942.5333 | 0 | 100 | 100% | 90%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100% | 90%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100% | 90%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100% | 90%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100% | 90%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100% | 90%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100% | 90%
42 | 400kV V'chal - Satna # 3 | 0 | 14 | 0 | 18 | 0.23333 | 0.3 | 743.7 | 258.31 | 2 | 120.5447 | 516.62 | 384210.294 | 0.00031375 | 99.9686 | 99.97% | 90%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 744 | 100.32 | 2 | 0 | 200.64 | 149276.16 | 0 | 100 | 100% | 90%
44 | 400kV Nigrie-Satna | 0 | 7 |  |  | 0.11667 | 0 | 744 | 161.11 | 2 | 37.5923 | 322.22 | 239731.68 | 0.00015681 | 99.9843 | 99.98% | 90%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100% | 90%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100% | 90%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100% | 90%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100% | 90%
49 | 765 kV Gwalior-Bina # 1 |  |  |  |  | 0 | 0 | 744 | 234.931 | 4 | 0 | 939.724 | 699154.656 | 0 | 100 | 100% | 90% | Upgraded to 765kV level w.e.f 01.04.2013
50 | 400KV Satna-Bina # 4 |  |  | 0 | 6 | 0 | 0.1 | 743.9 | 272.586 | 2 | 0 | 545.172 | 405553.4508 | 0 | 100 | 100% | 90%
51 | 400KV Satna-Bina # 3 | 0 | 5 | 0 | 4 | 0.083333 | 0.066667 | 743.9333 | 272.586 | 2 | 45.431 | 545.172 | 405571.6232 | 0.00011202 | 99.9888 | 99.99% | 90%
52 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100% | 90%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100% | 90%
54 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100% | 90%
55 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100% | 90%
56 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 0 | 100 | 100% | 90%
57 | 400KV Nagda - Dehgam # 1 |  |  | 0 | 18 | 0 | 0.3 | 743.7 | 331.442 | 2 | 0 | 662.884 | 492986.8308 | 0 | 100 | 100% | 90%
58 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 0 | 100 | 100% | 90%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504 | 0 | 100 | 100% | 90%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100% | 90%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 457 | 123 | 0 | 459.05 | 284.95 | 4.01 | 2 | 0 | 8.02 | 2285.299 | 0 | 100 | 100% | 90%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 171 | 63 | 0 | 172.05 | 571.95 | 4.01 | 2 | 0 | 8.02 | 4587.039 | 0 | 100 | 100% | 90%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100% | 90%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100% | 90%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100% | 90%
66 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100% | 90%
67 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100% | 90%
68 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 0 | 100 | 100% | 90%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 0 | 100 | 100% | 90%
70 | 765 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352 | 0 | 100 | 100% | 90% | Upgraded to 765kV level w.e.f 01.04.2013
71 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 0 | 100 | 100% | 90%
72 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 0 | 100 | 100% | 90%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 0 | 100 | 100% | 90%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 0 | 100 | 100% | 90%
75 | 220 KV Vapi - Sayali |  |  | 1 | 30 | 0 | 1.5 | 742.5 | 18.3 | 1 | 0 | 18.3 | 13587.75 | 0 | 100 | 100% | 90%
76 | 220kV Sayali-Khadoli |  |  |  |  | 0 | 0 | 744 | 12.235 | 1 | 0 | 12.235 | 9102.84 | 0 | 100 | 100% | 90%
77 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100% | 90%
78 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100% | 90%
79 | 400kV Dehgam-Pirana#1 | 2 | 24 |  |  | 2.4 | 0 | 744 | 46.67 | 2 | 224.016 | 93.34 | 69444.96 | 0.0032258 | 99.6774 | 99.68% | 90%
80 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 0 | 100 | 100% | 90%
81 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100% | 90%
82 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100% | 90%
83 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100% | 90%
84 | 400kV Bhachau - Ranchodpura # 2 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100% | 90%
85 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 0 | 100 | 100% | 90%
86 | 400kV Mundra - Limbdi # 2 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 0 | 100 | 100% | 90%
87 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 0 | 100 | 100% | 90%
88 | 765kV Satna - Bina # 2 |  |  | 22 | 11 | 0 | 22.1833 | 721.8167 | 275.635 | 4 | 0 | 1102.54 | 795831.7477 | 0 | 100 | 100% | 90%
89 | 765kV Bina - Indore |  |  |  | 32 | 0 | 0.53333 | 743.4667 | 311 | 4 | 0 | 1244 | 924872.5333 | 0 | 100 | 100% | 90% | upgraded to 765kV level w.e.f. 01.07.2013
90 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100% | 90%
91 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100% | 90%
92 | 400kV Mundra-Jetpur#1 |  |  |  |  | 0 | 0 | 744 | 337 | 3 | 0 | 1011 | 752184 | 0 | 100 | 100% | 90%
93 | 400kV Mundra-Jetpur#2 |  |  |  |  | 0 | 0 | 744 | 337 | 3 | 0 | 1011 | 752184 | 0 | 100 | 100% | 90%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100% | 90%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100% | 90%
96 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100% | 90%
97 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100% | 90%
98 | 765kV Sasan - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 245.7 | 4 | 0 | 982.8 | 731203.2 | 0 | 100 | 100% | 90%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.03.2013
100 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 744 | 116.85 | 2 | 0 | 233.7 | 173872.8 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.04.2013
101 | 400kV Vapi-Navsari#2 | 4 | 21 |  |  | 4.35 | 0 | 744 | 116.85 | 2 | 1016.595 | 233.7 | 173872.8 | 0.0058468 | 99.4153 | 99.42% | 90%
102 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 242.23 | 4 | 0 | 968.92 | 720876.48 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.05.2013
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.06.2013
104 | 400kV Indore (MP)-Indore (PG)#1 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.07.2013
105 | 400kV Indore (MP)-Indore (PG)#2 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100% | 90%
| Total Sr.No. 1 to 105 | 75 | 158 | 666 | 347 |  |  |  | 16432.199 |  | 7602.016 |  | 29573061.6711
* | Lines charged with 400kV level
|  | 77.6333 |  | 671.7833
[10 empty] | NAFM | 0.00025706
Availability of ( Sl no 1 to 105) transmission lines during OCTOBER-2013 = | [9 empty] | TAFM | 99.9743
106 | 765 kV Gwalior -Agra # 1 | 0 | 0 | 0 | 26 | 0 | 0.43333 | 743.5667 | 129.435 | 4 | 0 | 517.74 | 384974.206 | 0 | 100 | 100% | 90%
107 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 0 | 100 | 100% | 90%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
108 | 400/220kV ICT # 1 / Jabalpur. | 4 | 29 |  |  | 4.4833 | 0 | 744 | 315 | 2.5 | 3530.625 | 787.5 | 585900 | 0.006026 | 99.3974 | 99.4% | 90%
109 | 400/220kV ICT # 2 /Jabalpur. | 3 | 13 |  |  | 3.2167 | 0 | 744 | 315 | 2.5 | 2533.125 | 787.5 | 585900 | 0.0043235 | 99.5677 | 99.57% | 90%
110 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
111 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90% |  | 0.83333
112 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
113 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
114 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
115 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
116 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
117 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
118 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
119 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
120 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
121 | 400/220kV ICT # 1 / Itarsi | 2 | 56 |  |  | 2.9333 | 0 | 744 | 315 | 2.5 | 2310 | 787.5 | 585900 | 0.0039427 | 99.6057 | 99.61% | 90%
122 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
123 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
124 | 400/220 KV ICT # 2 / Rajgarh | 2 | 58 |  |  | 2.9667 | 0 | 744 | 315 | 2.5 | 2336.25 | 787.5 | 585900 | 0.0039875 | 99.6013 | 99.6% | 90%
125 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
126 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
127 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
128 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
129 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
130 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
131 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
132 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
133 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
134 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
135 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90%
136 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
137 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.03.2013
138 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.04.2013
139 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | 90%
140 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
141 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90%
142 | 765/400KV ICT# 2 / INDORE |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.07.2013
143 | 765/400KV ICT# 1 / INDORE |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.10.2013
144 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
145 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100% | 90%
146 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100% | 90%
147 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
148 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
149 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
150 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
151 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 0 | 100 | 100% | 90%
152 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
153 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
154 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
155 | Bus Reactor-I / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100% | 90%
156 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
157 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
158 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
159 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
160 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
161 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
162 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
163 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
164 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.04.2013
165 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
166 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
167 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
168 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.06.2013
169 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
170 | Bus Reactor-II/Gwalior |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.10.2013
171 | Bus Reactor-III/Gwalior |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
172 | Bus Reactor-I/Indore |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | 90%
173 | Switchable Indore - Line Reactor / Bina 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | 90%
174 | Switchable Shujalpur-II Line Reactor / Bina 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | 90%
| Total of sl no 1 to 31 | 0 | 0 | 0 | 0 |  |  |  | 3263 |  | 0 |  | 9710688
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 31 ( Sl no 1 to 31) Bus Reactors in OCTOBER-2013 = | [7 empty] | TAFM | 100
[11 empty] | #REF! |  | #REF!
[8 empty] | NAFM = | #REF!
% System Availability for OCTOBER-2013 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | #REF!
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B136: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B137: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## Oct'13 Tripping details
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF October'2013
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | OUTAGE HOURS ATTRIBUTED TO | [11 empty] | Outage Category | Details | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM E | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
[7 empty] | ATTRIBUTED TO PGCIL |  |  | OTHERS |  |  | SYSTEM CONSTR. |  |  | OUTAGE DEEMED AVAILABLE |  |  |  |  | TRIPPING | CHARGING
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  |  |  |  | A | B | C | D=A*B*C | 744 | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 |  | SATPURA-ITARSI 400kV |  |  |  |  | - | [5 empty] | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 79 | 2 | 0 | 0 | 744 | 158 | 117552 | 0 | 100%
2 |  | ITARSI-INDORE I 400kV | [7 empty] | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 207 | 2 | 0 | 0 | 744 | 414 | 308016 | 0 | 100%
3 |  | ITARSI-INDORE II 400kV |  |  |  |  | - | [5 empty] | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 214 | 2 | 0 | 0 | 744 | 428 | 318432 | 0 | 100%
4 |  | INDORE-ASOJ I 400kV |  |  |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 289 | 2 | 0 | 0 | 744 | 578 | 430032 | 0 | 100%
5 | 910039 | INDORE-ASOJ II 400kV | 2013-10-09 | 01:15 | 2013-10-09 | 07:37 | - |  |  | - |  |  | - |  |  | 0.26528 | 6 | 22 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/584 | LD10/592
| 910090 | INDORE-ASOJ II 400kV | 2013-10-22 | 19:22 | 2013-10-22 | 19:22 | 0 | 0 | 0 | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully on Y ph to E/F from both ends.F/L:254km from asoj,36.62km from indore,F/C:6.7kA(indr),1.405kA(asoj),LL:291km, middle ph
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26528 | 6 | 22
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.3667 |  |  |  |  | 273 | 2 | 0 | 0 | 744 | 546 | 406224 | 0 | 100%
6 | 910089 | VINDHYACHAL-JABALPUR I 400kV | 2013-10-22 | 09:52 | 2013-10-23 | 09:28 | - |  |  | - |  |  | - |  |  | 0.98333 | 23 | 36 | OSPD | Line H/T to avail OCC S/D by NTPC for LMU replacement and shunt reactor testing | LD10/.1483 | LD 10/1562
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98333 | 23 | 36
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 23.6 |  |  |  |  | 360 | 2 | 0 | 0 | 744 | 720 | 535680 | 0 | 100%
7 | 910093 | VINDHYACHAL-JABALPUR II 400kV | 2013-10-23 | 10:41 | 2013-10-24 | 13:32 | - |  |  | - |  |  | - |  |  | 1899-12-31 02:51 | 26 | 51 | OSPD | Line H/T to avail OCC S/D for replacement of LMU by NTPC V'chal. | LD10/1579 | LD10/1670
| 910115 | VINDHYACHAL-JABALPUR II 400kV | 2013-10-29 | 12:52 | 2013-10-29 | 16:05 | 0.13403 | 3 | 13 | - |  |  | - |  |  | - |  |  | OSFT | Line H/T to avail emergency S/d for repair of melted and hanging top ph jumper at loc 742 | LD10/2032 | LD10/2041
|  | SUBTOTAL |  |  |  |  | 0.13403 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 02:51 | 26 | 51
|  | Element Availability= | [6 empty] | 3.2167 |  |  | 0 |  |  | 0 |  |  | 26.85 |  |  |  |  | 360 | 2 | 3.2167 | 2316 | 744 | 720 | 535680 | 0.0043235 | 99.57%
8 |  | JABALPUR-ITARSI I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 232 | 2 | 0 | 0 | 744 | 464 | 345216 | 0 | 100%
9 |  | JABALPUR-ITARSI II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 232 | 2 | 0 | 0 | 744 | 464 | 345216 | 0 | 100%
10 |  | GANDHAR-DEHGAM I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 744 | 314 | 233616 | 0 | 100%
11 |  | GANDHAR-DEHGAM II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 744 | 314 | 233616 | 0 | 100%
12 | 910098 | VINDHYACHAL(NTPC)-SASAN III (RELIANCE) 400KV | 2013-10-25 | 09:45 | 2013-10-25 | 20:11 | - |  |  | - |  |  | - |  |  | 0.43472 | 10 | 26 | OSPD | Line H/T to avail outage by SASAN | LD10/1723 | LD10/1765
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43472 | 10 | 26
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.4333 |  |  |  |  | 376 | 2 | 0 | 0 | 744 | 752 | 559488 | 0 | 100%
13 |  | 400kV Sasan-Vindhyachal
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21 | 2 | 0 | 0 | 744 | 42 | 31248 | 0 | 100%
14 | 910031 | VINDHYACHAL-JABALPUR IV 400kV | 2013-10-07 | 05:18 | 2013-10-07 | 05:18 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully on B ph to E/F,F/L:294.5km from JBP,70.79km from V'chal,F/C:1.15kA
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 389 | 2 | 0 | 0 | 744 | 778 | 578832 | 0 | 100%
15 |  | JABALPUR-ITARSI III 400kV |  |  |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 234 | 2 | 0 | 0 | 744 | 468 | 348192 | 0 | 100%
16 | 909094 | JABALPUR-ITARSI IV 400kV | 2013-09-20 | 16:06 | 2013-10-09 | 09:04 | - |  |  | - |  |  | - |  |  | 1900-01-07 09:04 | 201 | 4 | LVRD | Line kept out on Voltage regulation as per WRLDC Instruction. | LD09/1485 | LD 10/591
| 910043 | JABALPUR-ITARSI IV 400kV | 2013-10-09 | 23:44 | 2013-10-17 | 09:56 | - |  |  | - |  |  | - |  |  | 1900-01-06 10:12 | 178 | 12 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/646 | LD 10/1153
| 910092 | JABALPUR-ITARSI IV 400kV | 2013-10-23 | 10:20 | 2013-10-23 | 13:28 | 0.13056 | 3 | 8 | - |  |  | - |  |  | - |  |  | OSFT | Line H/T to avail emergency S/D for replacing decapped flashed over string at Loc 600. | LD10/1567 | LD10/1596
|  | SUBTOTAL |  |  |  |  | 0.13056 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-14 19:16 | 379 | 16
|  | Element Availability= | [6 empty] | 3.1333 |  |  | 0 |  |  | 0 |  |  | 379.2667 |  |  |  |  | 234 | 2 | 3.1333 | 1466.4 | 744 | 468 | 348192 | 0.0042115 | 99.58%
17 | 910011 | ITARSI-KHANDWA I 400kV | 2013-10-03 | 20:55 | 2013-10-05 | 10:13 | - |  |  | - |  |  | - |  |  | 1899-12-31 13:18 | 37 | 18 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/200 | LD 10/329
| 910022 | ITARSI-KHANDWA I 400kV | 2013-10-05 | 11:36 | 2013-10-25 | 09:58 | - |  |  | - |  |  | - |  |  | 1900-01-18 22:22 | 478 | 22 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/341 | LD 10/1727
| 910109 | ITARSI-KHANDWA I 400kV | 2013-10-29 | 00:15 | 2013-10-29 | 06:16 | - |  |  | - |  |  | - |  |  | 0.25069 | 6 | 1 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1983 | LD10/1993
| 910117 | ITARSI-KHANDWA I 400kV | 2013-10-29 | 21:19 | 2013-10-30 | 06:13 | - |  |  | - |  |  | - |  |  | 0.37083 | 8 | 54 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/2076 | LD10/2094
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-21 02:35 | 529 | 95
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 530.5833 |  |  |  |  | 196.64 | 2 | 0 | 0 | 744 | 393.28 | 292600.32 | 0 | 100%
18 | 909136 | ITARSI-KHANDWA II 400kV | 2013-09-26 | 21:54 | 2013-10-03 | 09:54 | - |  |  | - |  |  | - |  |  | 1900-01-01 09:54 | 57 | 54 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2060 | LD 10/156
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 09:54 | 57 | 54
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 57.9 |  |  |  |  | 196.64 | 2 | 0 | 0 | 744 | 393.28 | 292600.32 | 0 | 100%
19 |  | KHANDWA-DHULE I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 261.78 | 2 | 0 | 0 | 744 | 523.56 | 389528.64 | 0 | 100%
20 |  | KHANDWA-DHULE II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 261.78 | 2 | 0 | 0 | 744 | 523.56 | 389528.64 | 0 | 100%
21 |  | JHANOR - SUGEN 400kV | [17 empty] | Line H/T for power regulation on WRLDC Instruction | LD 08/524 | LD 08/539
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 57 | 2 | 0 | 0 | 744 | 114 | 84816 | 0 | 100%
22 |  | SUGEN-VAPI 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 110 | 2 | 0 | 0 | 744 | 220 | 163680 | 0 | 100%
23 |  | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 2 | 0 | 0 | 744 | 26 | 19344 | 0 | 100%
24 |  | JHANOR - HALDARWA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 744 | 13 | 9672 | 0 | 100%
25 |  | JHANOR - HALDARWA II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 744 | 13 | 9672 | 0 | 100%
26 |  | KAWAS-NAVSARI (PG GIS) I 220kV | [7 empty] | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 58.149 | 1 | 0 | 0 | 744 | 58.149 | 43262.856 | 0 | 100%
27 |  | KAWAS-NAVSARI II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 58.149 | 1 | 0 | 0 | 744 | 58.149 | 43262.856 | 0 | 100%
28 | 910008 | NAVSARI (PG GIS)-NAVSARI I 220kV | 2013-10-03 | 09:51 | 2013-10-03 | 13:23 | - |  |  | - |  |  | - |  |  | 0.14722 | 3 | 32 | OSPD | Line H/T to avail OCC approved S/D by Getco for logic Test. | LD10/160 | LD10/173
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14722 | 3 | 32
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 3.5333 |  |  |  |  | 31.334 | 1 | 0 | 0 | 744 | 31.334 | 23312.496 | 0 | 100%
29 | 910005 | NAVSARI (PG GIS)-NAVSARI II 220kV | 2013-10-02 | 09:05 | 2013-10-02 | 16:23 | - |  |  | - |  |  | - |  |  | 0.30417 | 7 | 18 | OSPD | Line H/T to avail S/D by GETCO for logic check of relay | LD10/88 | LD10/121
| 910085 | NAVSARI (PG GIS)-NAVSARI II 220kV | 2013-10-21 | 10:20 | 2013-10-23 | 17:50 | 1900-01-01 07:30 | 55 | 30 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC Approved S/D for atteding Sf6 leakege | LD10/1402 | LD 10/1614
|  | SUBTOTAL |  |  |  |  | 1900-01-01 07:30 | 55 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30417 | 7 | 18
|  | Element Availability= | [6 empty] | 55.5 |  |  | 0 |  |  | 0 |  |  | 7.3 |  |  |  |  | 31.334 | 1 | 55.5 | 1739.037 | 744 | 31.334 | 23312.496 | 0.074597 | 92.54%
30 | 910013 | KAWAS-VAV I 220kV | 2013-10-03 | 21:40 | 2013-10-14 | 20:12 | - |  |  | - |  |  | - |  |  | 1900-01-09 22:32 | 262 | 32 | LPRD | Line H/T for power regulation on WRLDC instruction |  | LD 09/846
| 910071 | KAWAS-VAV I 220kV | 2013-10-17 | 01:39 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-13 22:21 | 358 | 21 | LPRD | Line H/T for Power Regulation on WRLDC Instruction | LD 10/1200
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-24 20:53 | 620 | 53
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 620.8833 |  |  |  |  | 37 | 1 | 0 | 0 | 744 | 37 | 27528 | 0 | 100%
31 |  | KAWAS-VAV II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 37 | 1 | 0 | 0 | 744 | 37 | 27528 | 0 | 100%
32 | 910111 | KAWAS-HALDARWA I 220kV | 2013-10-29 | 10:05 | 2013-10-29 | 23:14 | - |  |  | - |  |  | - |  |  | 0.54792 | 13 | 9 | OSPD | Line H/T to avail S/D by GETCO for construction work | LD10/2011 | LD10/2066
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54792 | 13 | 9
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 13.15 |  |  |  |  | 81 | 1 | 0 | 0 | 744 | 81 | 60264 | 0 | 100%
33 | 910112 | KAWAS-HALDARWA II 220kV | 2013-10-29 | 10:10 | 2013-10-29 | 20:44 | - |  |  | - |  |  | - |  |  | 0.44028 | 10 | 34 | OSPD | Line H/T to avail S/D by GETCO for construction work | LD10/2011 | LD10/2067
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44028 | 10 | 34
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.5667 |  |  |  |  | 81 | 1 | 0 | 0 | 744 | 81 | 60264 | 0 | 100%
34 | 910010 | KAKRAPAR-HALDARWA I 220kV | 2013-10-03 | 15:30 | 2013-10-04 | 14:06 | 0.35833 | 8 | 36 | 0.58333 | 14 | 0 | - |  |  | - |  |  | LHWT | Line A/T on R-ph to E/F, F/L - 65.6kms from Haldarwa end due to Flashover of Insulator string at loc no. 33. Outage from 19:00hrs/03.10.13 to 09:00hrs/04.10.13 shall not be attributable to POWERGRID account as Restoration work could not be started due to adverse weather condition and Night hours |  | LD 10/248
|  | SUBTOTAL |  |  |  |  | 0.35833 | 8 | 36 | 0.58333 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 8.6 |  |  | 14 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 8.6 | 636.4 | 730 | 74 | 54020 | 0.011781 | 98.82%
35 | 910012 | KAKRAPAR-HALDARWA II 220kV | 2013-10-03 | 21:12 | 2013-10-03 | 22:44 | - |  |  | 0.063889 | 1 | 32 | - |  |  | - |  |  | OMSU | Line H/T on emergency due to failure of AC supply at Haldarwa end(Getco) | LD10/202 | LD10/207
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.063889 | 1 | 32 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 1.5333 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 0 | 0 | 742.4667 | 74 | 54942.5333 | 0 | 100%
36 |  | KAKRAPAR-VAV I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 43 | 1 | 0 | 0 | 744 | 43 | 31992 | 0 | 100%
37 |  | KAKRAPAR-VAV II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 43 | 1 | 0 | 0 | 744 | 43 | 31992 | 0 | 100%
38 |  | KAKRAPAR-VAPI I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 117 | 1 | 0 | 0 | 744 | 117 | 87048 | 0 | 100%
39 |  | KAKRAPAR-VAPI II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 117 | 1 | 0 | 0 | 744 | 117 | 87048 | 0 | 100%
40 |  | VINDHYACHAL-SATNA I 400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 744 | 534 | 397296 | 0 | 100%
41 |  | VINDHYACHAL-SATNA II 400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 744 | 534 | 397296 | 0 | 100%
42 | 910105 | VINDHYACHAL-SATNA III 400kV | 2013-10-28 | 10:36 | 2013-10-28 | 10:50 | 0.0097222 | 0 | 14 | - |  |  | - |  |  | - |  |  | OMST | LINE H/T TO TAKE L/R AT SATNA END OUT TO TAKE BUSHING OIL SAMPLE | LD10/1926 | LD10/1929
| 910113 | VINDHYACHAL-SATNA III 400kV | 2013-10-29 | 10:34 | 2013-10-29 | 10:52 | - |  |  | 0.0125 | 0 | 18 | - |  |  | - |  |  | OMSU | Line H/T to take L/R at satna end in service. | LD10/2017 | LD10/2017
|  | SUBTOTAL |  |  |  |  | 0.0097222 | 0 | 14 | 0.0125 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.23333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 258.31 | 2 | 0.23333 | 120.5447 | 744 | 516.62 | 384365.28 | 0.00031362 | 99.97%
43 |  | VINDHYACHAL-NIGRIE 400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 100.32 | 2 | 0 | 0 | 744 | 200.64 | 149276.16 | 0 | 100%
44 | 910114 | Satna -Nigrie 400kV | 2013-10-29 | 11:52 | 2013-10-29 | 11:59 | 0.0048611 | 0 | 7 | - |  |  | - |  |  | - |  |  | OMST | Line H/T to take out L/R at satna end to take oil sample of reactor bushing | LD10/2022 | LD10/2022
|  | SUBTOTAL |  |  |  |  | 0.0048611 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.11667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 161.11 | 2 | 0.11667 | 37.5923 | 744 | 322.22 | 239731.68 | 0.00015681 | 99.98%
45 | 910003 | SATNA-BINA(PG) I 400kV | 2013-10-01 | 12:11 | 2013-10-05 | 10:38 | - |  |  | - |  |  | - |  |  | 1900-01-02 22:27 | 94 | 27 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/30 | LD 10/329
| 910047 | SATNA-BINA(PG) I 400kV | 2013-10-11 | 07:59 | 2013-10-11 | 14:50 | - |  |  | - |  |  | - |  |  | 0.28542 | 6 | 51 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/738 | LD 10/765
| 910054 | SATNA-BINA(PG) I 400kV | 2013-10-12 | 22:40 | 2013-10-14 | 10:42 | - |  |  | - |  |  | - |  |  | 1899-12-31 12:02 | 36 | 2 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/875 | LD 10/995
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-04 17:20 | 136 | 80
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 137.3333 |  |  |  |  | 276 | 2 | 0 | 0 | 744 | 552 | 410688 | 0 | 100%
46 | 910026 | SATNA-BINA(PG) II 400kV | 2013-10-06 | 00:06 | 2013-10-10 | 18:40 | - |  |  | - |  |  | - |  |  | 1900-01-03 18:34 | 114 | 34 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/392 | LD 10/695
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 18:34 | 114 | 34
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 114.5667 |  |  |  |  | 276 | 2 | 0 | 0 | 744 | 552 | 410688 | 0 | 100%
47 |  | BINA(PG)-BINA(MPEB) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 744 | 1.484 | 1104.096 | 0 | 100%
48 |  | BINA(PG)-BINA(MPEB) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 744 | 1.484 | 1104.096 | 0 | 100%
49 |  | GWALIOR-BINA I 765KV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 234.931 | 4 | 0 | 0 | 744 | 939.724 | 699154.656 | 0 | 100%
50 | 910088 | Satna - Bina IV 400kV | 2013-10-22 | 00:57 | 2013-10-22 | 07:12 | - |  |  | - |  |  | - |  |  | 0.26042 | 6 | 15 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1452 | LD10/1468
| 910103 | Satna - Bina IV 400kV | 2013-10-27 | 09:39 | 2013-10-27 | 09:45 | - |  |  | 0.0041667 | 0 | 6 | - |  |  | - |  |  | OMSU | Line H/T to take line reactor back into service on WRLDC Instruction | LD10/1855 | LD10/1856
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.0041667 | 0 | 6 | 0 | 0 | 0 | 0.26042 | 6 | 15
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.25 |  |  |  |  | 272.586 | 2 | 0 | 0 | 744 | 545.172 | 405607.968 | 0 | 100%
51 | 910083 | Satna - Bina III 400 KV | 2013-10-20 | 21:56 | 2013-10-21 | 06:46 | - |  |  | - |  |  | - |  |  | 0.36806 | 8 | 50 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1372 | LD10/1391
| 910100 | Satna - Bina III 400 KV | 2013-10-26 | 11:28 | 2013-10-26 | 11:33 | 0.0034722 | 0 | 5 | - |  |  | - |  |  | - |  |  | OMST | Line H/T to take oil sample of bushing of L/R | LD10/1795 | LD10/1797
| 910107 | Satna - Bina III 400 KV | 2013-10-28 | 12:05 | 2013-10-28 | 12:09 | - |  |  | 0.0027778 | 0 | 4 | - |  |  | - |  |  | OMSU | Line H/T to take line reactor at Satna end in service. | LD10/1936 | LD10/1937
|  | SUBTOTAL |  |  |  |  | 0.0034722 | 0 | 5 | 0.0027778 | 0 | 4 | 0 | 0 | 0 | 0.36806 | 8 | 50
|  | Element Availability= | [6 empty] | 0.083333 |  |  | 0.066667 |  |  | 0 |  |  | 8.8333 |  |  |  |  | 272.586 | 2 | 0.083333 | 45.431 | 743.9333 | 545.172 | 405571.6232 | 0.00011202 | 99.99%
52 | 910015 | BINA-SHUJALPUR I 400kV | 2013-10-04 | 04:47 | 2013-10-04 | 18:07 | - |  |  | - |  |  | - |  |  | 0.55556 | 13 | 20 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/212 | LD10/272
| 910018 | BINA-SHUJALPUR I 400kV | 2013-10-04 | 21:47 | 2013-10-05 | 08:04 | - |  |  | - |  |  | - |  |  | 0.42847 | 10 | 17 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/288 | LD10/309
| 910024 | BINA-SHUJALPUR I 400kV | 2013-10-05 | 23:47 | 2013-10-07 | 07:15 | - |  |  | - |  |  | - |  |  | 1899-12-31 07:28 | 31 | 28 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/389 | LD 10/452
| 910045 | BINA-SHUJALPUR I 400kV | 2013-10-11 | 00:45 | 2013-10-11 | 10:39 | - |  |  | - |  |  | - |  |  | 0.4125 | 9 | 54 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/725 | LD10/749
| 910049 | BINA-SHUJALPUR I 400kV | 2013-10-11 | 23:49 | 2013-10-12 | 15:55 | - |  |  | - |  |  | - |  |  | 0.67083 | 16 | 6 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/800 | LD 10/844
| 910055 | BINA-SHUJALPUR I 400kV | 2013-10-13 | 01:36 | 2013-10-13 | 07:11 | - |  |  | - |  |  | - |  |  | 0.23264 | 5 | 35 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/885 | LD 10905
| 910059 | BINA-SHUJALPUR I 400kV | 2013-10-13 | 13:11 | 2013-10-13 | 19:09 | - |  |  | - |  |  | - |  |  | 0.24861 | 5 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/930 | LD 10/954
| 910061 | BINA-SHUJALPUR I 400kV | 2013-10-14 | 01:31 | 2013-10-14 | 07:09 | - |  |  | - |  |  | - |  |  | 0.23472 | 5 | 38 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/973 | LD10/981
| 910069 | BINA-SHUJALPUR I 400kV | 2013-10-17 | 00:31 | 2013-10-17 | 09:14 | - |  |  | - |  |  | - |  |  | 0.36319 | 8 | 43 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1141 | LD10/1149
| 910077 | BINA-SHUJALPUR I 400kV | 2013-10-20 | 03:25 | 2013-10-20 | 08:17 | - |  |  | - |  |  | - |  |  | 0.20278 | 4 | 52 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1332 | LD 10/1340
| 910110 | BINA-SHUJALPUR I 400kV | 2013-10-29 | 00:22 | 2013-10-29 | 06:26 | - |  |  | - |  |  | - |  |  | 0.25278 | 6 | 4 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1984 | LD10/1992
| 910118 | BINA-SHUJALPUR I 400kV | 2013-10-29 | 21:21 | 2013-10-30 | 06:16 | - |  |  | - |  |  | - |  |  | 0.37153 | 8 | 55 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/2075 | LD10/2093
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-04 06:50 | 120 | 410
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 126.8333 |  |  |  |  | 199.936 | 2 | 0 | 0 | 744 | 399.872 | 297504.768 | 0 | 100%
53 | 910063 | BINA-SHUJALPUR II 400kV | 2013-10-14 | 21:51 | 2013-10-15 | 07:48 | - |  |  | - |  |  | - |  |  | 0.41458 | 9 | 57 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/1025 | LD 10/1036
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41458 | 9 | 57
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.95 |  |  |  |  | 199.936 | 2 | 0 | 0 | 744 | 399.872 | 297504.768 | 0 | 100%
54 | 910019 | SHUJALPUR-NAGDA I 400kV | 2013-10-05 | 01:03 | 2013-10-05 | 07:46 | - |  |  | - |  |  | - |  |  | 0.27986 | 6 | 43 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/296 | LD10/310
| 910038 | SHUJALPUR-NAGDA I 400kV | 2013-10-09 | 00:45 | 2013-10-10 | 07:30 | - |  |  | - |  |  | - |  |  | 1899-12-31 06:45 | 30 | 45 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/579 | LD 10/652
| 910046 | SHUJALPUR-NAGDA I 400kV | 2013-10-11 | 03:30 | 2013-10-11 | 10:41 | - |  |  | - |  |  | - |  |  | 0.29931 | 7 | 11 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/732 | LD10/750
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 20:39 | 43 | 99
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 44.65 |  |  |  |  | 152.229 | 2 | 0 | 0 | 744 | 304.458 | 226516.752 | 0 | 100%
55 | 910050 | SHUJALPUR-NAGDA II 400kV | 2013-10-12 | 01:51 | 2013-10-12 | 15:46 | - |  |  | - |  |  | - |  |  | 0.57986 | 13 | 55 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/804 | LD 10/845
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57986 | 13 | 55
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 13.9167 |  |  |  |  | 152.229 | 2 | 0 | 0 | 744 | 304.458 | 226516.752 | 0 | 100%
56 | 910014 | NAGDA-DEHGAM II 400kV | 2013-10-04 | 02:55 | 2013-10-04 | 07:55 | - |  |  | - |  |  | - |  |  | 0.20833 | 5 | 0 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 010/211 | LD 10/220
| 910051 | NAGDA-DEHGAM II 400KV | 2013-10-12 | 07:08 | 2013-10-18 | 19:27 | - |  |  | - |  |  | - |  |  | 1900-01-05 12:19 | 156 | 19 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/811 | LD 10/1257
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-05 17:19 | 161 | 19
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 161.3167 |  |  |  |  | 331.442 | 2 | 0 | 0 | 744 | 662.884 | 493185.696 | 0 | 100%
57 | 910004 | NAGDA-DEHGAM I 400KV | 2013-10-02 | 01:13 | 2013-10-02 | 08:01 | - |  |  | - |  |  | - |  |  | 0.28333 | 6 | 48 | LVRD | Line kept out on voltage regulation on WRLDC instruction | LD10/78 | LD10/84
| 910006 | NAGDA-DEHGAM I 400KV | 2013-10-03 | 01:10 | 2013-10-03 | 08:31 | - |  |  | - |  |  | - |  |  | 0.30625 | 7 | 21 | LVRD | Line kept out on voltage regulation on WRLDC instruction | LD10/143 | LD10/149
| 910028 | NAGDA-DEHGAM I 400KV | 2013-10-06 | 19:23 | 2013-10-06 | 19:23 | 0 | 0 | 0 | - |  |  | - |  |  | - |  |  | LART | A/R successfully at dehgam end only and A/T from Nagda MPPTCL end on R-ph to E/F, F/L - 233km from Dehgam & 99.5kM from Nagda end.
| 910029 | NAGDA-DEHGAM I 400KV | 2013-10-06 | 19:23 | 2013-10-06 | 19:41 | - |  |  | 0.0125 | 0 | 18 | - |  |  | - |  |  | OMSU | A/R successfully at dehgam end only and A/R attemt failed at Nagda MPPTCL end on R-ph to E/F due to problem at Nagda MPPTCL , F/L - 233km from Dehgam & 99.5kM from Nagda end.
| 910030 | NAGDA-DEHGAM I 400KV | 2013-10-07 | 03:18 | 2013-10-12 | 06:57 | - |  |  | - |  |  | - |  |  | 1900-01-04 03:39 | 123 | 39 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/445 | LD 10/809
| 910078 | NAGDA-DEHGAM I 400KV | 2013-10-20 | 03:29 | 2013-10-20 | 10:27 | - |  |  | - |  |  | - |  |  | 0.29028 | 6 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1333 | LD 10/1345
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.0125 | 0 | 18 | 0 | 0 | 0 | 1900-01-05 00:46 | 142 | 166
|  | Element Availability= | [6 empty] | 0 |  |  | 0.3 |  |  | 0 |  |  | 144.7667 |  |  |  |  | 331.442 | 2 | 0 | 0 | 743.7 | 662.884 | 492986.8308 | 0 | 100%
58 | 910027 | SEONI-KHANDWA I 400kV | 2013-10-06 | 12:55 | 2013-10-07 | 06:56 | - |  |  | - |  |  | - |  |  | 0.75069 | 18 | 1 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/418
| 910034 | SEONI-KHANDWA I 400kV | 2013-10-07 | 23:51 | 2013-10-08 | 06:31 | - |  |  | - |  |  | - |  |  | 0.27778 | 6 | 40 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/510 | LD 10/525
| 910037 | SEONI-KHANDWA I 400kV | 2013-10-09 | 00:28 | 2013-10-12 | 14:16 | - |  |  | - |  |  | - |  |  | 1900-01-02 13:48 | 85 | 48 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/578 | LD 10/841
| 910056 | SEONI-KHANDWA I 400kV | 2013-10-13 | 02:15 | 2013-10-13 | 02:25 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | A/T on operation of O/V STG-I protection at Khandwa s/s.
| 910057 | SEONI-KHANDWA I 400kV | 2013-10-13 | 02:25 | 2013-10-13 | 08:07 | - |  |  | - |  |  | - |  |  | 0.2375 | 5 | 42 | LVRD | Line kept out on V/R as per WRLDC Instruction. |  | LD10/913
| 910058 | SEONI-KHANDWA I 400kV | 2013-10-13 | 11:01 | 2013-10-13 | 18:35 | - |  |  | - |  |  | - |  |  | 0.31528 | 7 | 34 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/922 | LD 10/952
| 910065 | SEONI-KHANDWA I 400kV | 2013-10-14 | 23:53 | 2013-10-15 | 07:18 | - |  |  | - |  |  | - |  |  | 0.30903 | 7 | 25 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/1029 | LD 10/1035
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069444 | 0 | 10 | 1900-01-04 11:10 | 128 | 190
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 131.1667 |  |  |  |  | 351.729 | 4 | 0 | 0 | 743.8333 | 1406.916 | 1046511.018 | 0 | 100%
59 | 910007 | SEONI-KHANDWA II 400kV | 2013-10-03 | 03:48 | 2013-10-03 | 09:15 | - |  |  | - |  |  | - |  |  | 0.22708 | 5 | 27 | LVRD | Line kept out on voltage regulation on WRLDC instruction | LD10/144 | LD10/151
| 910070 | SEONI-KHANDWA II 400kV | 2013-10-17 | 00:33 | 2013-10-17 | 09:31 | - |  |  | - |  |  | - |  |  | 0.37361 | 8 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1140 | LD10/1151
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60069 | 13 | 85
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 14.4167 |  |  |  |  | 351.729 | 4 | 0 | 0 | 744 | 1406.916 | 1046745.504 | 0 | 100%
60 | 909157 | KHANDWA-RAJGARH II 400kV | 2013-09-30 | 12:16 | 2013-10-05 | 10:11 | - |  |  | - |  |  | - |  |  | 1900-01-03 10:11 | 106 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/2296 | LD 10/324
| 910025 | KHANDWA-RAJGARH II 400kV | 2013-10-05 | 23:59 | 2013-10-09 | 08:21 | - |  |  | - |  |  | - |  |  | 1900-01-02 08:22 | 80 | 22 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/390 | LD 10/590
| 910042 | KHANDWA-RAJGARH II 400kV | 2013-10-09 | 13:08 | 2013-10-16 | 11:31 | - |  |  | - |  |  | - |  |  | 1900-01-05 22:23 | 166 | 23 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/617 | LD 10/1109
| 910074 | KHANDWA-RAJGARH II 400kV | 2013-10-17 | 21:42 | 2013-10-20 | 08:16 | - |  |  | - |  |  | - |  |  | 1900-01-01 10:34 | 58 | 34 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/1190 | LD 10/1341
| 910082 | KHANDWA-RAJGARH II 400kV | 2013-10-20 | 22:00 | 2013-10-22 | 14:25 | - |  |  | - |  |  | - |  |  | 1899-12-31 16:25 | 40 | 25 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1373 | LD 10/1509
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-17 19:55 | 450 | 115
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 451.9167 |  |  |  |  | 220.588 | 2 | 0 | 0 | 744 | 441.176 | 328234.944 | 0 | 100%
61 | 909097 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-09-20 | 23:04 | 2013-10-04 | 14:22 | - |  |  | - |  |  | - |  |  | 1900-01-02 14:22 | 86 | 22 | LVRD | Line kept out on Voltage regulation as per WRLDC Instruction. | LD09/1514 | LD 10/249
| 910020 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-10-05 | 04:56 | 2013-10-20 | 12:25 | - |  |  | 1900-01-14 07:29 | 367 | 29 | - |  |  | - |  |  | OMSU | Line A/T on R ph to E/F, 145km from Rajgarh end,F/C:1.3kA//3.1km from SSP, F/C:15.7kA ( Beyond POWERGRID juridiction). |  | LD 10/1349
| 910081 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-10-20 | 21:13 | 2013-10-20 | 21:55 | - |  |  | 0.029167 | 0 | 42 | - |  |  | - |  |  | OMSU | Line A/T on R ph to E/F, 82km from Rajgarh end, ( Beyond POWERGRID juridiction). |  | LD10/1371
| 910087 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2013-10-21 | 13:49 | 2013-10-25 | 08:41 | - |  |  | 1900-01-02 18:52 | 90 | 52 | - |  |  | - |  |  | OMSU | Line A/T on R ph to E/F, 118km from SSP end,F/C:2.5kA ( Beyond POWERGRID juridiction). |  | LD 10/1713
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-18 03:03 | 457 | 123 | 0 | 0 | 0 | 1900-01-02 14:22 | 86 | 22
|  | Element Availability= | [6 empty] | 0 |  |  | 459.05 |  |  | 0 |  |  | 86.3667 |  |  |  |  | 4.01 | 2 | 0 | 0 | 284.95 | 8.02 | 2285.299 | 0 | 100%
62 | 910079 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-10-20 | 11:40 | 2013-10-21 | 14:30 | - |  |  | 1899-12-31 02:50 | 26 | 50 | - |  |  | - |  |  | OMSU | Line A/T on B ph to E/F, 108km from Rajgarh end,F/C:2.9kA ( Beyond POWERGRID juridiction). |  | LD 10/1420
| 910097 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-10-25 | 09:39 | 2013-10-31 | 10:42 | - |  |  | 1900-01-05 01:03 | 145 | 3 | - |  |  | - |  |  | OMSU | Line H/T to avail outage by MPPTCL | LD10/1722 | LD10/2219
| 910121 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-10-31 | 11:12 | 2013-10-31 | 11:12 | - |  |  | 0 | 0 | 0 | - |  |  | - |  |  | OMSU | Line A/R successfully on Y ph to E/F.5km from Rajgarh( Beyond Power grid jurisdiction )
| 910122 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-10-31 | 18:02 | 2013-10-31 | 18:12 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V protection at Rajgarh SS.
| 910123 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2013-10-31 | 18:12 |  |  | - |  |  | - |  |  | - |  |  | 0.24167 | 5 | 48 | LVRD | After tripping on O/V Line Kept out on voltage regulation as per instruction of WRLDC.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-06 03:53 | 171 | 53 | 0.0069444 | 0 | 10 | 0.24167 | 5 | 48
|  | Element Availability= | [6 empty] | 0 |  |  | 171.8833 |  |  | 0.16667 |  |  | 5.8 |  |  |  |  | 4.01 | 2 | 0 | 0 | 571.95 | 8.02 | 4587.039 | 0 | 100%
63 | 910009 | RAJGARH-NAGDA I 400kV (LILO) | 2013-10-03 | 10:15 | 2013-10-04 | 09:30 | - |  |  | - |  |  | - |  |  | 0.96875 | 23 | 15 | OSPD | Line H/T for line maintenance work by MPPTCL | LD10/154 | LD 10/221
| 910021 | RAJGARH-NAGDA I 400kV (LILO) | 2013-10-05 | 10:38 | 2013-10-21 | 13:38 | - |  |  | - |  |  | - |  |  | 1900-01-15 03:00 | 387 | 0 | OSPD | Line H/T to avail outage by MPPTCL for maintenance work | LD10/331 | LD 10/1416
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-16 02:15 | 410 | 15
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 410.25 |  |  |  |  | 4.12 | 2 | 0 | 0 | 744 | 8.24 | 6130.56 | 0 | 100%
64 | 909135 | RAJGARH-NAGDA II 400kV (LILO) | 2013-09-26 | 12:22 | 2013-10-03 | 10:04 | - |  |  | - |  |  | - |  |  | 1900-01-01 10:04 | 58 | 4 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2035 | LD 10/153
| 910016 | RAJGARH-NAGDA II 400kV (LILO) | 2013-10-04 | 09:54 | 2013-10-05 | 10:08 | - |  |  | - |  |  | - |  |  | 1899-12-31 00:14 | 24 | 14 | OSPD | Line H/T to avail OCC Approved S/D by MPPTCL | LD 10/230 | LD 10/320
| 910086 | RAJGARH-NAGDA II 400kV (LILO) | 2013-10-21 | 13:24 | 2013-10-30 | 09:22 | - |  |  | - |  |  | - |  |  | 1900-01-07 19:58 | 211 | 58 | OSPD | Line H/T to avail S/D by MPPTCL | LD10/1417 | LD 10/2100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-11 06:16 | 293 | 76
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 294.2667 |  |  |  |  | 4.12 | 2 | 0 | 0 | 744 | 8.24 | 6130.56 | 0 | 100%
65 | 909153 | KHANDWA-RAJGARH I 400kV | 2013-09-29 | 21:29 | 2013-10-05 | 07:58 | - |  |  | - |  |  | - |  |  | 1900-01-03 07:58 | 103 | 58 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/2254 | LD 10/308
| 910023 | KHANDWA-RAJGARH I 400kV | 2013-10-05 | 16:09 | 2013-10-07 | 10:42 | - |  |  | - |  |  | - |  |  | 1899-12-31 18:33 | 42 | 33 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/360 | LD 10/473
| 910033 | KHANDWA-RAJGARH I 400kV | 2013-10-07 | 21:24 | 2013-10-12 | 15:49 | - |  |  | - |  |  | - |  |  | 1900-01-03 18:25 | 114 | 25 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/505 | LD 10/847
| 910053 | KHANDWA-RAJGARH I 400kV | 2013-10-12 | 22:24 | 2013-10-18 | 16:03 | - |  |  | - |  |  | - |  |  | 1900-01-04 17:39 | 137 | 39 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/874 | LD 10/1241
| 910076 | KHANDWA-RAJGARH I 400kV | 2013-10-20 | 00:46 | 2013-10-21 | 06:49 | - |  |  | - |  |  | - |  |  | 1899-12-31 06:03 | 30 | 3 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1330 | LD10/1390
| 910091 | KHANDWA-RAJGARH I 400kV | 2013-10-22 | 20:25 | 2013-10-23 | 09:46 | - |  |  | - |  |  | - |  |  | 0.55625 | 13 | 21 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1536 | LD 10/1570
| 910095 | KHANDWA-RAJGARH I 400kV | 2013-10-23 | 20:03 | 2013-10-29 | 10:55 | - |  |  | - |  |  | - |  |  | 1900-01-04 14:52 | 134 | 52 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/1625 | LD 10/2020
| 910116 | KHANDWA-RAJGARH I 400kV | 2013-10-29 | 17:41 | 2013-10-30 | 09:55 | - |  |  | - |  |  | - |  |  | 0.67639 | 16 | 14 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/2054 | LD 10/2113
| 910126 | KHANDWA RAJGARH I 400KV | 2013-10-31 | 20:08 | 2013-11-01 | 07:19 | - |  |  | - |  |  | - |  |  | 0.46597 | 11 | 11 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD10/2278 | LD11/06
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-24 04:16 | 600 | 256
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 604.2667 |  |  |  |  | 220.588 | 2 | 0 | 0 | 744 | 441.176 | 328234.944 | 0 | 100%
66 |  | VAPI-MAGARWADA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 744 | 25.71 | 19128.24 | 0 | 100%
67 |  | VAPI-MAGARWADA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 0 | 0 | 744 | 25.71 | 19128.24 | 0 | 100%
68 |  | VAPI-KHARADPARA I 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 744 | 29.66 | 22067.04 | 0 | 100%
69 |  | VAPI-KHARADPARA II 220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 744 | 29.66 | 22067.04 | 0 | 100%
70 |  | GWALIOR-BINA II 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 233.652 | 4 | 0 | 0 | 744 | 934.608 | 695348.352 | 0 | 100%
71 |  | SEONI-BINA 765kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 292.45 | 4 | 0 | 0 | 744 | 1169.8 | 870331.2 | 0 | 100%
72 | 909103 | DAMOH-BHOPAL I 400KV | 2013-09-21 | 13:30 | 2013-10-09 | 08:47 | - |  |  | - |  |  | - |  |  | 1900-01-07 08:47 | 200 | 47 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 09/1564 | LD 10/596
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-07 08:47 | 200 | 47
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 200.7833 |  |  |  |  | 241.471 | 2 | 0 | 0 | 744 | 482.942 | 359308.848 | 0 | 100%
73 | 910040 | DAMOH-BHOPAL II 400KV | 2013-10-09 | 08:57 | 2013-10-30 | 11:28 | - |  |  | - |  |  | - |  |  | 1900-01-20 02:31 | 506 | 31 | LVRD | Line kept out on V/R as per WRLDC Instruction. | LD10/598 | LD 10/2117
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-20 02:31 | 506 | 31
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 506.5167 |  |  |  |  | 213.8 | 2 | 0 | 0 | 744 | 427.6 | 318134.4 | 0 | 100%
74 |  | VAPI-KHADOLI I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.549 | 1 | 0 | 0 | 744 | 28.549 | 21240.456 | 0 | 100%
75 | 910068 | VAPI-SAYALI 220kV | 2013-10-16 | 18:04 | 2013-10-16 | 19:34 | - |  |  | 0.0625 | 1 | 30 | - |  |  | - |  |  | OMSU | Line A/T on Y ph to E/F,19.31kms from vapi,fault lies beyond PG section(ie in LILO portion of DNH),LL:19km |  | LD10/1130
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.0625 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 1.5 |  |  | 0 |  |  | 0 |  |  |  |  | 18.3 | 1 | 0 | 0 | 742.5 | 18.3 | 13587.75 | 0 | 100%
76 |  | SAYALI-KHADOLI 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 12.235 | 1 | 0 | 0 | 744 | 12.235 | 9102.84 | 0 | 100%
77 |  | DAMOH-BIRSINGHPUR I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 228.474 | 2 | 0 | 0 | 744 | 456.948 | 339969.312 | 0 | 100%
78 | 910001 | DAMOH-BIRSINGHPUR II 400kV | 2013-10-01 | 03:52 | 2013-10-30 | 10:23 | - |  |  | - |  |  | - |  |  | 1900-01-28 06:31 | 702 | 31 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/02 | LD 10/2116
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-28 06:31 | 702 | 31
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 702.5167 |  |  |  |  | 228.474 | 2 | 0 | 0 | 744 | 456.948 | 339969.312 | 0 | 100%
79 | 910106 | DEHGAM PIRANA I 400kV | 2013-10-28 | 11:03 | 2013-10-28 | 13:27 | 0.1 | 2 | 24 | - |  |  | - |  |  | - |  |  | OSFT | LINE H/T FOR REPLACEMENT OF INSULATOR STRING AT LOC 74 | LD10/1918 | LD10/1940
|  | SUBTOTAL |  |  |  |  | 0.1 | 2 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 2.4 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 2.4 | 224.016 | 744 | 93.34 | 69444.96 | 0.0032258 | 99.68%
80 |  | DEHGAM PIRANA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 0 | 0 | 744 | 93.34 | 69444.96 | 0 | 100%
81 |  | MUNDRA-BHACHAU I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 99.468 | 3 | 0 | 0 | 744 | 298.404 | 222012.576 | 0 | 100%
82 |  | MUNDRA-BHACHAU II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 99.468 | 3 | 0 | 0 | 744 | 298.404 | 222012.576 | 0 | 100%
83 |  | BHACHAU-RANCHODPURA I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0 | 0 | 744 | 848.568 | 631334.592 | 0 | 100%
84 |  | BHACHAU-RANCHODPURA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0 | 0 | 744 | 848.568 | 631334.592 | 0 | 100%
85 | 910066 | MUNDRA-LIMBDI I 400kV | 2013-10-15 | 11:05 | 2013-10-15 | 20:55 | - |  |  | - |  |  | - |  |  | 0.40972 | 9 | 50 | OSFD | Line H/T to avail emergency S/D to attend hot spot in Y ph line isolator at limdi end. | LD10/ | LD10/1080
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40972 | 9 | 50
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.8333 |  |  |  |  | 314.053 | 3 | 0 | 0 | 744 | 942.159 | 700966.296 | 0 | 100%
86 | 910067 | MUNDRA-LIMBDI II 400kV | 2013-10-16 | 11:00 | 2013-10-16 | 23:23 | - |  |  | - |  |  | - |  |  | 0.51597 | 12 | 23 | OSFD | Line H/T to avail emergency outage by GETCO for attending hot spot at limdi end(all 3 ph of Bus#1 &2) | LD10/1104 | LD10/1138
| 910073 | MUNDRA-LIMBDI II 400kV | 2013-10-17 | 12:03 | 2013-10-17 | 23:05 | - |  |  | - |  |  | - |  |  | 0.45972 | 11 | 2 | OSPD | Line H/T to attend hot spot by Getco at Limbdi end. | LD10/1159 | LD10/1192
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97569 | 23 | 25
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 23.4167 |  |  |  |  | 314.053 | 3 | 0 | 0 | 744 | 942.159 | 700966.296 | 0 | 100%
87 | 910060 | SATNA-BINA(PG ) I 765kV | 2013-10-13 | 18:14 | 30/10/13 | 11:06 | - |  |  | - |  |  | - |  |  | 1900-01-15 16:52 | 400 | 52 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 10/928 NLD 10/146 | LD 10/2118
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-15 16:52 | 400 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 400.8667 |  |  |  |  | 274.164 | 4 | 0 | 0 | 744 | 1096.656 | 815912.064 | 0 | 100%
88 | 909154 | SATNA-BINA(PG ) II 765kV | 2013-09-30 | 01:05 | 2013-10-13 | 18:12 | - |  |  | - |  |  | - |  |  | 1900-01-11 18:12 | 306 | 12 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 09/2262 NLD 09/241 | WR 10/927 NLD 10/145
| 910120 | SATNA-BINA(PG) II 765kV | 2013-10-30 | 17:29 | 2013-10-31 | 15:40 | - |  |  | 0.92431 | 22 | 11 | - |  |  | - |  |  | OMSU | Line H/T for voltage regulation on WRLDC instruction | LD10/2172 | WR 10/2250 NLD 10/359
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.92431 | 22 | 11 | 0 | 0 | 0 | 1900-01-11 18:12 | 306 | 12
|  | Element Availability= | [6 empty] | 0 |  |  | 22.1833 |  |  | 0 |  |  | 306.2 |  |  |  |  | 275.635 | 4 | 0 | 0 | 721.8167 | 1102.54 | 795831.7477 | 0 | 100%
89 | 909151 | BINA (PG) -INDORE I 765kV | 2013-09-29 | 17:12 | 2013-10-07 | 18:29 | - |  |  | - |  |  | - |  |  | 1900-01-05 18:29 | 162 | 29 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WRLD09/2203 | WR 10/489 NLD 10/88
| 910035 | BINA (PG) -INDORE I 765kV | 2013-10-08 | 04:01 | 2013-10-08 | 04:11 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | A/T on operation of O/V protection at Indore S/S.
| 910036 | BINA (PG) -INDORE I 765kV | 2013-10-08 | 04:11 | 2013-10-23 | 11:00 | - |  |  | - |  |  | - |  |  | 1900-01-14 06:49 | 366 | 49 | LVRD | Line kept out on V/R as per WRLDC Instruction. |  | WR 10/1577 NLD 10/260
| 910094 | BINA (PG) -INDORE I 765kV | 2013-10-23 | 12:02 | 2013-10-24 | 09:41 | - |  |  | - |  |  | - |  |  | 0.90208 | 21 | 39 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD 10/1585 NLD 10/261 | LD 10/1648 NLD 10/270
| 910096 | BINA (PG) -INDORE I 765kV | 2013-10-24 | 19:30 | 2013-10-26 | 15:59 | - |  |  | - |  |  | - |  |  | 1899-12-31 20:29 | 4 | 29 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR10/1695 NLD 10/278 | WR 10/1806 NLD 10/300
| 910101 | BINA (PG) -INDORE I 765kV | 2013-10-27 | 03:04 | 2013-10-27 | 03:14 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V at Indore end & DT recd at Bina End.
| 910102 | BINA (PG) -INDORE I 765kV | 2013-10-27 | 03:14 | 2013-10-27 | 10:56 | - |  |  | - |  |  | - |  |  | 0.32083 | 7 | 42 | LVRD | After tripping on Over voltage line kept out for voltage regulation on WRLDC Instruction |  | WR 10/1927 NLD 10/319
| 910124 | BINA (PG) -INDORE I 765kV | 2013-10-31 | 19:02 | 2013-10-31 | 19:14 | - |  |  | - |  |  | 0.0083333 | 0 | 12 | - |  |  | GOVC | Line A/T on operation of O/V protection at Indore
| 910125 | BINA (PG) -INDORE I 765kV | 2013-10-31 | 19:14 |  |  | - |  |  | - |  |  | - |  |  | 0.19861 | 4 | 46 | LVRD | After tripping on O/V Line Kept out on voltage regulation as per instruction of WRLDC.
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.022222 | 0 | 32 | 1900-01-24 07:54 | 564 | 234
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.53333 |  |  | 567.9 |  |  |  |  | 311 | 4 | 0 | 0 | 743.4667 | 1244 | 924872.5333 | 0 | 100%
90 |  | GANDHAR-NAVSARI (PG) II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 102.152 | 2 | 0 | 0 | 744 | 204.304 | 152002.176 | 0 | 100%
91 |  | GANDHAR-NAVSARI (PG) I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 102.152 | 2 | 0 | 0 | 744 | 204.304 | 152002.176 | 0 | 100%
92 |  | MUNDRA-JETPUR II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337 | 3 | 0 | 0 | 744 | 1011 | 752184 | 0 | 100%
93 |  | MUNDRA-JETPUR II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337 | 3 | 0 | 0 | 744 | 1011 | 752184 | 0 | 100%
94 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 744 | 114.2 | 84964.8 | 0 | 100%
95 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 744 | 114.2 | 84964.8 | 0 | 100%
96 | 910084 | V'CHAL-SASAN I 400 KV | 2013-10-21 | 09:25 | 2013-10-21 | 18:20 | - |  |  | - |  |  | - |  |  | 0.37153 | 8 | 55 | OSPD | Line H/T to avail OCC Approved S/D by SASAN | LD10/1401 | LD10/1432
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37153 | 8 | 55
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.9167 |  |  |  |  | 5.443 | 2 | 0 | 0 | 744 | 10.886 | 8099.184 | 0 | 100%
97 |  | VINDHYACHAL (NTPC) -SASAN (RELIANCE) II 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 744 | 10.886 | 8099.184 | 0 | 100%
98 | 910017 | SASAN-SATNA I 765kV | 2013-10-04 | 16:54 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-26 07:06 | 655 | 6 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 10/264 NLD 10/50
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-26 07:06 | 655 | 6
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 655.1 |  |  |  |  | 245.7 | 4 | 0 | 0 | 744 | 982.8 | 731203.2 | 0 | 100%
99 |  | BINA(PG)-BINA(MPEB) III 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.8 | 2 | 0 | 0 | 744 | 1.6 | 1190.4 | 0 | 100%
100 |  | VAPI - NAVASARI (GIS) I 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 744 | 233.7 | 173872.8 | 0 | 100%
101 | 910002 | VAPI - NAVASARI (GIS) II 400kV | 2013-10-01 | 10:39 | 2013-10-01 | 15:00 | 0.18125 | 4 | 21 | - |  |  | - |  |  | - |  |  | OSFT | Line H/T to avail emergency S/D for rectification of burnt jumper at loc no.77 | LD10/15 | LD10/39
|  | SUBTOTAL |  |  |  |  | 0.18125 | 4 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 4.35 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 4.35 | 1016.595 | 744 | 233.7 | 173872.8 | 0.0058468 | 99.42%
102 | 909027 | SASAN-SATNA II 765kV | 2013-09-06 | 22:27 | 2013-10-04 | 15:39 | - |  |  | - |  |  | - |  |  | 1900-01-02 15:39 | 87 | 39 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 09/452 NLD 09/39 | WR 10/247 NLD 10/46
| 910064 | SASAN-SATNA II 765kV | 2013-10-14 | 22:11 | 2013-10-17 | 10:41 | - |  |  | - |  |  | - |  |  | 1900-01-01 12:30 | 60 | 30 | LVRD | Line H/T for voltage regulation on WRLDC instruction | WR 10/1026 NLD 10/165 | WR 10/1152 NLD 10/181
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-05 04:09 | 147 | 69
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 148.15 |  |  |  |  | 245.7 | 4 | 0 | 0 | 744 | 982.8 | 731203.2 | 0 | 100%
103 |  | BINA(PG)-BINA(MPEB) IV 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.8 | 2 | 0 | 0 | 744 | 1.6 | 1190.4 | 0 | 100%
104 | 909120 | INDORE (PG) - INDORE ( MPPTCL) I 400kV | 2013-09-25 | 00:05 | 2013-10-23 | 10:21 | - |  |  | - |  |  | - |  |  | 1900-01-21 10:21 | 538 | 21 | LVRD | Line H/T for voltage regulation on WRLDC instruction | LD09/1876 | LD 10/1571
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-21 10:21 | 538 | 21
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 538.35 |  |  |  |  | 49.7 | 4 | 0 | 0 | 744 | 198.8 | 147907.2 | 0 | 100%
105 |  | Indore (PG) - Indore ( MPPTCL) - II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 49.7 | 4 | 0 | 0 | 744 | 198.8 | 147907.2 | 0 | 100%
[20 empty] | TRANSMISSION LINE AVAILABILITY | [5 empty] | 7602.016 |  |  | 29623773.8943
0.00025662
99.97%
106 | 910080 | AGRA-GWALIOR I 765KV | 2013-10-20 | 19:50 | 2013-10-20 | 20:16 | - |  |  | - |  |  | 0.018056 | 0 | 26 | - |  |  | GOVC | Line A/T on O/V . DT received from Agra |  | WR 10/1366 NLD 10/221, NR 10/1674
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.018056 | 0 | 26 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.43333 |  |  | 0 |  |  |  |  | 129.435 | 4 | 0 | 0 | 743.5667 | 517.74 | 384974.206 | 0 | 100%
107 |  | AGRA-GWALIOR II 765KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 127.934 | 4 | 0 | 0 | 744 | 511.736 | 380731.584 | 0 | 100%
ICTs
108 | 910072 | ICT1 JABALPUR 400/220kV | 2013-10-17 | 10:52 | 2013-10-17 | 15:21 | 0.18681 | 4 | 29 | - |  |  | - |  |  | - |  |  | OSPT | To avail OCC approved S/D for AMP | LD10/1161 | LD10/1172
|  | SUBTOTAL |  |  |  |  | 0.18681 | 4 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 4.4833 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 4.4833 | 3530.625 | 744 | 787.5 | 585900 | 0.006026 | 99.4%
109 | 910075 | ICT II JABALPUR 400/220kV | 2013-10-18 | 10:07 | 2013-10-18 | 13:20 | 0.13403 | 3 | 13 | - |  |  | - |  |  | - |  |  | OSPT | To avail OCC approved S/D for AMP | LD10/1218 | LD10/1235
|  | SUBTOTAL |  |  |  |  | 0.13403 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.2167 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 3.2167 | 2533.125 | 744 | 787.5 | 585900 | 0.0043235 | 99.57%
110 |  | ICT1 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
111 |  | ICT2 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
112 |  | ICT1 SATNA 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
113 |  | ICT2 SATNA 400/220KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
114 |  | ICT1 KHANDWA 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
115 |  | ICT2 KHANDWA 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
116 |  | ICT1 VAPI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
117 |  | ICT2 VAPI 400/220/33kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
118 |  | ICT1 GWALIOR 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
119 |  | ICT1 RAJGARH 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
120 |  | ICT2 GWALIOR 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
121 | 910099 | ICT I ITARSI 400/220kV | 2013-10-25 | 12:32 | 2013-10-25 | 15:28 | 0.12222 | 2 | 56 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail OCC approved S/D for AMP | LD10/1739 | LD10/1749
|  | SUBTOTAL |  |  |  |  | 0.12222 | 2 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 2.9333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 2.9333 | 2310 | 744 | 787.5 | 585900 | 0.0039427 | 99.61%
122 |  | ICT1 DAMOH 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
123 |  | ICT2 DAMOH 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
124 | 910041 | ICT2 RAJGARH 400/220KV | 2013-10-09 | 11:12 | 2013-10-09 | 14:10 | 0.12361 | 2 | 58 | - |  |  | - |  |  | - |  |  | OSFT | ICT H/T to avail emergency S/D for replacement of faulty B ph bushing due to high gas content | LD10/610 | LD10/623
|  | SUBTOTAL |  |  |  |  | 0.12361 | 2 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 2.9667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 2.9667 | 2336.25 | 744 | 787.5 | 585900 | 0.0039875 | 99.6%
125 |  | ICT1 BINA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
126 |  | ICT1 PIRANA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
127 |  | ICT2 PIRANA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
128 | 910052 | ICT3 GWALIOR 400/220/33kV | 2013-10-12 | 09:35 | 2013-10-13 | 17:50 | - |  |  | - |  |  | - |  |  | 1899-12-31 08:15 | 32 | 15 | SCSD | H/T to avail OCC S/D by Powergrid for construction work to facilitate replacement of twin moose condutor with quad conductor of Jack Bus. | LD 10/822 | LD 10/950
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 32.25 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
129 |  | ICT1 SHUJALPUR 400/220/33kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
130 |  | ICT1 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
131 |  | ICT2 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
132 |  | ICT2 SHUJALPUR 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
133 | 910048 | ICT1 SATNA 765/400KV | 2013-10-11 | 15:07 | 2013-10-12 | 16:12 | - |  |  | - |  |  | - |  |  | 1899-12-31 01:05 | 25 | 5 | SCSD | ICT H/T to avail S/D for charging of Spare ICT | LD 10/767 LD 10/120 | WR 10/846 NLD 10/132
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 01:05 | 25 | 5
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 25.0833 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
134 |  | ICT2 NAVSARI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
135 |  | ICT1 NAVSARI 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
136 |  | ICT2 SATNA 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
137 |  | ICT1 BINA 765/400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
138 |  | ICT3 VAPI 400/220/33kV | [17 empty] | H/T to avail S/D by Powergrid for taking oil sample of 220kV side CTs. | LD 08/1041
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 744 | 787.5 | 585900 | 0 | 100%
139 |  | ICT2 BINA 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 744 | 2500 | 1860000 | 0 | 100%
140 | 910032 | ICT1 GWALIOR 765/400KV | 2013-10-07 | 11:16 | 2013-10-09 | 14:00 | - |  |  | - |  |  | - |  |  | 1900-01-01 02:44 | 50 | 44 | SCSD | H/T to avail OCC S/D by Powergrid for construction work to facilitate replacement of twin moose condutor with quad conductor of Jack Bus. | WR 10/476 NLD 10/86 | WR 10/619 NLD 10/98
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 02:44 | 50 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 50.7333 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
141 | 910044 | ICT2 GWALIOR 765/400KV | 2013-10-10 | 07:50 | 2013-10-11 | 19:45 | - |  |  | - |  |  | - |  |  | 1899-12-31 11:55 | 35 | 55 | SCSD | H/T to avail OCC S/D by Powergrid for construction work to facilitate replacement of twin moose condutor with quad conductor of Jack Bus. | LD 10/655 LD 10/105 | LD 10/782 LD 10/125
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 11:55 | 35 | 55
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 35.9167 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
142 |  | ICT2 INDORE 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
143 |  | ICT1 INDORE 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 744 | 3750 | 2790000 | 0 | 100%
[20 empty] | ICT AVAILABILITY | [5 empty] | 10710 |  |  | 35005200
0.00030595
99.97%
Bus Reactors
144 |  | BUS REACTOR DEHGAM I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
145 |  | BUS REACTOR JABALPUR I 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 744 | 100 | 74400 | 0 | 100%
146 |  | BUS REACTOR JABALPUR II 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 744 | 100 | 74400 | 0 | 100%
147 |  | BUS REACTOR ITARSI I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
148 |  | BUS REACTOR ITARSI II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
149 |  | BUS REACTOR ITARSI III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
150 |  | BUS REACTOR JABALPUR III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
151 | 910108 | BUS REACTOR DHULE 400 KV | 2013-10-28 | 14:44 | 2013-10-28 | 17:11 | - |  |  | - |  |  | - |  |  | 0.10208 | 2 | 27 | SVRD | REACTOR H/T FOR VOLTAGE REGULATION ON WRLDC INSTRUCTION | LD10/1944 | LD10/1954
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10208 | 2 | 27
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 2.45 |  |  |  |  | 80 | 4 | 0 | 0 | 744 | 320 | 238080 | 0 | 100%
152 |  | BUS REACTOR SATNA 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
153 |  | Bus Reactor # 1 / Bina |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
154 |  | Bus Reactor / Damoh |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
155 | 910062 | BUS REACTOR GWALIOR 400kV | 2013-10-14 | 10:11 | 2013-10-15 | 21:18 | - |  |  | - |  |  | - |  |  | 1899-12-31 11:07 | 35 | 7 | SCSD | H/T to avail OCC S/D by Powergrid for construction work for upgradation of existing equipments with higher rating. | LD 10/993 | LD 10/1081
| 910104 | BUS REACTOR, GWALIOR 400kV | 2013-10-28 | 09:58 | 2013-10-28 | 19:52 | - |  |  | - |  |  | - |  |  | 0.4125 | 9 | 54 | SVRD | B/R H/T FOR V/R ON WRLDC INSTR | LD10/1924 | LD10/1971
| 910119 | BUS REACTOR GWALIOR 400kV | 2013-10-30 | 08:43 | 2013-10-30 | 13:06 | - |  |  | - |  |  | - |  |  | 0.18264 | 4 | 23 | SVRD | B/R taken out on voltage regulation | LD10/2102 | LD10/2150
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 01:24 | 48 | 84
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 35.1167 |  |  |  |  | 50 | 4 | 0 | 0 | 744 | 200 | 148800 | 0 | 100%
156 |  | BUS REACTOR KHANDWA 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
157 |  | BUS REACTOR DEHGAM II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
158 |  | BUS REACTOR BHACHAU 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
159 |  | Bus Reactor / Shujalpur |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
160 |  | BUS REACTOR RAJGARH 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
161 |  | BUS REACTOR SATNA 765kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
162 |  | Bus Reactor / Navsari |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
163 |  | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
164 |  | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
165 |  | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
166 |  | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
167 |  | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
168 |  | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
169 |  | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
170 |  | Bus Reactor-II/Gwalior |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
171 |  | Bus Reactor-III/Gwalior |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
172 |  | Bus Reactor-I/Indore |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 744 | 500 | 372000 | 0 | 100%
173 |  | Switchable Indore - Line Reactor / Bina 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 744 | 960 | 714240 | 0 | 100%
174 |  | Switchable Shujalpur-II Line Reactor / Bina 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 744 | 252 | 187488 | 0 | 100%
[20 empty] | BUS REACTOR AVAILABILITY | [5 empty] | 0 |  |  | 9710688
0
100%
[20 empty] | SYSTEM AVAILABILITY | [5 empty] | 18312.016 |  |  | 74339661.8943
0.00024633
99.98%
Formulas:
OUTAGE HOURS ATTRIBUTED TO = SUM([OUTAGE HOURS ATTRIBUTED TO, row above]:[OUTAGE HOURS ATTRIBUTED TO, row above])
OUTAGE HOURS ATTRIBUTED TO = IF((RIGHT([Outage Category],1)="T"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE DEEMED AVAILABLE = IF((RIGHT([Outage Category],1)="D"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE DEEMED AVAILABLE = SUM(Q70:[OUTAGE DEEMED AVAILABLE, row above])
OTHERS = IF((RIGHT([Outage Category],1)="U"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
SYSTEM CONSTR. = IF((RIGHT([Outage Category],1)="C"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")

## availability sheet
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR OCTOBER-2013
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552 | 0 | 100 | 100%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016 | 0 | 100 | 100%
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432 | 0 | 100 | 100%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032 | 0 | 100 | 100%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 744 | 273 | 2 | 0 | 546 | 406224 | 0 | 100 | 100%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680 | 0 | 100 | 100%
7 | 400 KV V'chal - Jabalpur # 2 | 3 | 13 |  |  | 3.2167 | 0 | 744 | 360 | 2 | 2316 | 720 | 535680 | 0.0043235 | 99.5677 | 99.57%
8 | 400 KV Jabalpur - Itarsi # 1 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 744 | 232 | 2 | 0 | 464 | 345216 | 0 | 100 | 100%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616 | 0 | 100 | 100%
12 | 400 KV Jabalpur-Sasan |  |  |  |  | 0 | 0 | 744 | 376 | 2 | 0 | 752 | 559488 | 0 | 100 | 100%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 744 | 21 | 2 | 0 | 42 | 31248 | 0 | 100 | 100%
14 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832 | 0 | 100 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 744 | 234 | 2 | 0 | 468 | 348192 | 0 | 100 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 | 3 | 8 |  |  | 3.1333 | 0 | 744 | 234 | 2 | 1466.4 | 468 | 348192 | 0.0042115 | 99.5789 | 99.58%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32 | 0 | 100 | 100%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100%
20 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64 | 0 | 100 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 57 | 2 | 0 | 114 | 84816 | 0 | 100 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  |  |  | 0 | 0 | 744 | 110 | 2 | 0 | 220 | 163680 | 0 | 100 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 744 | 13 | 2 | 0 | 26 | 19344 | 0 | 100 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 744 | 13 | 1 | 0 | 13 | 9672 | 0 | 100 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 0 | 100 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  |  |  | 0 | 0 | 744 | 58.149 | 1 | 0 | 58.149 | 43262.856 | 0 | 100 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 744 | 31.334 | 1 | 0 | 31.334 | 23312.496 | 0 | 100 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 55 | 30 |  |  | 55.5 | 0 | 744 | 31.334 | 1 | 1739.037 | 31.334 | 23312.496 | 0.074597 | 92.5403 | 92.54%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528 | 0 | 100 | 100%
32 | 220kV Kawas - Haldarwa # 1 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 0 | 100 | 100%
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 744 | 81 | 1 | 0 | 81 | 60264 | 0 | 100 | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 | 8 | 36 | 14 | 0 | 8.6 | 14 | 730 | 74 | 1 | 636.4 | 74 | 54020 | 0.011781 | 98.8219 | 98.82%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 1 | 32 | 0 | 1.5333 | 742.4667 | 74 | 1 | 0 | 74 | 54942.5333 | 0 | 100 | 100%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992 | 0 | 100 | 100%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 744 | 117 | 1 | 0 | 117 | 87048 | 0 | 100 | 100%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 267 | 2 | 0 | 534 | 397296 | 0 | 100 | 100%
42 | 400kV V'chal - Satna # 3 | 0 | 14 | 0 | 18 | 0.23333 | 0.3 | 743.7 | 258.31 | 2 | 120.5447 | 516.62 | 384210.294 | 0.00031375 | 99.9686 | 99.97%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 744 | 100.32 | 2 | 0 | 200.64 | 149276.16 | 0 | 100 | 100%
44 | 400kV Nigrie-Satna | 0 | 7 |  |  | 0.11667 | 0 | 744 | 161.11 | 2 | 37.5923 | 322.22 | 239731.68 | 0.00015681 | 99.9843 | 99.98%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688 | 0 | 100 | 100%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 744 | 0.742 | 2 | 0 | 1.484 | 1104.096 | 0 | 100 | 100%
49 | 765 kV Gwalior-Bina # 1 |  |  |  |  | 0 | 0 | 744 | 234.931 | 4 | 0 | 939.724 | 699154.656 | 0 | 100 | 100% | Upgraded to 765kV level w.e.f 01.04.2013
50 | 400KV Satna-Bina # 4 |  |  | 0 | 6 | 0 | 0.1 | 743.9 | 272.586 | 2 | 0 | 545.172 | 405553.4508 | 0 | 100 | 100%
51 | 400KV Satna-Bina # 3 | 0 | 5 | 0 | 4 | 0.083333 | 0.066667 | 743.9333 | 272.586 | 2 | 45.431 | 545.172 | 405571.6232 | 0.00011202 | 99.9888 | 99.99%
52 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 744 | 199.936 | 2 | 0 | 399.872 | 297504.768 | 0 | 100 | 100%
54 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100%
55 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 744 | 152.229 | 2 | 0 | 304.458 | 226516.752 | 0 | 100 | 100%
56 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696 | 0 | 100 | 100%
57 | 400KV Nagda - Dehgam # 1 |  |  | 0 | 18 | 0 | 0.3 | 743.7 | 331.442 | 2 | 0 | 662.884 | 492986.8308 | 0 | 100 | 100%
58 | 400KV Seoni - Khandwa # 1 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 351.729 | 4 | 0 | 1406.916 | 1046511.018 | 0 | 100 | 100%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504 | 0 | 100 | 100%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  | 457 | 123 | 0 | 459.05 | 284.95 | 4.01 | 2 | 0 | 8.02 | 2285.299 | 0 | 100 | 100%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  | 171 | 63 | 0 | 172.05 | 571.95 | 4.01 | 2 | 0 | 8.02 | 4587.039 | 0 | 100 | 100%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56 | 0 | 100 | 100%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944 | 0 | 100 | 100%
66 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100%
67 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24 | 0 | 100 | 100%
68 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 0 | 100 | 100%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04 | 0 | 100 | 100%
70 | 765 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352 | 0 | 100 | 100% | Upgraded to 765kV level w.e.f 01.04.2013
71 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2 | 0 | 100 | 100%
72 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848 | 0 | 100 | 100%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4 | 0 | 100 | 100%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456 | 0 | 100 | 100%
75 | 220 KV Vapi - Sayali |  |  | 1 | 30 | 0 | 1.5 | 742.5 | 18.3 | 1 | 0 | 18.3 | 13587.75 | 0 | 100 | 100%
76 | 220kV Sayali-Khadoli |  |  |  |  | 0 | 0 | 744 | 12.235 | 1 | 0 | 12.235 | 9102.84 | 0 | 100 | 100%
77 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100%
78 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312 | 0 | 100 | 100%
79 | 400kV Dehgam-Pirana#1 | 2 | 24 |  |  | 2.4 | 0 | 744 | 46.67 | 2 | 224.016 | 93.34 | 69444.96 | 0.0032258 | 99.6774 | 99.68%
80 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96 | 0 | 100 | 100%
81 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100%
82 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 744 | 99.468 | 3 | 0 | 298.404 | 222012.576 | 0 | 100 | 100%
83 | 400kV Bhachau - Ranchodpura # 1 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100%
84 | 400kV Bhachau - Ranchodpura # 2 |  |  |  |  | 0 | 0 | 744 | 282.856 | 3 | 0 | 848.568 | 631334.592 | 0 | 100 | 100%
85 | 400kV Mundra - Limbdi # 1 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 0 | 100 | 100%
86 | 400kV Mundra - Limbdi # 2 |  |  |  |  | 0 | 0 | 744 | 314.053 | 3 | 0 | 942.159 | 700966.296 | 0 | 100 | 100%
87 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 744 | 274.164 | 4 | 0 | 1096.656 | 815912.064 | 0 | 100 | 100%
88 | 765kV Satna - Bina # 2 |  |  | 22 | 11 | 0 | 22.1833 | 721.8167 | 275.635 | 4 | 0 | 1102.54 | 795831.7477 | 0 | 100 | 100%
89 | 765kV Bina - Indore |  |  |  | 32 | 0 | 0.53333 | 743.4667 | 311 | 4 | 0 | 1244 | 924872.5333 | 0 | 100 | 100% | upgraded to 765kV level w.e.f. 01.07.2013
90 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100%
91 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 744 | 102.152 | 2 | 0 | 204.304 | 152002.176 | 0 | 100 | 100%
92 | 400kV Mundra-Jetpur#1 |  |  |  |  | 0 | 0 | 744 | 337 | 3 | 0 | 1011 | 752184 | 0 | 100 | 100%
93 | 400kV Mundra-Jetpur#2 |  |  |  |  | 0 | 0 | 744 | 337 | 3 | 0 | 1011 | 752184 | 0 | 100 | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 744 | 28.55 | 4 | 0 | 114.2 | 84964.8 | 0 | 100 | 100%
96 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100%
97 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 744 | 5.443 | 2 | 0 | 10.886 | 8099.184 | 0 | 100 | 100%
98 | 765kV Sasan - Satna # 1 |  |  |  |  | 0 | 0 | 744 | 245.7 | 4 | 0 | 982.8 | 731203.2 | 0 | 100 | 100%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100% | Commercial operation w.e.f. 01.03.2013
100 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 744 | 116.85 | 2 | 0 | 233.7 | 173872.8 | 0 | 100 | 100% | Commercial operation w.e.f. 01.04.2013
101 | 400kV Vapi-Navsari#2 | 4 | 21 |  |  | 4.35 | 0 | 744 | 116.85 | 2 | 1016.595 | 233.7 | 173872.8 | 0.0058468 | 99.4153 | 99.42%
102 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 744 | 242.23 | 4 | 0 | 968.92 | 720876.48 | 0 | 100 | 100% | Commercial operation w.e.f. 01.05.2013
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 744 | 0.8 | 2 | 0 | 1.6 | 1190.4 | 0 | 100 | 100% | Commercial operation w.e.f. 01.06.2013
104 | 400kV Indore (MP)-Indore (PG)#1 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100% | Commercial operation w.e.f. 01.07.2013
105 | 400kV Indore (MP)-Indore (PG)#2 |  |  |  |  | 0 | 0 | 744 | 49.7 | 4 | 0 | 198.8 | 147907.2 | 0 | 100 | 100%
| Total Sr.No. 1 to 105 | 75 | 158 | 666 | 347 |  |  |  | 16432.199 |  | 7602.016 |  | 29573061.6711
* | Lines charged with 400kV level
|  | 77.6333 |  | 671.7833
[10 empty] | NAFM | 0.00025706
Availability of ( Sl no 1 to 105) transmission lines during OCTOBER-2013 = | [9 empty] | TAFM | 99.9743
106 | 765 kV Gwalior -Agra # 1 | 0 | 0 | 0 | 26 | 0 | 0.43333 | 743.5667 | 129.435 | 4 | 0 | 517.74 | 384974.206 | 0 | 100 | 100%
107 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 127.934 | 4 | 0 | 511.736 | 380731.584 | 0 | 100 | 100%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. | 4 | 29 |  |  | 4.4833 | 0 | 744 | 315 | 2.5 | 3530.625 | 787.5 | 585900 | 0.006026 | 99.3974 | 99.4%
2 | 400/220kV ICT # 2 /Jabalpur. | 3 | 13 |  |  | 3.2167 | 0 | 744 | 315 | 2.5 | 2533.125 | 787.5 | 585900 | 0.0043235 | 99.5677 | 99.57%
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% |  | 0.83333
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
10 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
14 | 400/220kV ICT # 1 / Itarsi | 2 | 56 |  |  | 2.9333 | 0 | 744 | 315 | 2.5 | 2310 | 787.5 | 585900 | 0.0039427 | 99.6057 | 99.61%
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
17 | 400/220 KV ICT # 2 / Rajgarh | 2 | 58 |  |  | 2.9667 | 0 | 744 | 315 | 2.5 | 2336.25 | 787.5 | 585900 | 0.0039875 | 99.6013 | 99.6%
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
20 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
21 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
22 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
23 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
24 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
25 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
26 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
27 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
28 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100%
29 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
30 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.03.2013
31 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0 | 100 | 100% | Commercial operation w.e.f. 01.04.2013
32 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 744 | 1000 | 2.5 | 0 | 2500 | 1860000 | 0 | 100 | 100%
33 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100%
34 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100%
35 | 765/400KV ICT# 2 / INDORE |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.07.2013
36 | 765/400KV ICT# 1 / INDORE |  |  |  |  | 0 | 0 | 744 | 1500 | 2.5 | 0 | 3750 | 2790000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.10.2013
| Total Sr.No. 1 to 36 | 11 | 156 | 0 | 0 |  |  |  | 18820 |  | 10710 |  | 35005200
|  | 13.6 |  | 0 | [5 empty] | NAFM | 0.00030595
Availability of 35 ( Sl no 1 to 35) ICTs in OCTOBER-2013 = | [9 empty] | TAFM | 99.9694
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100%
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400 | 0 | 100 | 100%
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080 | 0 | 100 | 100%
9 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
12 | Bus Reactor-I / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800 | 0 | 100 | 100%
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
15 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
16 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
17 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
18 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
19 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
20 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
21 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100% | Commercial operation w.e.f. 01.04.2013
22 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
23 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
24 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
25 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100% | Commercial operation w.e.f. 01.06.2013
26 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
27 | Bus Reactor-II/Gwalior |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.10.2013
28 | Bus Reactor-III/Gwalior |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
29 | Bus Reactor-I/Indore |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000 | 0 | 100 | 100%
30 | Switchable Indore - Line Reactor / Bina 765KV |  |  |  |  | 0 | 0 | 744 | 240 | 4 | 0 | 960 | 714240 | 0 | 100 | 100%
31 | Switchable Shujalpur-II Line Reactor / Bina 400kV |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488 | 0 | 100 | 100%
| Total of sl no 1 to 31 | 0 | 0 | 0 | 0 |  |  |  | 3263 |  | 0 |  | 9710688
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 31 ( Sl no 1 to 31) Bus Reactors in OCTOBER-2013 = | [7 empty] | TAFM | 100
[11 empty] | 18312.016 |  | 74288949.6711
[8 empty] | NAFM = | 0.0002465
% System Availability for OCTOBER-2013 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9754
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B136: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B137: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## ANX-II
MONTH : OCTOBER-2013
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : OCTOBER-2013
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
OCTOBER 2013
Sl. No. | Name of Elements | Type of failures | Restoration Time (Days) |  |  | Remarks
A |  | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 |  | Insualtor Failure | Terrain Type
|  |  | Plain | River bed | Hilly
i | KAKRAPAR-HALDARWA I 220kV | Insualtor Failure in single phase | Less than 1 day
ii |  | Insualtor Failure in two phases | NIL
ii |  | Insualtor Failure in three phases
2 |  | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 |  | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 |  | Tower Damage ( not collapse)
i |  | One arm damage
ii |  | Two arm damage
5 |  | Snapping of phase conductor
i |  | Conductor snapping in single phase
ii |  | Conductor snapping in two phases
iii |  | Conductor snapping in three phases
6 |  | Failure of Earth wire
7 |  | Insulator failure with conductor snapping
8 |  | Any other combination of failures
B |  | Elements of sub-station for each KV class seperately
1 |  | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
|  | Other major failures in ICTs | Single phase Unit |  | Three phase Unit
|  | (i) Replacement of faulty bushings | NIL
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 |  | Failures of Reactors
Restoration of failed Reactors

## Supporting Annex V
Supporting Annex V
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF OCTOBER -2013
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | Outage Category | Details | WRLDC CODE FOR |  | Outage in Days |  |  | REMARKS
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING | Flashover | Snapping | Collapes of Tower
1 | 910010 | KAKRAPAR-HALDARWA I 220kV | 2013-10-03 | 15:30 | 2013-10-04 | 14:06 | 0.35833 | 0.58333 | - | - | LHWT | Line A/T on R-ph to E/F, F/L - 65.6kms from Haldarwa end due to Flashover of Insulator string at loc no. 33. Outage from 19:00hrs/03.10.13 to 09:00hrs/04.10.13 shall not be attributable to POWERGRID account as Restoration work could not be started due to adverse weather condition and Night hours |  | LD 10/248 | 0.35833