## Tripping AC SYSTEM (hidden)
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR MARCH- 2011
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =31*24-OH2
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 744 | 79 | 2 | 0 | 158 | 117552
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 744 | 207 | 2 | 0 | 414 | 308016
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 744 | 214 | 2 | 0 | 428 | 318432
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 744 | 289 | 2 | 0 | 578 | 430032
5 | 400kV Indore-Asoj # 2 | 8 | 38 |  |  | 8.6333 | 0 | 744 | 273 | 2 | 4713.8 | 546 | 406224
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 744 | 360 | 2 | 0 | 720 | 535680
8 | 400 KV Jabalpur - Itarsi # 1 | 4 | 54 |  |  | 4.9 | 0 | 744 | 232 | 2 | 2273.6 | 464 | 345216
9 | 400 KV Jabalpur - Itarsi # 2 | 6 | 25 |  |  | 6.4167 | 0 | 744 | 232 | 2 | 2977.3333 | 464 | 345216
10 | 400kV Jhanor-Dehgam#1 | 0 | 0 |  |  | 0 | 0 | 744 | 157 | 2 | 0 | 314 | 233616
11 | 400kV Jhanor-Dehgam#2 | 12 | 59 |  |  | 12.9833 | 0 | 744 | 157 | 2 | 4076.7667 | 314 | 233616
12 | 400 KV V'chal - Jabalpur # 3 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
13 | 400 KV V'chal - Jabalpur # 4 |  |  |  |  | 0 | 0 | 744 | 389 | 2 | 0 | 778 | 578832
14 | 400 KV Jabalpur - Itarsi # 3 | 4 | 45 |  |  | 4.75 | 0 | 744 | 234 | 2 | 2223 | 468 | 348192
15 | 400 KV Jabalpur - Itarsi # 4 | 5 | 52 |  |  | 5.8667 | 0 | 744 | 234 | 2 | 2745.6 | 468 | 348192
16 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
17 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 196.64 | 2 | 0 | 393.28 | 292600.32
18 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
19 | 400 KV Khandwa - Dhule # 2 |  |  |  |  | 0 | 0 | 744 | 261.78 | 2 | 0 | 523.56 | 389528.64
20 | 400 KV Jhanor - Sugen(PGCIL portion) | 13 | 31 | 0 | 51 | 13.5167 | 0.85 | 743.15 | 57 | 2 | 1540.9 | 114 | 84719.1
21 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 9 | 3 | 0 | 9.05 | 734.95 | 110 | 2 | 0 | 220 | 161689
22 | 400 KV Jhanor - Jhanor(GPEC) |  |  | 1 | 88 | 0 | 2.4667 | 741.5333 | 13 | 2 | 0 | 26 | 19279.8667
23 | 220kV Jhanor-Haldarwa ckI # 1 | 0 | 15 | 3 | 42 | 0.25 | 3.7 | 740.3 | 13 | 1 | 3.25 | 13 | 9623.9
24 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  | 71 | 0 | 1.1833 | 742.8167 | 13 | 1 | 0 | 13 | 9656.6167
25 | 220kV Kawas-Navsari ckt # 1 | 0 | 22 |  |  | 0.36667 | 0 | 744 | 49 | 1 | 17.9667 | 49 | 36456
26 | 220kV Kawas-Navsari ckt # 2 | 0 | 13 | 0 | 52 | 0.21667 | 0.86667 | 743.1333 | 49 | 1 | 10.6167 | 49 | 36413.5333
27 | 220kV Kawas-Ichchapur |  |  |  |  | 0 | 0 | 744 | 3 | 1 | 0 | 3 | 2232
28 | 220kV Kawas-Vav |  |  |  |  | 0 | 0 | 744 | 37 | 1 | 0 | 37 | 27528
29 | 220kV Kawas - Haldarwa # 1 | 0 | 80 | 8 | 25 | 1.3333 | 8.4167 | 735.5833 | 81 | 1 | 108 | 81 | 59582.25
30 | 220kV Kawas-Haldarwa # 2 |  |  | 0 | 33 | 0 | 0.55 | 743.45 | 81 | 1 | 0 | 81 | 60219.45
31 | 220 kV Kakrapar - Haldarwa # 1 | 5 | 20 |  | 74 | 5.3333 | 1.2333 | 742.7667 | 74 | 1 | 394.6667 | 74 | 54964.7333
32 | 220 KV Kakrapar - Haldarwa # 2 |  |  | 0 | 35 | 0 | 0.58333 | 743.4167 | 74 | 1 | 0 | 74 | 55012.8333
33 | 220 KV Kakrapar - Vav # 1 |  |  | 1 | 18 | 0 | 1.3 | 742.7 | 43 | 1 | 0 | 43 | 31936.1
35 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 744 | 43 | 1 | 0 | 43 | 31992
35 | 220kV Kakrapar-Vapi ckt # 1 | 0 | 26 |  |  | 0.43333 | 0 | 744 | 117 | 1 | 50.7 | 117 | 87048
36 | 220kV Kakrapar-Vapi ckt # 2 | 0 | 53 | 7 | 82 | 0.88333 | 8.3667 | 735.6333 | 117 | 1 | 103.35 | 117 | 86069.1
37 | 220kV Ichchapur-Vav |  |  |  |  | 0 | 0 | 744 | 34 | 1 | 0 | 34 | 25296
38 | 400kV V'chal - Satna # 1 |  |  | 0 | 14 | 0 | 0.23333 | 743.7667 | 267 | 2 | 0 | 534 | 397171.4
39 | 400kV V'chal - Satna # 2 | 0 | 50 | 0 | 18 | 0.83333 | 0.3 | 743.7 | 267 | 2 | 445 | 534 | 397135.8
40 | 400kV V'chal - Satna # 3 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
41 | 400kV V'chal - Satna # 4 |  |  |  |  | 0 | 0 | 744 | 258.31 | 2 | 0 | 516.62 | 384365.28
42 | 400kV Satna - Bina # 1 | 0 | 24 |  |  | 0.4 | 0 | 744 | 276 | 2 | 220.8 | 552 | 410688
43 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 744 | 276 | 2 | 0 | 552 | 410688
44 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  | 1 | 49 | 0 | 1.8167 | 742.1833 | 0.742 | 2 | 0 | 1.484 | 1101.4001
45 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  | 1 | 50 | 0 | 1.8333 | 742.1667 | 0.742 | 2 | 0 | 1.484 | 1101.3753
46 | 400 kV Gwalior-Bina # 1 | 5 | 38 |  |  | 5.6333 | 0 | 744 | 234.931 | 4 | 5293.7785 | 939.724 | 699154.656
47 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
48 | 400KV Satna-Bina # 3 |  |  |  |  | 0 | 0 | 744 | 272.586 | 2 | 0 | 545.172 | 405607.968
49 | 400KV Bina - Nagda # 1 | 0 | 18 |  |  | 0.3 | 0 | 744 | 330.155 | 2 | 198.093 | 660.31 | 491270.64
50 | 400KV Bina - Nagda # 2 |  |  | 0 | 10 | 0 | 0.16667 | 743.8333 | 330.155 | 2 | 0 | 660.31 | 491160.5883
51 | 400KV Nagda - Dehgam # 2 |  |  | 3 | 58 | 0 | 3.9667 | 740.0333 | 331.442 | 2 | 0 | 662.884 | 490556.2561
52 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 744 | 331.442 | 2 | 0 | 662.884 | 493185.696
53 | 400KV Seoni - Khandwa # 1 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
54 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 744 | 351.729 | 4 | 0 | 1406.916 | 1046745.504
55 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
56 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
57 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.01 | 2 | 0 | 8.02 | 5966.88
58 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
59 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 744 | 4.12 | 2 | 0 | 8.24 | 6130.56
60 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 744 | 220.588 | 2 | 0 | 441.176 | 328234.944
61 | 220 KV Vapi - Magarwada # 1 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
62 | 220 KV Vapi - Magarwada # 2 |  |  |  |  | 0 | 0 | 744 | 25.71 | 1 | 0 | 25.71 | 19128.24
63 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
64 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 744 | 29.66 | 1 | 0 | 29.66 | 22067.04
65 | 400 kV Gwalior-Bina # 2 |  |  |  |  | 0 | 0 | 744 | 233.652 | 4 | 0 | 934.608 | 695348.352
66 | 400 kV Seoni - Bina |  |  |  |  | 0 | 0 | 744 | 292.45 | 4 | 0 | 1169.8 | 870331.2
67 | 400kV Damoh - Bhopal # 1 |  |  |  |  | 0 | 0 | 744 | 214.471 | 2 | 0 | 428.942 | 319132.848
68 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 744 | 213.8 | 2 | 0 | 427.6 | 318134.4
69 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
70 | 220 KV Vapi - Khadoli # 2 |  |  |  |  | 0 | 0 | 744 | 28.549 | 1 | 0 | 28.549 | 21240.456
71 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
72 | 400kV Damoh-Birsinghpur#2 |  |  |  |  | 0 | 0 | 744 | 228.474 | 2 | 0 | 456.948 | 339969.312
73 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
74 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 744 | 46.67 | 2 | 0 | 93.34 | 69444.96
| Total Sr.No. 1 to 74 | 73 | 705 | 34 | 773 | 73.05 |  |  | 12271.634 |  | 27397.2215 |  | 19691267.3032
|  |  | 84.75 |  | 46.8833 |  |  |  |  | NAFM | 0.0013913
| Availability of 74 ( Sl no 1 to 74) transmission lines during MARCH-2011 = | [8 empty] | TAFM | 99.8609
Sr.No. 71,72,73 & 74 lines are declared for commercial operation w.e.f. 01.03.11
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5] | [THM*MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
0.63333
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
5 | 400/220kV ICT # 1 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900 | 0.83333
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
10 | 400/220kV ICT # 2 / Vapi | 11 | 51 |  |  | 11.85 | 0 | 744 | 315 | 2.5 | 9331.875 | 787.5 | 585900
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
12 | 400/220 KV ICT # 1 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
13 | 400/220kV ICT # 2 / Gwalior |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
14 | 400/220kV ICT # 1 / Itarsi | 2 | 48 |  |  | 2.8 | 0 | 744 | 315 | 2.5 | 2205 | 787.5 | 585900
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
17 | 400/220 KV ICT # 2 / Rajgarh |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 744 | 315 | 2.5 | 0 | 787.5 | 585900
| Total Sr.No. 1 to 19 | 13 | 99 | 0 | 0 | 14.65 |  |  | 5040 | 47.5 | 11536.875 |  | 11132100
|  | 14.65 |  | 0 | [5 empty] | NAFM | 0.0010364
[10 empty] | TAFM | 99.8964
Availability of 19 ( Sl no 1 to 19) ICTs in MARCH-2011 =
ICT # 1 at Pirana was declared for commercial operation w.e.f. 01.03.11
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4
|  | Hours | Mints | Hours | Mints |  | OH2 | =31*24-OH2
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 25 | 4 | 0 | 100 | 74400
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 744 | 80 | 4 | 0 | 320 | 238080
9 | Bus Reactor / Satna |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
10 | Bus Reactor # 1 / Bina |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 744 | 63 | 4 | 0 | 252 | 187488
12 | Bus Reactor / Gwalior |  |  |  |  | 0 | 0 | 744 | 50 | 4 | 0 | 200 | 148800
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 744 | 125 | 4 | 0 | 500 | 372000
| Total of sl no 1 to 14 | 0 | 0 | 0 | 0 |  |  |  | 882 | 56 | 0 |  | 2624832
0
[8 empty] | NAFM | 0
| Availability of 14( Sl no 1 to 14) Bus Reactors in MARCH-2011 = | [6 empty] | TAFM | 100
[11 empty] | 38934.0965 |  | 33448199.3032
[8 empty] | NAFM = | 0.001164
| % System Availability for MARCH 2011 = |  |  |  |  | TAFM= (100-100*NAFM) = |  |  | 99.8836
3
Note on B43: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B45: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B47: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B49: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B187: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B189: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## certificate
| Baart sarkar Government of India kond`Iya ivaVut p`aiQakrNa Central Electricity Authority piScama xao~Iya ivaVut saimait Western Regional Power Committee ef -3, emaAayaDIsaI xao~, AMQaorI (pUva-), mauMba[- - 400 093 F-3, MIDC Area, Andheri (East), Mum |  |  |  | Aa[- esa Aao : 9001--2008 ISO : 9001-2008
dUrBaaYa Phone: 022- 28221636; 28221681; 28220194-6; fO@sa Fax : 022 – 28370193 Website : www.wrpc.nic.in E-mail : opc-wrpc@nic.in
Ref: no: WRPC/OPN/PGCIL-TRAVAI/2013-14: Date:
CERTIFICATE FOR AVAILABILITY OF PGCIL(WRTS-II) TRANSMISSION SYSTEM (ELEMENT-WISE)
This is to certify that as per records the element-wise availability of PGCIL (WRTS-II) Transmission System in Western Region for the month of FEBRUARY 2014 is as under: -
SN | Element Name | % Availability | SN | Element Name | % Availability
1 | 400kV Satpura-Itarsi | 100% | 43 | 400kV V'chal -Nigrie | 100%
2 | 400kV Itarsi-Indore # 1 | 100% | 44 | 400kV Nigrie-Satna | 100%
3 | 400kV Itarsi-Indore # 2 | 100% | 45 | 400kV Satna - Bina # 1 | 100%
4 | 400kV Indore-Asoj # 1 | 100% | 46 | 400kV Satna - Bina # 2 | 100%
5 | 400kV Indore-Asoj # 2 | 100% | 47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 | 100%
6 | 400 KV V'chal - Jabalpur # 1 | 100% | 48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 | 100%
7 | 400 KV V'chal - Jabalpur # 2 | 100% | 49 | 765 kV Gwalior-Bina # 1 | 100%
8 | 400 KV Jabalpur - Itarsi # 1 | 99.55% | 50 | 400KV Satna-Bina # 4 | 100%
9 | 400 KV Jabalpur - Itarsi # 2 | 100% | 51 | 400KV Satna-Bina # 3 | 100%
10 | 400kV Jhanor-Dehgam#1 | 100% | 52 | 400KV Bina - Sujalpur # 1 | 100%
11 | 400kV Jhanor-Dehgam#2 | 100% | 53 | 400KV Bina - Sujalpur # 2 | 100%
12 | 400 KV Jabalpur-Sasan | 100% | 54 | 400KV Sujalpur - Nagda # 1 | 100%
13 | 400kV Sasan-Vindhyachal | 100% | 55 | 400KV Sujalpur - Nagda # 2 | 100%
14 | 400 KV V'chal - Jabalpur # 4 | 98.8% | 56 | 400KV Nagda - Dehgam # 2 | 100%
15 | 400 KV Jabalpur - Itarsi # 3 | 100% | 57 | 400KV Nagda - Dehgam # 1 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 | 99.98% | 58 | 400KV Seoni - Khandwa # 1 | 99.84%
17 | 400 KV Itarsi - Khandwa # 1 | 100% | 59 | 400KV Seoni - Khandwa # 2 | 100%
18 | 400 KV Itarsi - Khandwa # 2 | 100% | 60 | 400KV Khandwa - Rajgarh # 2 | 100%
19 | 400 KV Khandwa - Dhule # 1 | 100% | 61 | 400KV Rajgarh - SSP (LILO portion) # 1 | 100%
20 | 400 KV Khandwa - Dhule # 2 | 98.96% | 62 | 400KV Rajgarh - SSP (LILO portion) # 2 | 100%
21 | 400 KV Jhanor - Sugen(PGCIL portion) | 100% | 63 | 400KV Rajgarh - Nagda (LILO portion) # 1 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) | 100% | 64 | 400KV Rajgarh - Nagda (LILO portion) # 2 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) | 100% | 65 | 400KV Khandwa - Rajgarh # 1 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 | 100% | 66 | 220 KV Vapi - Magarwada # 1 | 99.2%
25 | 200kV Jhanor-Haldarwa ckt # 2 | 100% | 67 | 220 KV Vapi - Magarwada # 2 | 99.5%
26 | 220kV Kawas-Navsari (GIS)#1 | 100% | 68 | 220 KV Vapi - Karadpada # 1 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 | 100% | 69 | 220 KV Vapi - Karadpada # 2 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 | 100% | 70 | 765 kV Gwalior-Bina # 2 | 99.9%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 | 100% | 71 | 765 kV Seoni - Bina | 100%
30 | 220kV Kawas-Vav#1 | 100% | 72 | 400kV Damoh - Bhopal # 1 | 100%
31 | 220kV Kawas-Vav#2 | 100% | 73 | 400kV Damoh - Bhopal # 2 | 100%
32 | 220kV Kawas - Haldarwa # 1 | 99.98% | 74 | 220 KV Vapi - Khadoli # 1 | 100%
33 | 220kV Kawas-Haldarwa # 2 | 100% | 75 | 220 KV Vapi - Sayali | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 | 100% | 76 | 220kV Sayali-Khadoli | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 | 100% | 77 | 400kV Damoh-Birsinghpur#1 | 100%
36 | 220 KV Kakrapar - Vav # 1 | 100% | 78 | 400kV Damoh-Birsinghpur#2 | 100%
37 | 220 KV Kakrapar - Vav # 2 | 100% | 79 | 400kV Dehgam-Pirana#1 | 100%
38 | 220kV Kakrapar-Vapi ckt # 1 | 100% | 80 | 400kV Dehgam-Pirana#2 | 100%
39 | 220kV Kakrapar-Vapi ckt # 2 | 100% | 81 | 400kV Mundra - Bhachau # 1 | 100%
40 | 400kV V'chal - Satna # 1 | 100% | 82 | 400kV Mundra - Bhachau # 2 | 100%
41 | 400kV V'chal - Satna # 2 | 100% | 83 | 400kV Bhachau - Ranchodpura # 1 | 100%
42 | 400kV V'chal - Satna # 3 | 100% | 84 | 400kV Bhachau - Ranchodpura # 2 | 100%
85 | 400kV Mundra - Limbdi # 1 | 97.27% | 135 | 400/220 KV ICT # 2 / Bhachau | 100%
86 | 400kV Mundra - Limbdi # 2 | 100% | 136 | 400/220 KV ICT # 2 / Shujalpur | 100%
87 | 765kV Satna - Bina # 1 | 100% | 137 | 765/400KV ICT# 1 / Satna | 100%
88 | 765kV Satna - Bina # 2 | 99.26% | 138 | 400/220 KV ICT # 2 / Navsari | 100%
89 | 765kV Bina - Indore | 100% | 139 | 400/220 KV ICT # 1 / Navsari | 100%
90 | 400kV Gandhar - Navsari # 2 | 100% | 140 | 765/400KV ICT# 2 / Satna | 100%
91 | 400kV Gandhar - Navsari # 1 | 100% | 141 | 765/400KV ICT# 1 / Bina | 100%
92 | 400kV Mundra-Jetpur#1 | 100% | 142 | 400kV ICT#3/Vapi | 100%
93 | 400kV Mundra-Jetpur#2 | 100% | 143 | 765/400KV ICT# 2 / Bina | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 | 100% | 144 | 765/400KV ICT# 1 / Gwalior | 100%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 | 100% | 145 | 765/400KV ICT# 2 / Gwalior | 100%
96 | 400kV V'chal (Pooling) - Sasan #1 | 100% | 146 | 765/400KV ICT# 2 / INDORE | 100%
97 | 400k V'chal (Pooling) - Sasan # 2 | 100% | 147 | 765/400KV ICT# 1 / INDORE | 100%
98 | 765kV Sasan - Satna # 1 | 100% | 148 | 765/400KV ICT# 1 / JABALPUR POOL | 100%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 | 100% | 149 | Bus reactor / Dehgam | 100%
100 | 400kV Vapi-Navsari#1 | 100% | 150 | 25 MVAR reactor # 1 / Jabalpur | 100%
101 | 400kV Vapi-Navsari#2 | 100% | 151 | 25 MVAR reactor # 2 / Jabalpur | 100%
102 | 765kV Sasan - Satna # 2 | 100% | 152 | Bus reactor # 1 / Itarsi | 100%
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 | 100% | 153 | Bus reactor # 2 / Itarsi | 100%
104 | 400kV Indore (MP)-Indore (PG)#1 | 100% | 154 | Bus Reactor # 3 / Itarsi | 100%
105 | 400kV Indore (MP)-Indore (PG)#2 | 100% | 155 | Bus Reactor # 3 / Jabalpur | 100%
106 | 400kV Jabalpur - Jabalpur Pooling#1 | 100% | 156 | Bus Reactor / Dhule | 100%
107 | 400kV Jabalpur - Jabalpur Pooling#2 | 99.97% | 157 | Bus Reactor-I (50 MVAR) / Satna | 100%
108 | 765kV Jabalpur Pooling - Bina # 1 | 99.68% | 158 | Bus Reactor # 1 (63 MVAR) / Bina | 100%
109 | 765kV Jabalpur Pooling - Bina # 2 | 100% | 159 | Bus Reactor / Damoh | 100%
110 | 765 kV Gwalior -Agra # 1 | 100% | 160 | Bus Reactor-I / Gwalior | 100%
111 | 765 kV Gwalior -Agra # 2 | 100% | 161 | Bus Reactor / Khandwa | 100%
112 | 400/220kV ICT # 1 / Jabalpur. | 100% | 162 | Bus Reactor / Dehgam | 100%
113 | 400/220kV ICT # 2 /Jabalpur. | 100% | 163 | Bus Reactor / Bhachau | 100%
114 | 400/220 KV ICT # 1 / Dehgam | 100% | 164 | Bus Reactor / Shujalpur | 100%
115 | 400/220 KV ICT # 2/ Dehgam | 100% | 165 | Bus Reactor/ Rajgarh | 100%
116 | 400/220kV ICT # 1 / Satna | 99.77% | 166 | Bus Reactor / Satna 765KV | 100%
117 | 400/220kV ICT # 2 / Satna | 100% | 167 | Bus Reactor / Navsari | 100%
118 | 400/220kV ICT # 1 / Khandwa | 100% | 168 | Switchable Bina-I Line Reactor / Satna 765KV | 100%
119 | 400/220kV ICT # 2 / Khandwa | 100% | 169 | Switchable Bina-II Line Reactor / Satna 765KV | 100%
120 | 400/220kV ICT # 1 / Vapi | 100% | 170 | Bus Reactor-II (63 MVAR)/Satna | 100%
121 | 400/220kV ICT # 2 / Vapi | 100% | 171 | Switchable Bina-I Line Reactor / Gwalior 765KV | 100%
122 | 400/220kV ICT # 1 / Gwalior | 100% | 172 | Switchable Bina-II Line Reactor / Gwalior 765KV | 100%
123 | 400/220 KV ICT # 1 / Rajgarh | 99.42% | 173 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV | 100%
124 | 400/220kV ICT # 2 / Gwalior | 99.41% | 174 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV | 100%
125 | 400/220kV ICT # 1 / Itarsi | 100% | 175 | Bus Reactor-II/Gwalior 400kV | 100%
126 | 400/220kV ICT # 1 / Damoh | 100% | 176 | Bus Reactor-III/Gwalior 400kV | 100%
127 | 400/220kV ICT # 2 / Damoh | 100% | 177 | Bus Reactor-I/Indore 400kV | 100%
128 | 400/220 KV ICT # 2 / Rajgarh | 99.6% | 178 | Switchable Indore - Line Reactor / Bina 765KV | 100%
129 | 400/220 KV ICT / Bina | 100% | 179 | Switchable Shujalpur-II Line Reactor / Bina 400kV | 100%
130 | 400/220 KV ICT # 1 / Pirana | 100% | 180 | Switchable Shujalpur-I Line Reactor / Bina 400kV | 100%
131 | 400/220 KV ICT # 2 / Pirana | 100% | 181 | Bus Reactor-I / Indore 765kV | 100%
132 | 400/220 KV ICT # 3 / Gwalior | 100% | 182 | Switchable Bina - I Line Reactor / Jabalpur Pooling 765kV | 100%
133 | 400/220 KV ICT # 1 / Shujalpur | 100% | 183 | Bus Reactor 400kV / Jabalpur Pool 765kV | 100%
134 | 400/220 KV ICT # 1 / Bhachau | 100% | 184 | Bus Reactor-I / Bina 765kV | 100%
The above availability has been calculated as per the procedure specified in CERC Regulations for 2009 – 2014 and CERC notification L-1/67/2012-CERC Dated 17/09/2012.
(S D TAKSANDE) Member Secretary I/c
Availability Bus Reactors =
System Availability :-
Note on B23: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B24: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B25: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B77: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B78: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## INDEX
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR FEBRUARY -2014
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved | Target Availability as per SOP
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =28*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 672 | 79 | 2 | 0 | 158 | 106176 | 0 | 100 | 100% | 90%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 672 | 207 | 2 | 0 | 414 | 278208 | 0 | 100 | 100% | 90%
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 672 | 214 | 2 | 0 | 428 | 287616 | 0 | 100 | 100% | 90%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 672 | 289 | 2 | 0 | 578 | 388416 | 0 | 100 | 100% | 90%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 672 | 273 | 2 | 0 | 546 | 366912 | 0 | 100 | 100% | 90%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 672 | 360 | 2 | 0 | 720 | 483840 | 0 | 100 | 100% | 90%
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 672 | 360 | 2 | 0 | 720 | 483840 | 0 | 100 | 100% | 90%
8 | 400 KV Jabalpur - Itarsi # 1 | 3 | 2 |  |  | 3.0333 | 0 | 672 | 232 | 2 | 1407.4667 | 464 | 311808 | 0.0045139 | 99.5486 | 99.55% | 90%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 672 | 232 | 2 | 0 | 464 | 311808 | 0 | 100 | 100% | 90%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 672 | 157 | 2 | 0 | 314 | 211008 | 0 | 100 | 100% | 90%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 672 | 157 | 2 | 0 | 314 | 211008 | 0 | 100 | 100% | 90%
12 | 400 KV Jabalpur-Sasan |  |  | 0 | 53 | 0 | 0.88333 | 671.1167 | 376 | 2 | 0 | 752 | 504679.7333 | 0 | 100 | 100% | 90%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 672 | 21 | 2 | 0 | 42 | 28224 | 0 | 100 | 100% | 90%
14 | 400 KV V'chal - Jabalpur # 4 | 7 | 56 | 10 | 76 | 7.9333 | 11.2667 | 660.7333 | 389 | 2 | 6172.1333 | 778 | 514050.5333 | 0.012007 | 98.7993 | 98.8% | 90%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 672 | 234 | 2 | 0 | 468 | 314496 | 0 | 100 | 100% | 90%
16 | 400 KV Jabalpur - Itarsi # 4 | 0 | 10 | 0 | 6 | 0.16667 | 0.1 | 671.9 | 234 | 2 | 78 | 468 | 314449.2 | 0.00024805 | 99.9752 | 99.98% | 90%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 672 | 196.64 | 2 | 0 | 393.28 | 264284.16 | 0 | 100 | 100% | 90%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 672 | 196.64 | 2 | 0 | 393.28 | 264284.16 | 0 | 100 | 100% | 90%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 672 | 261.78 | 2 | 0 | 523.56 | 351832.32 | 0 | 100 | 100% | 90%
20 | 400 KV Khandwa - Dhule # 2 | 6 | 52 | 12 | 0 | 6.8667 | 12 | 660 | 261.78 | 2 | 3595.112 | 523.56 | 345549.6 | 0.010404 | 98.9596 | 98.96% | 90%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 672 | 57 | 2 | 0 | 114 | 76608 | 0 | 100 | 100% | 90%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 0 | 55 | 0 | 0.91667 | 672 | 110 | 2 | 0 | 220 | 147840 | 0 | 100 | 100% | 90%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 672 | 13 | 2 | 0 | 26 | 17472 | 0 | 100 | 100% | 90%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 672 | 13 | 1 | 0 | 13 | 8736 | 0 | 100 | 100% | 90%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 672 | 13 | 1 | 0 | 13 | 8736 | 0 | 100 | 100% | 90%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 672 | 58.149 | 1 | 0 | 58.149 | 39076.128 | 0 | 100 | 100% | 90%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  |  |  | 0 | 0 | 672 | 58.149 | 1 | 0 | 58.149 | 39076.128 | 0 | 100 | 100% | 90%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 672 | 31.334 | 1 | 0 | 31.334 | 21056.448 | 0 | 100 | 100% | 90%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 |  |  |  |  | 0 | 0 | 672 | 31.334 | 1 | 0 | 31.334 | 21056.448 | 0 | 100 | 100% | 90%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 672 | 37 | 1 | 0 | 37 | 24864 | 0 | 100 | 100% | 90%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 672 | 37 | 1 | 0 | 37 | 24864 | 0 | 100 | 100% | 90%
32 | 220kV Kawas - Haldarwa # 1 | 0 | 10 | 1 | 47 | 0.16667 | 1.7833 | 670.2167 | 81 | 1 | 13.5 | 81 | 54287.55 | 0.00024868 | 99.9751 | 99.98% | 90%
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 672 | 81 | 1 | 0 | 81 | 54432 | 0 | 100 | 100% | 90%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 672 | 74 | 1 | 0 | 74 | 49728 | 0 | 100 | 100% | 90%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 672 | 74 | 1 | 0 | 74 | 49728 | 0 | 100 | 100% | 90%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 672 | 43 | 1 | 0 | 43 | 28896 | 0 | 100 | 100% | 90%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 672 | 43 | 1 | 0 | 43 | 28896 | 0 | 100 | 100% | 90%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 672 | 117 | 1 | 0 | 117 | 78624 | 0 | 100 | 100% | 90%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 672 | 117 | 1 | 0 | 117 | 78624 | 0 | 100 | 100% | 90%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 672 | 267 | 2 | 0 | 534 | 358848 | 0 | 100 | 100% | 90%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 672 | 267 | 2 | 0 | 534 | 358848 | 0 | 100 | 100% | 90%
42 | 400kV V'chal - Satna # 3 |  |  | 11 | 10 | 0 | 11.1667 | 660.8333 | 258.31 | 2 | 0 | 516.62 | 341399.7167 | 0 | 100 | 100% | 90%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 672 | 100.32 | 2 | 0 | 200.64 | 134830.08 | 0 | 100 | 100% | 90%
44 | 400kV Nigrie-Satna |  |  |  |  | 0 | 0 | 672 | 161.11 | 2 | 0 | 322.22 | 216531.84 | 0 | 100 | 100% | 90%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 672 | 276 | 2 | 0 | 552 | 370944 | 0 | 100 | 100% | 90%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 672 | 276 | 2 | 0 | 552 | 370944 | 0 | 100 | 100% | 90%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 672 | 0.742 | 2 | 0 | 1.484 | 997.248 | 0 | 100 | 100% | 90%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 672 | 0.742 | 2 | 0 | 1.484 | 997.248 | 0 | 100 | 100% | 90%
49 | 765 kV Gwalior-Bina # 1 |  |  | 0 | 55 | 0 | 0.91667 | 671.0833 | 234.931 | 4 | 0 | 939.724 | 630633.1143 | 0 | 100 | 100% | 90% | Upgraded to 765kV level w.e.f 01.04.2013
50 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 672 | 272.586 | 2 | 0 | 545.172 | 366355.584 | 0 | 100 | 100% | 90%
51 | 400KV Satna-Bina # 3 |  |  | 8 | 21 | 0 | 8.35 | 663.65 | 272.586 | 2 | 0 | 545.172 | 361803.3978 | 0 | 100 | 100% | 90%
52 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 672 | 199.936 | 2 | 0 | 399.872 | 268713.984 | 0 | 100 | 100% | 90%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 672 | 199.936 | 2 | 0 | 399.872 | 268713.984 | 0 | 100 | 100% | 90%
54 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 672 | 152.229 | 2 | 0 | 304.458 | 204595.776 | 0 | 100 | 100% | 90%
55 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 672 | 152.229 | 2 | 0 | 304.458 | 204595.776 | 0 | 100 | 100% | 90%
56 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 672 | 331.442 | 2 | 0 | 662.884 | 445458.048 | 0 | 100 | 100% | 90%
57 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 672 | 331.442 | 2 | 0 | 662.884 | 445458.048 | 0 | 100 | 100% | 90%
58 | 400KV Seoni - Khandwa # 1 | 1 | 3 |  |  | 1.05 | 0 | 672 | 351.729 | 4 | 1477.2618 | 1406.916 | 945447.552 | 0.0015625 | 99.8438 | 99.84% | 90%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 672 | 351.729 | 4 | 0 | 1406.916 | 945447.552 | 0 | 100 | 100% | 90%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 672 | 220.588 | 2 | 0 | 441.176 | 296470.272 | 0 | 100 | 100% | 90%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 672 | 4.01 | 2 | 0 | 8.02 | 5389.44 | 0 | 100 | 100% | 90%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  | 10 | 0 | 0.16667 | 671.8333 | 4.01 | 2 | 0 | 8.02 | 5388.1033 | 0 | 100 | 100% | 90%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  | 51 | 29 | 0 | 51.4833 | 620.5167 | 4.12 | 2 | 0 | 8.24 | 5113.0573 | 0 | 100 | 100% | 90%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 672 | 4.12 | 2 | 0 | 8.24 | 5537.28 | 0 | 100 | 100% | 90%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 672 | 220.588 | 2 | 0 | 441.176 | 296470.272 | 0 | 100 | 100% | 90%
66 | 220 KV Vapi - Magarwada # 1 | 5 | 21 |  |  | 5.35 | 0 | 672 | 25.71 | 1 | 137.5485 | 25.71 | 17277.12 | 0.0079613 | 99.2039 | 99.2% | 90%
67 | 220 KV Vapi - Magarwada # 2 | 3 | 21 |  |  | 3.35 | 0 | 672 | 25.71 | 1 | 86.1285 | 25.71 | 17277.12 | 0.0049851 | 99.5015 | 99.5% | 90%
68 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 672 | 29.66 | 1 | 0 | 29.66 | 19931.52 | 0 | 100 | 100% | 90%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 672 | 29.66 | 1 | 0 | 29.66 | 19931.52 | 0 | 100 | 100% | 90%
70 | 765 kV Gwalior-Bina # 2 | 0 | 42 |  |  | 0.7 | 0 | 672 | 233.652 | 4 | 654.2256 | 934.608 | 628056.576 | 0.0010417 | 99.8958 | 99.9% | 90% | Upgraded to 765kV level w.e.f 01.04.2013
71 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 672 | 292.046 | 4 | 0 | 1168.184 | 785019.648 | 0 | 100 | 100% | 90%
72 | 400kV Damoh - Bhopal # 1 |  |  | 0 | 10 | 0 | 0.16667 | 671.8333 | 214.471 | 2 | 0 | 428.942 | 288177.5337 | 0 | 100 | 100% | 90%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 672 | 213.8 | 2 | 0 | 427.6 | 287347.2 | 0 | 100 | 100% | 90%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 672 | 28.549 | 1 | 0 | 28.549 | 19184.928 | 0 | 100 | 100% | 90%
75 | 220 KV Vapi - Sayali |  |  |  |  | 0 | 0 | 672 | 18.3 | 1 | 0 | 18.3 | 12297.6 | 0 | 100 | 100% | 90%
76 | 220kV Sayali-Khadoli |  |  |  |  | 0 | 0 | 672 | 12.235 | 1 | 0 | 12.235 | 8221.92 | 0 | 100 | 100% | 90%
77 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 672 | 228.474 | 2 | 0 | 456.948 | 307069.056 | 0 | 100 | 100% | 90%
78 | 400kV Damoh-Birsinghpur#2 |  |  | 0 | 10 | 0 | 0.16667 | 671.8333 | 228.474 | 2 | 0 | 456.948 | 306992.898 | 0 | 100 | 100% | 90%
79 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 672 | 46.67 | 2 | 0 | 93.34 | 62724.48 | 0 | 100 | 100% | 90%
80 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 672 | 46.67 | 2 | 0 | 93.34 | 62724.48 | 0 | 100 | 100% | 90%
81 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 672 | 99.468 | 3 | 0 | 298.404 | 200527.488 | 0 | 100 | 100% | 90%
82 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 672 | 99.468 | 3 | 0 | 298.404 | 200527.488 | 0 | 100 | 100% | 90%
83 | 400kV Bhachau - Ranchodpura # 1 | 0 | 2 |  |  | 0.033333 | 0 | 672 | 282.856 | 3 | 28.2856 | 848.568 | 570237.696 | 4.9603e-05 | 99.995 | 100% | 90%
84 | 400kV Bhachau - Ranchodpura # 2 |  |  |  |  | 0 | 0 | 672 | 282.856 | 3 | 0 | 848.568 | 570237.696 | 0 | 100 | 100% | 90%
85 | 400kV Mundra - Limbdi # 1 | 18 | 1 | 12 | 30 | 18.0167 | 12.5 | 659.5 | 314.053 | 3 | 16974.5647 | 942.159 | 621353.8605 | 0.027319 | 97.2681 | 97.27% | 90%
86 | 400kV Mundra - Limbdi # 2 |  |  |  |  | 0 | 0 | 672 | 314.053 | 3 | 0 | 942.159 | 633130.848 | 0 | 100 | 100% | 90%
87 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 672 | 274.164 | 4 | 0 | 1096.656 | 736952.832 | 0 | 100 | 100% | 90%
88 | 765kV Satna - Bina # 2 | 5 | 0 |  |  | 5 | 0 | 672 | 275.635 | 4 | 5512.7 | 1102.54 | 740906.88 | 0.0074405 | 99.256 | 99.26% | 90%
89 | 765kV Bina - Indore |  |  |  |  | 0 | 0 | 672 | 311.81 | 4 | 0 | 1247.24 | 838145.28 | 0 | 100 | 100% | 90% | upgraded to 765kV level w.e.f. 01.07.2013
90 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 672 | 102.152 | 2 | 0 | 204.304 | 137292.288 | 0 | 100 | 100% | 90%
91 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 672 | 102.152 | 2 | 0 | 204.304 | 137292.288 | 0 | 100 | 100% | 90%
92 | 400kV Mundra-Jetpur#1 |  |  |  |  | 0 | 0 | 672 | 337 | 3 | 0 | 1011 | 679392 | 0 | 100 | 100% | 90%
93 | 400kV Mundra-Jetpur#2 |  |  |  |  | 0 | 0 | 672 | 337 | 3 | 0 | 1011 | 679392 | 0 | 100 | 100% | 90%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 672 | 28.55 | 4 | 0 | 114.2 | 76742.4 | 0 | 100 | 100% | 90%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 672 | 28.55 | 4 | 0 | 114.2 | 76742.4 | 0 | 100 | 100% | 90%
96 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 672 | 5.443 | 2 | 0 | 10.886 | 7315.392 | 0 | 100 | 100% | 90%
97 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 672 | 5.443 | 2 | 0 | 10.886 | 7315.392 | 0 | 100 | 100% | 90%
98 | 765kV Sasan - Satna # 1 |  |  | 3 | 17 | 0 | 3.2833 | 668.7167 | 245.7 | 4 | 0 | 982.8 | 657214.74 | 0 | 100 | 100% | 90%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 672 | 0.62 | 2 | 0 | 1.24 | 833.28 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.03.2013
100 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 672 | 116.85 | 2 | 0 | 233.7 | 157046.4 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.04.2013
101 | 400kV Vapi-Navsari#2 |  |  |  |  | 0 | 0 | 672 | 116.85 | 2 | 0 | 233.7 | 157046.4 | 0 | 100 | 100% | 90%
102 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 672 | 242.23 | 4 | 0 | 968.92 | 651114.24 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.05.2013
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 672 | 0.62 | 2 | 0 | 1.24 | 833.28 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.06.2013
104 | 400kV Indore (MP)-Indore (PG)#1 |  |  |  |  | 0 | 0 | 672 | 49.726 | 4 | 0 | 198.904 | 133663.488 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.07.2013
105 | 400kV Indore (MP)-Indore (PG)#2 |  |  |  |  | 0 | 0 | 672 | 49.726 | 4 | 0 | 198.904 | 133663.488 | 0 | 100 | 100% | 90%
106 | 400kV Jabalpur - Jabalpur Pooling#1 |  |  |  |  | 0 | 0 | 672 | 15.456 | 4 | 0 | 61.824 | 41545.728 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.01.2014
107 | 400kV Jabalpur - Jabalpur Pooling#2 | 0 | 13 |  |  | 0.21667 | 0 | 672 | 15.456 | 4 | 13.3952 | 61.824 | 41545.728 | 0.00032242 | 99.9678 | 99.97% | 90%
108 | 765kV Jabalpur Pooling - Bina # 1 | 2 | 11 | 0 | 10 | 2.1833 | 0.16667 | 671.8333 | 229.74 | 4 | 2006.396 | 918.96 | 617387.96 | 0.0032498 | 99.675 | 99.68% | 90%
109 | 765kV Jabalpur Pooling - Bina # 2 |  |  |  |  | 0 | 0 | 672 | 229.74 | 4 | 0 | 918.96 | 617541.12 | 0 | 100 | 100% | 90%
| Total Sr.No. 1 to 109 | 50 | 244 | 108 | 439 |  |  |  | 16922.689 |  | 38156.7179 |  | 28016195.4623
* | Lines charged with 400kV level
|  | 54.0667 |  | 115.3167
[10 empty] | NAFM | 0.001362
Availability of ( Sl no 1 to 109) transmission lines during FEBRUARY -2014 = | [9 empty] | TAFM | 99.8638
110 | 765 kV Gwalior -Agra # 1 | 0 | 0 | 4 | 52 | 0 | 4.8667 | 667.1333 | 129.435 | 4 | 0 | 517.74 | 345401.612 | 0 | 100 | 100% | 90%
111 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 672 | 127.934 | 4 | 0 | 511.736 | 343886.592 | 0 | 100 | 100% | 90%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =28*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
112 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
113 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
114 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
115 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90% |  | 0.83333
116 | 400/220kV ICT # 1 / Satna | 1 | 33 |  |  | 1.55 | 0 | 672 | 315 | 2.5 | 1220.625 | 787.5 | 529200 | 0.0023065 | 99.7693 | 99.77% | 90%
117 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
118 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
119 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
120 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
121 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
122 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
123 | 400/220 KV ICT # 1 / Rajgarh | 3 | 52 |  |  | 3.8667 | 0 | 672 | 315 | 2.5 | 3045 | 787.5 | 529200 | 0.005754 | 99.4246 | 99.42% | 90%
124 | 400/220kV ICT # 2 / Gwalior | 3 | 58 |  |  | 3.9667 | 0 | 672 | 315 | 2.5 | 3123.75 | 787.5 | 529200 | 0.0059028 | 99.4097 | 99.41% | 90%
125 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
126 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
127 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
128 | 400/220 KV ICT # 2 / Rajgarh | 2 | 40 |  |  | 2.6667 | 0 | 672 | 315 | 2.5 | 2100 | 787.5 | 529200 | 0.0039683 | 99.6032 | 99.6% | 90%
129 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
130 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
131 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
132 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
133 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
134 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
135 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
136 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
137 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100% | 90%
138 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
139 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90%
140 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100% | 90%
141 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.03.2013
142 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.04.2013
143 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100% | 90%
144 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | 90%
145 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | 90%
146 | 765/400KV ICT# 2 / INDORE |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.07.2013
147 | 765/400KV ICT# 1 / INDORE |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.10.2013
148 | 765/400KV ICT# 1 / JABALPUR POOL |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.01.2014
| Total Sr.No. 1 to 37 | 9 | 183 | 0 | 0 |  |  |  | 20320 |  | 9489.375 |  | 34137600
|  | 12.05 |  | 0 | [5 empty] | NAFM | 0.00027797
Availability of 37 ( Sl no 1 to 37) ICTs in FEBRUARY -2014 = | [9 empty] | TAFM | 99.9722
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =28*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
149 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
150 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 672 | 25 | 4 | 0 | 100 | 67200 | 0 | 100 | 100% | 90%
151 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 672 | 25 | 4 | 0 | 100 | 67200 | 0 | 100 | 100% | 90%
152 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100% | 90%
153 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100% | 90%
154 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100% | 90%
155 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
156 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 672 | 80 | 4 | 0 | 320 | 215040 | 0 | 100 | 100% | 90%
157 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100% | 90%
158 | Bus Reactor # 1 (63 MVAR) / Bina |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
159 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
160 | Bus Reactor-I / Gwalior |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100% | 90%
161 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90%
162 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90%
163 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
164 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
165 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90%
166 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90%
167 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
168 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90%
169 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.04.2013
170 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
171 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90%
172 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90%
173 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.06.2013
174 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
175 | Bus Reactor-II/Gwalior |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.10.2013
176 | Bus Reactor-III/Gwalior |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90%
177 | Bus Reactor-I/Indore |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90%
178 | Switchable Indore - Line Reactor / Bina 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90%
179 | Switchable Shujalpur-II Line Reactor / Bina 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
180 | Switchable Shujalpur-I Line Reactor / Bina 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | 90%
181 | Bus Reactor-I / Indore 765kV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.11.2013
182 | Switchable Bina - I Line Reactor / Jabalpur Pooling 765kV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90% | Commercial operation w.e.f. 01.01.2014
183 | Bus Reactor 400kV / Jabalpur Pool 765kV |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | 90%
184 | Bus Reactor-I / Bina 765kV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | 90%
| Total of sl no 1 to 36 | 0 | 0 | 0 | 0 |  |  |  | 4171 |  | 0 |  | 11211648
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 36 ( Sl no 1 to 36) Bus Reactors in FEBRUARY -2014 = | [7 empty] | TAFM | 100
[11 empty] | 47646.0929 |  | 73365443.4623
[8 empty] | NAFM = | 0.00064944
% System Availability for FEBRUARY -2014 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9351
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B142: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B143: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## Feb'14 Tripping details
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF FEBRUARY 2014
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | OUTAGE HOURS ATTRIBUTED TO | [11 empty] | Outage Category | Details | WRLDC CODE FOR |  | Line length(ckt Km) /MVA /MVAR Rating | NSC/ Factor | Outage Hrs (OH) Attributed to PGCIL | Line/MVA/MVAr * NSC * OH | THM E | Line/MVA/MVAr * NSC/Factor | THM * Ckt Km * NSC | NAFM | % Availability
[7 empty] | ATTRIBUTED TO PGCIL |  |  | OTHERS |  |  | SYSTEM CONSTR. |  |  | OUTAGE DEEMED AVAILABLE |  |  |  |  | TRIPPING | CHARGING
[8 empty] | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  | HRS | MIN |  |  |  |  | A | B | C | D=A*B*C | 672 | F=A*B | G=E*F | I=D/(E*F) | J=(100-100*I)
1 | 902099 | SATPURA-ITARSI 400kV | 2014-02-18 | 14:50 | 2014-02-18 | 20:41 | - |  |  | - |  |  | - |  |  | 0.24375 | 5 | 51 | SCSD | Line H/T to avail S/D OCC approved S/D for CB replacement & retrofitting of AR relay at Satpura end. | LD 02/1908 | LD 02/1950
| 902107 | SATPURA-ITARSI 400kV | 2014-02-19 | 12:17 | 2014-02-19 | 20:27 | - |  |  | - |  |  | - |  |  | 0.34028 | 8 | 10 | SCSD | Line H/T to avail OCC approved S/D for retrofitting of CB at satpura end. | LD 02/2018 | LD 02/2087
| 902121 | SATPURA-ITARSI 400kV | 2014-02-24 | 17:35 | 2014-02-24 | 17:35 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Auto reclose successful at both ends, B ph to E/F, Dist- 58.42kM from Itarsi
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58403 | 13 | 61
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 14.0167 |  |  |  |  | 79 | 2 | 0 | 0 | 672 | 158 | 106176 | 0 | 100%
2 |  | ITARSI-INDORE I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 207 | 2 | 0 | 0 | 672 | 414 | 278208 | 0 | 100%
3 |  | ITARSI-INDORE II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 214 | 2 | 0 | 0 | 672 | 428 | 287616 | 0 | 100%
4 | 902109 | INDORE-ASOJ I 400kV | 2014-02-20 | 09:38 | 2014-02-20 | 18:39 | - |  |  | - |  |  | - |  |  | 0.37569 | 9 | 1 | OSPD | Line H/T to avail OCC approved S/D by MPPTCL to facilitate Line srossing work of 400kV Indore - Pithampura MPPTCL Line. | LD 01/2135 | LD 02/2178
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37569 | 9 | 1
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.0167 |  |  |  |  | 289 | 2 | 0 | 0 | 672 | 578 | 388416 | 0 | 100%
5 |  | INDORE-ASOJ II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 273 | 2 | 0 | 0 | 672 | 546 | 366912 | 0 | 100%
6 |  | VINDHYACHAL-JABALPUR I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 360 | 2 | 0 | 0 | 672 | 720 | 483840 | 0 | 100%
7 |  | VINDHYACHAL-JABALPUR II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 360 | 2 | 0 | 0 | 672 | 720 | 483840 | 0 | 100%
8 | 902042 | JABALPUR-ITARSI I 400kV | 2014-02-07 | 09:46 | 2014-02-07 | 12:48 | 0.12639 | 3 | 2 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC approved S/D by POWERGRID for AMP work. | LD 02/639 | LD 02/666
|  | SUBTOTAL |  |  |  |  | 0.12639 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.0333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 232 | 2 | 3.0333 | 1407.4667 | 672 | 464 | 311808 | 0.0045139 | 99.55%
9 |  | JABALPUR-ITARSI II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 232 | 2 | 0 | 0 | 672 | 464 | 311808 | 0 | 100%
10 |  | GANDHAR-DEHGAM I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 672 | 314 | 211008 | 0 | 100%
11 |  | GANDHAR-DEHGAM II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 157 | 2 | 0 | 0 | 672 | 314 | 211008 | 0 | 100%
12 | 902151 | SASAN (RELIANCE) - JABALPUR 400kV | 2014-02-27 | 20:12 | 2014-02-27 | 21:05 | - |  |  | - |  |  | 0.036806 | 0 | 53 | - |  |  | LNCC | A/T on B-ph to E/F (F/L-302km from JBP) during heavy lightening & thunder storm in that area. |  | LD 02/3060
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.036806 | 0 | 53 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.88333 |  |  | 0 |  |  |  |  | 376 | 2 | 0 | 0 | 671.1167 | 752 | 504679.7333 | 0 | 100%
13 |  | VINDHYACHAL (NTPC)-SASAN (RELIANCE) III 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 21 | 2 | 0 | 0 | 672 | 42 | 28224 | 0 | 100%
14 | 902113 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-22 | 15:27 | 2014-02-22 | 15:37 | 0.0069444 | 0 | 10 | - |  |  | - |  |  | - |  |  | LEFT | Line A/T on B-PH to E/F. F/L-386 KM AND F/C-1.025 KA from Jabalpur end.
| 902114 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-22 | 15:37 | 2014-02-22 | 17:15 | - |  |  | 0.068056 | 1 | 38 | - |  |  | - |  |  | OMSU | Line ready for charging but was delayed by NTPC. |  | LD 02/2384
| 902115 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-22 | 17:34 | 2014-02-22 | 19:35 | 0.084028 | 2 | 1 | - |  |  | - |  |  | - |  |  | LEFT | Line A/T on B-PH to E/F. F/L-386 KM AND F/C-1.042 KA from Jabalpur end.
| 902117 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-22 | 19:35 | 2014-02-22 | 23:59 | - |  |  | 0.18333 | 4 | 24 | - |  |  | - |  |  | OMSU | Line ready for charging but not allowed by WRLDC. |  | LD 02/2423
| 902144 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-27 | 08:46 | 2014-02-27 | 19:45 | 0.23958 | 5 | 45 | - |  |  | - |  |  | - |  |  | LEFT | A/T on B-ph (Top phase) to E/F due to Low clearance in B-ph and OPGW between span 26-27-28, F/L:Jabalpur-385km & V'chal-7.03km. After rectification of OPGW problem from 19:45Hrs onwards Line kept out for voltage regulation on WRLDC Instruction vide code LD 02/3068. The restoration was delayed due to severe rains & heavy winds persisting in that area till 14:00 hrs. As such outage till 14:00 hrs may not be attributed to POWERGRID.
| 902147 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-27 | 08:46 | 2014-02-27 | 19:45 | - |  |  | - |  |  | 0.21806 | 5 | 14 | - |  |  | LNCC | A/T on B-ph (Top phase) to E/F due to Low clearance in B-ph and OPGW between span 26-27-28, F/L:Jabalpur-385km & V'chal-7.03km. After rectification of OPGW problem from 19:45Hrs onwards Line kept out for voltage regulation on WRLDC Instruction vide code LD 02/3068. The restoration was delayed due to severe rains & heavy winds persisting in that area till 14:00 hrs. As such outage till 14:00 hrs may not be attributed to POWERGRID.
| 902150 | VINDHYACHAL-JABALPUR IV 400kV | 2014-02-27 | 19:45 | 2014-02-28 | 07:30 | - |  |  | - |  |  | - |  |  | 0.48958 | 11 | 45 | LVRD | After Complition of Rectification of OPGW clearance problem PTW returned by WRLDC by 19:45hrs | LD 02/3068 | LD 02/3096
|  | SUBTOTAL |  |  |  |  | 0.33056 | 7 | 56 | 0.25139 | 5 | 62 | 0.21806 | 5 | 14 | 0.48958 | 11 | 45
|  | Element Availability= | [6 empty] | 7.9333 |  |  | 6.0333 |  |  | 5.2333 |  |  | 11.75 |  |  |  |  | 389 | 2 | 7.9333 | 6172.1333 | 660.7333 | 778 | 514050.5333 | 0.012007 | 98.8%
15 | 902015 | JABALPUR-ITARSI III 400kV | 2014-02-02 | 23:03 | 2014-02-03 | 09:40 | - |  |  | - |  |  | - |  |  | 0.44236 | 10 | 37 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/185
| 902018 | JABALPUR-ITARSI III 400kV | 2014-02-03 | 09:40 | 2014-02-03 | 18:08 | - |  |  | - |  |  | - |  |  | 0.35278 | 8 | 28 | LCSD | Line H/T to avail S/D for replacement of Insulator string with polymer string where Corona Discharge observed during night patrolling. | LD 02/223 | LD 02/266
| 902058 | JABALPUR-ITARSI III 400kV | 2014-02-10 | 22:33 | 2014-02-11 | 07:36 | - |  |  | - |  |  | - |  |  | 0.37708 | 9 | 3 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1081 | LD 02/1100
| 902100 | JABALPUR-ITARSI III 400kV | 2014-02-18 | 23:25 | 2014-02-19 | 08:31 | - |  |  | - |  |  | - |  |  | 0.37917 | 9 | 6 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1963 | LD 02/1980
| 902126 | JABALPUR-ITARSI III 400kV | 2014-02-25 | 23:38 | 2014-02-26 | 07:27 | - |  |  | - |  |  | - |  |  | 0.32569 | 7 | 49 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/2775 | LD 02/2786
| 902141 | JABALPUR-ITARSI III 400kV | 2014-02-26 | 22:23 | 2014-02-27 | 07:34 | - |  |  | - |  |  | - |  |  | 0.38264 | 9 | 11 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/2923 | LD 02/2953
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 06:14 | 52 | 134
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 54.2333 |  |  |  |  | 234 | 2 | 0 | 0 | 672 | 468 | 314496 | 0 | 100%
16 | 902007 | JABALPUR-ITARSI IV 400kV | 2014-02-01 | 23:13 | 2014-02-02 | 07:16 | - |  |  | - |  |  | - |  |  | 0.33542 | 8 | 3 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/111 | LD 02/127
| 902022 | JABALPUR-ITARSI IV 400kV | 2014-02-04 | 08:49 | 2014-02-04 | 16:58 | - |  |  | - |  |  | - |  |  | 0.33958 | 8 | 9 | LCSD | Line H/T to avail S/D for replacement of Insulator string with polymer string where Corona Discharge observed during night patrolling. | LD 02/331 | LD 02/370
| 902037 | JABALPUR-ITARSI IV 400kV | 2014-02-07 | 07:57 | 2014-02-07 | 08:07 | 0.0069444 | 0 | 10 | - |  |  | - |  |  | - |  |  | OMST | H/T to avail S/D by Jabalpur end to take out L/R at JBP end for attending oil Leakage. | LD 02/635 | LD 02/637
| 902090 | JABALPUR-ITARSI IV 400kV | 2014-02-17 | 12:17 | 2014-02-17 | 12:23 | - |  |  | 0.0041667 | 0 | 6 | - |  |  | - |  |  | OMSU | H/T to avail outage to take Line reactor at Itarsi into service. | LD 02/1771 | LD 02/1772
| 902094 | JABALPUR-ITARSI IV 400kV | 2014-02-18 | 00:43 | 2014-02-18 | 10:09 | - |  |  | - |  |  | - |  |  | 0.39306 | 9 | 26 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1846 | LD 02/1878
|  | SUBTOTAL |  |  |  |  | 0.0069444 | 0 | 10 | 0.0041667 | 0 | 6 | 0 | 0 | 0 | 1899-12-31 01:38 | 25 | 38
|  | Element Availability= | [6 empty] | 0.16667 |  |  | 0.1 |  |  | 0 |  |  | 25.6333 |  |  |  |  | 234 | 2 | 0.16667 | 78 | 671.9 | 468 | 314449.2 | 0.00024805 | 99.98%
17 | 902005 | ITARSI-KHANDWA I 400kV | 2014-02-01 | 22:17 | 2014-02-03 | 07:32 | - |  |  | - |  |  | - |  |  | 1899-12-31 09:15 | 33 | 15 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/107 | LD 02/200
| 902057 | ITARSI-KHANDWA I 400kV | 2014-02-10 | 22:31 | 2014-02-11 | 07:20 | - |  |  | - |  |  | - |  |  | 0.36736 | 8 | 49 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1080 | LD 02/1099
| 902080 | ITARSI-KHANDWA I 400kV | 2014-02-15 | 18:08 | 2014-02-16 | 10:21 | - |  |  | - |  |  | - |  |  | 0.67569 | 16 | 13 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1597 | LD 02/1664
| 902093 | ITARSI-KHANDWA I 400kV | 2014-02-18 | 00:41 | 2014-02-18 | 10:06 | - |  |  | - |  |  | - |  |  | 0.39236 | 9 | 25 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1845 | LD 02/1884
| 902102 | ITARSI-KHANDWA I 400kV | 2014-02-18 | 23:29 | 2014-02-19 | 08:33 | - |  |  | - |  |  | - |  |  | 0.37778 | 9 | 4 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1962 | LD 02/1978
| 902128 | ITARSI-KHANDWA I 400kV | 2014-02-26 | 00:06 | 2014-02-27 | 08:07 | - |  |  | - |  |  | - |  |  | 1899-12-31 08:01 | 32 | 1 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/2777 | LD 02/2959
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-03 12:47 | 107 | 107
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 108.7833 |  |  |  |  | 196.64 | 2 | 0 | 0 | 672 | 393.28 | 264284.16 | 0 | 100%
18 |  | ITARSI-KHANDWA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 196.64 | 2 | 0 | 0 | 672 | 393.28 | 264284.16 | 0 | 100%
19 | 902011 | KHANDWA-DHULE I 400kV | 2014-02-02 | 11:17 | 2014-02-02 | 13:13 | - |  |  | - |  |  | - |  |  | 0.080556 | 1 | 56 | SCSD | Line H/T to avail OCC approved S/D to test newly retrofitted relays. | LD 02/151 | LD 02/155
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080556 | 1 | 56
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 1.9333 |  |  |  |  | 261.78 | 2 | 0 | 0 | 672 | 523.56 | 351832.32 | 0 | 100%
20 | 902035 | KHANDWA-DHULE II 400kV | 2014-02-06 | 17:46 | 2014-02-07 | 12:38 | 0.28611 | 6 | 52 | - |  |  | - |  |  | - |  |  | LHWT | A/T on R-ph to E/F, F/L - 147.5kM from Khandwa SS due to failure of R-ph inner V-string at Loc-768. The outage preriod from 19:00 hrs / 06.02.14 to 07:00 hrs / 07.02.14 may not be attributed to Powergrid due to poor visibility & rainy site condition. Fault jurisdiction comes under WRTS#1 portion. |  | LD 02/663
| 902036 | KHANDWA-DHULE II 400kV | 2014-02-06 | 17:46 | 2014-02-07 | 12:38 | - |  |  | - |  |  | 0.5 | 12 | 0 | - |  |  | LNCC | A/T on R-ph to E/F, F/L - 147.5kM from Khandwa SS due to failure of R-ph inner V-string at Loc-768. The outage period from 19:00 hrs / 06.02.14 to 07:00 hrs / 07.02.14 may not be attributed to Powergrid due to poor visibility & rainy site condition. Fault jurisdiction comes under WRTS#1 portion. |  | LD 02/663
|  | SUBTOTAL |  |  |  |  | 0.28611 | 6 | 52 | 0 | 0 | 0 | 0.5 | 12 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 6.8667 |  |  | 0 |  |  | 12 |  |  | 0 |  |  |  |  | 261.78 | 2 | 6.8667 | 3595.112 | 660 | 523.56 | 345549.6 | 0.010404 | 98.96%
21 |  | GANDHAR-SUGEN 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 57 | 2 | 0 | 0 | 672 | 114 | 76608 | 0 | 100%
22 | 902049 | SUGEN-VAPI 400kV | 2014-02-08 | 12:29 | 2014-02-08 | 13:24 | - |  |  | 0.038194 |  |  | - |  |  | - |  |  | OMSU | Line H/T for calibration of PMU installed at Vapi on WRLDC instruction | LD 02/799 | LD 02/802
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.038194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 110 | 2 | 0 | 0 | 672 | 220 | 147840 | 0 | 100%
23 | 902062 | GANDHAR - GTEC 400kV | 2014-02-11 | 11:34 | 2014-02-11 | 21:29 | - |  |  | - |  |  | - |  |  | 0.41319 | 9 | 55 | OSPD | Line H/T to avail S/D by NTPC Gandhar for maintenance work. | LD 02/1135 | LD 02/1183
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41319 | 9 | 55
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.9167 |  |  |  |  | 13 | 2 | 0 | 0 | 672 | 26 | 17472 | 0 | 100%
24 |  | GANDHAR-HALDARWA I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 672 | 13 | 8736 | 0 | 100%
25 |  | GANDHAR-HALDARWA II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 13 | 1 | 0 | 0 | 672 | 13 | 8736 | 0 | 100%
26 | 902061 | KAWAS - NAVSARI (GIS) I 220kV | 2014-02-11 | 09:59 | 2014-02-11 | 18:57 | - |  |  | - |  |  | - |  |  | 0.37361 | 8 | 58 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1124 | LD 02/1170
| 902065 | KAWAS - NAVSARI (GIS) I 220kV | 2014-02-12 | 09:45 | 2014-02-12 | 15:22 | - |  |  | - |  |  | - |  |  | 0.23403 | 5 | 37 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1224 | LD 02/1258
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37361 | 8 | 58
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.9667 |  |  |  |  | 58.149 | 1 | 0 | 0 | 672 | 58.149 | 39076.128 | 0 | 100%
27 | 902069 | KAWAS - NAVSARI (GIS) II 220kV | 2014-02-13 | 10:55 | 2014-02-13 | 19:12 | - |  |  | - |  |  | - |  |  | 0.34514 | 8 | 17 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1350 | LD 02/1400
| 902071 | KAWAS - NAVSARI (GIS) II 220kV | 2014-02-14 | 10:41 | 2014-02-14 | 17:14 | - |  |  | - |  |  | - |  |  | 0.27292 | 6 | 33 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1452 | LD 02/1484
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34514 | 8 | 17
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.2833 |  |  |  |  | 58.149 | 1 | 0 | 0 | 672 | 58.149 | 39076.128 | 0 | 100%
28 | 902079 | NAVSARI -NAVSARI I 220kV | 2014-02-15 | 09:18 | 2014-02-15 | 18:54 | - |  |  | - |  |  | - |  |  | 0.4 | 9 | 36 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1542 | LD 02/1602
| 902082 | NAVSARI -NAVSARI I 220kV | 2014-02-16 | 09:00 | 2014-02-16 | 15:13 | - |  |  | - |  |  | - |  |  | 0.25903 | 6 | 13 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1650 | LD 02/1683
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 9 | 36
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.6 |  |  |  |  | 31.334 | 1 | 0 | 0 | 672 | 31.334 | 21056.448 | 0 | 100%
29 | 902089 | NAVSARI (PG GIS)-NAVSARI II 220kV | 2014-02-17 | 10:00 | 2014-02-17 | 17:33 | - |  |  | - |  |  | - |  |  | 0.31458 | 7 | 33 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1753 | LD 02/1800
| 902098 | NAVSARI (PG GIS)-NAVSARI II 220kV | 2014-02-18 | 09:46 | 2014-02-18 | 16:07 | - |  |  | - |  |  | - |  |  | 0.26458 | 6 | 21 | LCSD | Line H/T to avail S/D for replacement of insulator strings by polymer insulators. | LD 02/1883 | LD 02/1913
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31458 | 7 | 33
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 7.55 |  |  |  |  | 31.334 | 1 | 0 | 0 | 672 | 31.334 | 21056.448 | 0 | 100%
30 | 902134 | KAWAS-VAV I 220kV | 2014-02-26 | 11:41 | 2014-02-26 | 12:39 | - |  |  | - |  |  | - |  |  | 0.040278 | 0 | 58 | LPRD | Line H/T for power regulation on WRLDC Instruction | LD 02/2834 | LD 02/2840
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040278 | 0 | 58
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0.96667 |  |  |  |  | 37 | 1 | 0 | 0 | 672 | 37 | 24864 | 0 | 100%
31 | 902135 | KAWAS-VAV II 220kV | 2014-02-26 | 11:53 | 2014-02-26 | 21:02 | - |  |  | - |  |  | - |  |  | 0.38125 | 9 | 9 | LPRD | Line H/T for power regulation on WRLDC Instruction | LD 02/2836 | LD 02/2910
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38125 | 9 | 9
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.15 |  |  |  |  | 37 | 1 | 0 | 0 | 672 | 37 | 24864 | 0 | 100%
32 | 902104 | KAWAS-HALDARWA I 220kV | 2014-02-19 | 09:26 | 2014-02-19 | 09:36 | 0.0069444 | 0 | 10 | - |  |  | - |  |  | - |  |  | LEFT | Line A/T on B-ph to E/F, F/L - 77kms fro Haldarwa end & 6kms from Kawas end.
| 902105 | KAWAS-HALDARWA I 220kV | 2014-02-19 | 09:36 | 2014-02-19 | 11:23 | - |  |  | 0.074306 | 1 | 47 | - |  |  | - |  |  | OMSU | After Tripping Test charging code delayed by WRLDC. |  | LD 02/12009
|  | SUBTOTAL |  |  |  |  | 0.0069444 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.16667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 81 | 1 | 0.16667 | 13.5 | 672 | 81 | 54432 | 0.00024802 | 99.98%
33 |  | KAWAS-HALDARWA II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 81 | 1 | 0 | 0 | 672 | 81 | 54432 | 0 | 100%
34 | 902097 | KAKRAPAR-HALDARWA II 220kV | 2014-02-18 | 08:57 | 2014-02-18 | 19:38 | - |  |  | - |  |  | - |  |  | 0.44514 | 10 | 41 | OSPD | Line H/T to avail S/D by NPCIL. | LD 02/1863 | LD 01/601
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44514 | 10 | 41
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.6833 |  |  |  |  | 74 | 1 | 0 | 0 | 672 | 74 | 49728 | 0 | 100%
35 |  | KAKRAPAR-HALDARWA II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 74 | 1 | 0 | 0 | 672 | 74 | 49728 | 0 | 100%
36 | 902108 | KAKRAPAR-VAV I 220kV | 2014-02-20 | 08:15 | 2014-02-20 | 21:07 | - |  |  | - |  |  | - |  |  | 0.53611 | 12 | 52 | OSPD | Line H/T to avail S/D by GETCO. |  | LD 02/2190
| 902131 | KAKRAPAR-VAV I 220kV | 2014-02-26 | 09:09 | 2014-02-26 | 20:37 | - |  |  | - |  |  | - |  |  | 0.47778 | 11 | 28 | OSPD | Line H/T to avail S/D by GETCO | LD 02/2799
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 00:20 | 23 | 80
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 24.3333 |  |  |  |  | 43 | 1 | 0 | 0 | 672 | 43 | 28896 | 0 | 100%
37 | 902103 | KAKRAPAR-VAV II 220kV | 2014-02-19 | 08:39 | 2014-02-19 | 20:27 | - |  |  | - |  |  | - |  |  | 0.49167 | 11 | 48 | OSPD | Line H/T to avail S/D by NPCIL. | LD 02/1983 | LD 02/2079
| 902136 | KAKRAPAR-VAV II 220kV | 2014-02-26 | 12:13 | 2014-02-26 | 20:38 | - |  |  | - |  |  | - |  |  | 0.35069 | 8 | 25 | OSPD | line H/T to avail OCC approved S/D by GETCO for line crossing work | LD 02/2839
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84236 | 19 | 73
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 20.2167 |  |  |  |  | 43 | 1 | 0 | 0 | 672 | 43 | 28896 | 0 | 100%
38 | 902083 | KAKRAPAR-VAPI I 220kV | 2014-02-16 | 08:26 | 2014-02-16 | 22:09 | - |  |  | - |  |  | - |  |  | 0.57153 | 13 | 43 | OSPD | Line H/T to avail S/D by NPCIL. | LD 02/1648 | LD 02/1713
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57153 | 13 | 43
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 13.7167 |  |  |  |  | 117 | 1 | 0 | 0 | 672 | 117 | 78624 | 0 | 100%
39 | 902118 | KAKRAPAR-VAPI II 220kV | 2014-02-23 | 08:04 | 2014-02-24 | 00:18 | - |  |  | - |  |  | - |  |  | 0.67639 | 16 | 14 | OSPD | Line H/t to avail OCC Approved S/D by NPCIL. | LD 02/2454 | LD 02/2537
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67639 | 16 | 14
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 16.2333 |  |  |  |  | 117 | 1 | 0 | 0 | 672 | 117 | 78624 | 0 | 100%
40 |  | VINDHYACHAL-SATNA I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 672 | 534 | 358848 | 0 | 100%
41 |  | VINDHYACHAL-SATNA II 400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 267 | 2 | 0 | 0 | 672 | 534 | 358848 | 0 | 100%
42 | 902148 | VINDHYACHAL-SATNA III 400kV | 2014-02-27 | 10:28 | 2014-02-27 | 21:38 | - |  |  | - |  |  | 0.46528 | 11 | 10 | - |  |  | LNCC | A/T on Y-ph to E/F (F/L-23km from satna) due to flashover of insulator string (top phase at Loc-715 during heavy lightening & thunder storm in that area. Restoration was delayed due to persisting bad weather. |  | LD 02/3063
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.46528 | 11 | 10 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 11.1667 |  |  | 0 |  |  |  |  | 258.31 | 2 | 0 | 0 | 660.8333 | 516.62 | 341399.7167 | 0 | 100%
43 |  | VINDHYACHAL-NIGRIE 400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 100.32 | 2 | 0 | 0 | 672 | 200.64 | 134830.08 | 0 | 100%
44 |  | Satna -Nigrie 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 161.11 | 2 | 0 | 0 | 672 | 322.22 | 216531.84 | 0 | 100%
45 | 902008 | SATNA-BINA(PG) I 400kV | 2014-02-02 | 01:19 | 2014-02-03 | 10:19 | - |  |  | - |  |  | - |  |  | 1899-12-31 09:00 | 33 | 0 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/115 | LD 02/206
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 09:00 | 33 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 33 |  |  |  |  | 276 | 2 | 0 | 0 | 672 | 552 | 370944 | 0 | 100%
46 |  | SATNA-BINA(PG) II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 276 | 2 | 0 | 0 | 672 | 552 | 370944 | 0 | 100%
47 |  | BINA(PG)-BINA(MPEB) I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 672 | 1.484 | 997.248 | 0 | 100%
48 |  | BINA(PG)-BINA(MPEB) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.742 | 2 | 0 | 0 | 672 | 1.484 | 997.248 | 0 | 100%
49 | 902076 | GWALIOR-BINA I 765kV | 2014-02-14 | 20:11 | 2014-02-14 | 20:21 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V protection at Gwalior end.
| 902077 | GWALIOR-BINA I 765kV | 2014-02-14 | 20:21 | 2014-02-15 | 08:24 | - |  |  | - |  |  | - |  |  | 0.50208 | 12 | 3 | LVRD | After Tripping on over voltage, line kept out for volatge regulation on WRLDC Instruction. |  | LD 02/1543 LD 02/230
| 902085 | GWALIOR-BINA I 765kV | 2014-02-16 | 23:58 | 2014-02-17 | 00:08 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V protection at Gwalior end.
| 902086 | GWALIOR-BINA I 765kV | 2014-02-17 | 00:08 | 2014-02-17 | 09:22 | - |  |  | - |  |  | - |  |  | 0.38472 | 9 | 14 | LVRD | After Tripping on over voltage, line kept out for volatge regulation on WRLDC Instruction. |  | LD 02/1737 LD 02/260
| 902164 | GWALIOR-BINA I 765kV | 2014-02-28 | 21:38 | 2014-02-28 | 22:13 | - |  |  | - |  |  | 0.024306 | 0 | 35 | - |  |  | GOVC | Line A/T on operation of O/V STG-I protection at GWL end. |  | WR 02/3202 NLD 02/436
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.038194 | 0 | 55 | 0.88681 | 21 | 17
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.91667 |  |  | 21.2833 |  |  |  |  | 234.931 | 4 | 0 | 0 | 671.0833 | 939.724 | 630633.1143 | 0 | 100%
50 | 901248 | SATNA-BINA(PG) IV 400kV | 2014-01-31 | 09:24 | 2014-02-01 | 20:11 | - |  |  | - |  |  | - |  |  | 0.84097 | 20 | 11 | LCSD | Line H/T to avail OCC Approved S/D for stringing work of 765kV Jabalpur Pooling - Bina S/C line. | LD 01/3377 | LD 02/91
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84097 | 20 | 11
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 20.1833 |  |  |  |  | 272.586 | 2 | 0 | 0 | 672 | 545.172 | 366355.584 | 0 | 100%
51 | 901247 | SATNA-BINA(PG) III 400kV | 2014-01-31 | 09:23 | 2014-02-01 | 20:51 | - |  |  | - |  |  | - |  |  | 20:51 | 20 | 51 | LCSD | Line H/T to avail OCC Approved S/D for stringing work of 765kV Jabalpur Pooling - Bina S/C line. | LD 01/3331 | LD 02/95
| 902081 | SATNA-BINA(PG) III 400kV | 2014-02-16 | 02:16 | 2014-02-16 | 10:05 | - |  |  | - |  |  | - |  |  | 0.32569 | 7 | 49 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1626 | LD 02/1660
| 902101 | SATNA-BINA III 400 KV | 2014-02-18 | 23:25 | 2014-02-19 | 08:39 | - |  |  | - |  |  | - |  |  | 0.38472 | 9 | 14 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1964 | LD 02/1979
| 902127 | SATNA-BINA(PG) III 400kV | 2014-02-25 | 23:40 | 2014-02-26 | 06:56 | - |  |  | - |  |  | - |  |  | 0.30278 | 7 | 16 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/2776 | LD 02/2785
| 902142 | SATNA-BINA(PG) III 400kV | 2014-02-26 | 22:52 | 2014-02-27 | 08:14 | - |  |  | - |  |  | - |  |  | 0.39028 | 9 | 22 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/2924 | LD 02/2958
| 902146 | SATNA-BINA(PG) III 400kV | 2014-02-27 | 10:07 | 2014-02-27 | 18:28 | - |  |  | - |  |  | 0.34792 | 8 | 21 | - |  |  | LNCC | A/T on R-ph to E/F (F/L-35.87km from Satna) due to flashover of insulator string at Location no. 97 during heavy lightening & thunder storm in that area. Restoration was delayed due to persisting bad weather. |  | LD 02/3040
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.34792 | 8 | 21 | 1899-12-31 09:41 | 52 | 152
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 8.35 |  |  | 54.5333 |  |  |  |  | 272.586 | 2 | 0 | 0 | 663.65 | 545.172 | 361803.3978 | 0 | 100%
52 | 902001 | BINA-SHUJALPUR I 400kV | 2014-02-01 | 01:27 | 2014-02-01 | 06:13 | - |  |  | - |  |  | - |  |  | 0.19861 | 4 | 46 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/05 | LD 02/09
| 902006 | BINA-SHUJALPUR I 400kV | 2014-02-01 | 22:18 | 2014-02-02 | 07:30 | - |  |  | - |  |  | - |  |  | 0.38333 | 9 | 12 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/106 | LD 02/126
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58194 | 13 | 58
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 13.9667 |  |  |  |  | 199.936 | 2 | 0 | 0 | 672 | 399.872 | 268713.984 | 0 | 100%
53 | 902016 | BINA-SHUJALPUR II 400kV | 2014-02-02 | 23:05 | 2014-02-03 | 07:50 | - |  |  | - |  |  | - |  |  | 0.36458 | 8 | 45 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/184 | LD 02/199
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36458 | 8 | 45
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.75 |  |  |  |  | 199.936 | 2 | 0 | 0 | 672 | 399.872 | 268713.984 | 0 | 100%
54 |  | SHUJALPUR-NAGDA I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 152.229 | 2 | 0 | 0 | 672 | 304.458 | 204595.776 | 0 | 100%
55 |  | SHUJALPUR-NAGDA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 152.229 | 2 | 0 | 0 | 672 | 304.458 | 204595.776 | 0 | 100%
56 | 902068 | NAGDA-DEHGAM II 400kV | 2014-02-13 | 09:56 | 2014-02-13 | 20:25 | - |  |  | - |  |  | - |  |  | 0.43681 | 10 | 29 | SCSD | Line H/T to avail OCC approved S/D for commissioning of CSD at Dehgam. | LD 02/1342 | LD 02/1404
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43681 | 10 | 29
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.4833 |  |  |  |  | 331.442 | 2 | 0 | 0 | 672 | 662.884 | 445458.048 | 0 | 100%
57 | 902055 | NAGDA-DEHGAM I 400KV | 2014-02-10 | 11:48 | 2014-02-11 | 00:45 | - |  |  | - |  |  | - |  |  | 0.53958 | 12 | 57 | SCSD | Line H/T to avail OCC approved S/D for commissioning of CSD relay at Dehgam end. Work copleted at 00:45 Hrs/11.02.2014. | LD 02/1026
| 902059 | NAGDA-DEHGAM I 400KV | 2014-02-11 | 00:45 | 2014-02-11 | 09:20 | - |  |  | - |  |  | - |  |  | 0.35764 | 8 | 35 | LVRD | After completion of commissioning work at 00:45 Hrs/11.02.2014, Line kept out on voltage regulation as per instruction of WRLDC. |  | LD 02/1115
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89722 | 20 | 92
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 21.5333 |  |  |  |  | 331.442 | 2 | 0 | 0 | 672 | 662.884 | 445458.048 | 0 | 100%
58 | 902124 | SEONI-KHANDWA I 400kV | 2014-02-25 | 21:49 | 2014-02-25 | 22:52 | 0.04375 | 1 | 3 | - |  |  | - |  |  | - |  |  | LEFT | Line A/T on R-ph to E/F , F/L 67.1kms from Khandwa F/C- 5.8kAmp.L |  | LD 02/2772
|  | SUBTOTAL |  |  |  |  | 0.04375 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.05 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 351.729 | 4 | 1.05 | 1477.2618 | 672 | 1406.916 | 945447.552 | 0.0015625 | 99.84%
59 |  | SEONI-KHANDWA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 351.729 | 4 | 0 | 0 | 672 | 1406.916 | 945447.552 | 0 | 100%
60 | 902014 | KHANDWA-RAJGARH II 400kV | 2014-02-02 | 18:16 | 2014-02-05 | 10:54 | - |  |  | - |  |  | - |  |  | 1900-01-01 16:38 | 64 | 38 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/165 | LD 02/456
| 902044 | KHANDWA-RAJGARH II 400kV | 2014-02-07 | 21:38 | 2014-02-08 | 09:34 | - |  |  | - |  |  | - |  |  | 0.49722 | 11 | 56 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/735 | LD 02/773
| 902075 | KHANDWA-RAJGARH II 400kV | 2014-02-14 | 17:40 | 2014-02-17 | 09:10 | - |  |  | - |  |  | - |  |  | 1900-01-01 15:30 | 63 | 30 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1489 | LD 02/1744
| 902125 | KHANDWA-RAJGARH II 400kV | 2014-02-25 | 22:15 | 2014-02-26 | 07:09 | - |  |  | - |  |  | - |  |  | 0.37083 | 8 | 54 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/2770 | LD 02/2787
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-05 04:58 | 146 | 178
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 148.9667 |  |  |  |  | 220.588 | 2 | 0 | 0 | 672 | 441.176 | 296470.272 | 0 | 100%
61 | 901229 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2014-01-29 | 22:04 | 2014-02-02 | 10:56 | - |  |  | - |  |  | - |  |  | 1899-12-31 10:56 | 34 | 56 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 01/3201 | LD 02/149
| 902009 | SARDAR SAROVAR-RAJGARH I 400kV (LILO) | 2014-02-02 | 10:57 | 2014-02-02 | 10:57 | - |  |  | 0 | 0 | 0 | - |  |  | - |  |  | OMSU | Line A/R successfully on Y ph to E/F, F/L:45km from Rajgarh end ( Beyond Powergrid jurisdiction ).
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 10:56 | 34 | 56
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 34.9333 |  |  |  |  | 4.01 | 2 | 0 | 0 | 672 | 8.02 | 5389.44 | 0 | 100%
62 | 902012 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2014-02-02 | 18:02 | 2014-02-02 | 18:12 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V protection at Rajgarh end.
| 902013 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2014-02-02 | 18:12 | 2014-02-08 | 09:52 | - |  |  | - |  |  | - |  |  | 1900-01-04 15:40 | 135 | 40 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/166 | LD 02/782
| 902050 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2014-02-08 | 16:51 | 2014-02-08 | 16:51 | - |  |  | 0 | 0 | 0 | - |  |  | - |  |  | OMSU | Line A/R successfully at both ends on R-ph to E/F, F/L - 23kms from Rajgarh. Fault lies beyond the jourisdiction of POWERGRID.
| 902066 | SARDAR SAROVAR-RAJGARH II 400kV (LILO) | 2014-02-12 | 13:30 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-15 10:30 | 394 | 30 | OSFD | Line H/T to avail Emergency S/D by MPPTCL. | LD 02/1247
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069444 | 0 | 10 | 1900-01-21 02:10 | 529 | 70
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 530.1667 |  |  |  |  | 4.01 | 2 | 0 | 0 | 671.8333 | 8.02 | 5388.1033 | 0 | 100%
63 | 901242 | RAJGARH-NAGDA I 400kV (LILO) | 2014-01-30 | 20:31 | 2014-02-04 | 12:46 | - |  |  | - |  |  | - |  |  | 1900-01-02 12:46 | 84 | 46 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 01/3331 | LD 02/356
| 902123 | RAJGARH-NAGDA I 400kV (LILO) | 2014-02-25 | 12:42 | 2014-02-27 | 16:11 | - |  |  | 1900-01-01 03:29 | 51 | 29 | - |  |  | - |  |  | OMSU | Line A/T on Y & B Ph-ph fault, F/L - 49kms from Rajgarh & 47.9kms from Nagda. Fault lies under the jourisdiction of MPPTCl. |  | LD 02/3020
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 1900-01-01 03:29 | 51 | 29 | 0 | 0 | 0 | 1900-01-02 12:46 | 84 | 46
|  | Element Availability= | [6 empty] | 0 |  |  | 51.4833 |  |  | 0 |  |  | 84.7667 |  |  |  |  | 4.12 | 2 | 0 | 0 | 620.5167 | 8.24 | 5113.0573 | 0 | 100%
64 | 902026 | RAJGARH-NAGDA II 400kV (LILO) | 2014-02-04 | 13:18 | 2014-02-12 | 17:47 | - |  |  | - |  |  | - |  |  | 1900-01-07 04:29 | 196 | 29 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/358 | LD 02/1276
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-07 04:29 | 196 | 29
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 196.4833 |  |  |  |  | 4.12 | 2 | 0 | 0 | 672 | 8.24 | 5537.28 | 0 | 100%
65 | 901251 | KHANDWA-RAJGARH I 400kV | 2014-01-31 | 18:06 | 2014-02-02 | 10:39 | - |  |  | - |  |  | - |  |  | 1899-12-31 06:39 | 30 | 39 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 01/3424 | LD 02/148
| 902030 | KHANDWA-RAJGARH I 400kV | 2014-02-05 | 21:29 | 2014-02-07 | 07:22 | - |  |  | - |  |  | - |  |  | 1899-12-31 09:53 | 33 | 53 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/513 | LD 02/622
| 902051 | KHANDWA-RAJGARH I 400kV | 2014-02-08 | 18:06 | 2014-02-11 | 10:44 | - |  |  | - |  |  | - |  |  | 1900-01-01 16:38 | 64 | 38 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/833 | LD 02/1128
| 902092 | KHANDWA-RAJGARH I 400kV | 2014-02-17 | 20:17 |  |  | - |  |  | - |  |  | - |  |  | 1900-01-10 03:43 | 267 | 43 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1826
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-15 12:53 | 394 | 173
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 396.8833 |  |  |  |  | 220.588 | 2 | 0 | 0 | 672 | 441.176 | 296470.272 | 0 | 100%
66 | 902019 | VAPI-MAGARWADA I 220kV | 2014-02-03 | 09:44 | 2014-02-03 | 15:05 | 0.22292 | 5 | 21 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC approved S/D by Powergrid to attend Hot spot and for AMP. | LD 02/218 | LD 02/254
|  | SUBTOTAL |  |  |  |  | 0.22292 | 5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 5.35 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 5.35 | 137.5485 | 672 | 25.71 | 17277.12 | 0.0079613 | 99.2%
67 | 902023 | VAPI-MAGARWADA II 220kV | 2014-02-04 | 09:27 | 2014-02-04 | 12:48 | 0.13958 | 3 | 21 | - |  |  | - |  |  | - |  |  | OSPT | Line H/T to avail OCC Approved S/D for AMP work. | LD 02/330 | LD 02/355
|  | SUBTOTAL |  |  |  |  | 0.13958 | 3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.35 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25.71 | 1 | 3.35 | 86.1285 | 672 | 25.71 | 17277.12 | 0.0049851 | 99.5%
68 |  | VAPI-KHARADPARA I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 672 | 29.66 | 19931.52 | 0 | 100%
69 |  | VAPI-KHARADPARA II 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 29.66 | 1 | 0 | 0 | 672 | 29.66 | 19931.52 | 0 | 100%
70 | 902072 | GWALIOR-BINA II 765kV | 2014-02-14 | 10:43 | 2014-02-14 | 10:55 | 0.0083333 | 0 | 12 | - |  |  | - |  |  | - |  |  | OMST | H/T to take out L/R at Bina SS for attending oil Leakage. | LD 02/1455 LD 02/212
| 902110 | GWALIOR-BINA II 765kV | 2014-02-21 | 10:46 | 2014-02-21 | 19:47 | - |  |  | - |  |  | - |  |  | 0.37569 | 9 | 1 | SCSD | OCC approved S/D availed for construction work to facilitate bay extension work at Gwalior end. | LD 02/2245 LD 02/322
| 902160 | GWALIOR-BINA II 765kV | 2014-02-28 | 16:45 | 2014-02-28 | 17:15 | 0.020833 | 0 | 30 | - |  |  | - |  |  | - |  |  | SRET | A/T due to operation of Reactor REF protection at Bina.
|  | SUBTOTAL |  |  |  |  | 0.020833 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.7 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 233.652 | 4 | 0.7 | 654.2256 | 672 | 934.608 | 628056.576 | 0.0010417 | 99.9%
71 |  | SEONI-BINA I 765kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 292.45 | 4 | 0 | 0 | 672 | 1169.8 | 786105.6 | 0 | 100%
72 | 901239 | DAMOH-BHOPAL I 400KV | 2014-01-30 | 12:44 | 2014-02-01 | 16:37 | - |  |  | - |  |  | - |  |  | 0.69236 | 16 | 37 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 01/3277 | LD 02/637
| 902154 | DAMOH-BHOPAL I 400KV | 2014-02-28 | 01:35 | 2014-02-28 | 01:45 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V STG-I protection at Damoh S/S
| 902156 | DAMOH-BHOPAL I 400KV | 2014-02-28 | 01:45 | 2014-02-28 | 07:51 | - |  |  | - |  |  | - |  |  | 0.25417 | 6 | 6 | LVRD | Line kept out for voltage regulation on WRLDC Instruction. |  | LD 02/3091
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069444 | 0 | 10 | 0.94653 | 22 | 43
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 22.7167 |  |  |  |  | 241.471 | 2 | 0 | 0 | 671.8333 | 482.942 | 324456.5337 | 0 | 100%
73 |  | DAMOH-BHOPAL II 400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 213.8 | 2 | 0 | 0 | 672 | 427.6 | 287347.2 | 0 | 100%
74 |  | VAPI-KHADOLI I 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.549 | 1 | 0 | 0 | 672 | 28.549 | 19184.928 | 0 | 100%
75 |  | VAPI-SAYALI 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 18.3 | 1 | 0 | 0 | 672 | 18.3 | 12297.6 | 0 | 100%
76 |  | SAYALI-KHADOLI 220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 12.235 | 1 | 0 | 0 | 672 | 12.235 | 8221.92 | 0 | 100%
77 | 901240 | DAMOH-BIRSINGHPUR I 400kV | 2014-01-30 | 13:56 | 2014-02-01 | 06:45 | - |  |  | - |  |  | - |  |  | 0.27986 | 6 | 43 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 01/3281 | LD 02/10
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27986 | 6 | 43
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 6.7167 |  |  |  |  | 228.474 | 2 | 0 | 0 | 672 | 456.948 | 307069.056 | 0 | 100%
78 | 902143 | DAMOH-BIRSINGHPUR II 400kV | 2014-02-27 | 07:30 | 2014-02-27 | 07:30 | 0 |  |  | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on Y-ph to E/F, F/L 122.2kms from Damoh. F/C - 2.1kamp
| 902153 | DAMOH-BIRSINGHPUR II 400kV | 2014-02-28 | 01:33 | 2014-02-28 | 01:43 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | GOVC | Line A/T on operation of O/V STG-I protection at Damoh S/S
| 902155 | DAMOH-BIRSINGHPUR II 400kV | 2014-02-28 | 01:43 | 2014-02-28 | 06:10 | - |  |  | - |  |  | - |  |  | 0.18542 | 4 | 27 | LVRD | Line kept out for voltage regulation on WRLDC Instruction. |  | LD 02/3090
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0069444 | 0 | 10 | 0.18542 | 4 | 27
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0.16667 |  |  | 4.45 |  |  |  |  | 228.474 | 2 | 0 | 0 | 671.8333 | 456.948 | 306992.898 | 0 | 100%
79 |  | DEHGAM PIRANA I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 0 | 0 | 672 | 93.34 | 62724.48 | 0 | 100%
80 |  | DEHGAM PIRANA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 46.67 | 2 | 0 | 0 | 672 | 93.34 | 62724.48 | 0 | 100%
81 |  | MUNDRA-BHACHAU I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 99.468 | 3 | 0 | 0 | 672 | 298.404 | 200527.488 | 0 | 100%
82 | 902046 | MUNDRA-BHACHAU II 400kV | 2014-02-08 | 08:47 | 2014-02-08 | 09:30 | - |  |  | - |  |  | - |  |  | 0.029861 | 0 | 43 | OSPD | Line H/T to avail OCC Approved S/D by CGPL for maintenance work at CGPL end. | LD 02/764 | LD 02/778
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029861 | 0 | 43
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0.71667 |  |  |  |  | 99.468 | 3 | 0 | 0 | 672 | 298.404 | 200527.488 | 0 | 100%
83 | 902074 | BHACHAU-RANCHODPURA I 400kV | 2014-02-14 | 12:34 | 2014-02-14 | 12:36 | 0.0013889 | 0 | 2 | - |  |  | - |  |  | - |  |  | OMST | H/T to take out L/R at R'pura (GETCO) SS due to DGA viuolation in R-ph bushing. | LD 02/1466 | LD 02/1467
|  | SUBTOTAL |  |  |  |  | 0.0013889 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.033333 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0.033333 | 28.2856 | 672 | 848.568 | 570237.696 | 4.9603e-05 | 100%
84 |  | BHACHAU-RANCHODPURA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 282.856 | 3 | 0 | 0 | 672 | 848.568 | 570237.696 | 0 | 100%
85 | 902020 | MUNDRA-LIMBDI I 400kV | 2014-02-03 | 12:34 | 2014-02-03 | 19:26 | - |  |  | - |  |  | - |  |  | 0.28611 | 6 | 52 | OSPD | Line H/T to avail OCC approved S/D by CGPL for AMP. | LD 02/241 | LD 02/282
| 902130 | MUNDRA-LIMBDI I 400kV | 2014-02-26 | 07:19 | 2014-02-27 | 13:50 | 0.75069 | 18 | 1 | - |  |  | - |  |  | - |  |  | LHWT | A/T on R&Y Ph. to ph fault, F/L - Mundra- 235KM & Limdi-98.6KM. Top Phase Conductor Snapped between location 592-593. Restoration was delayed due to poor visibility. Outage from 18:30 hrs / 26.02.14 to 07:00 hrs / 27.02.14 may not be attributed to POWERGRID. |  | LD 02/3004
| 902131 | MUNDRA-LIMBDI I 400kV | 2014-02-26 | 07:19 | 2014-02-27 | 13:50 | - |  |  | - |  |  | 0.52083 | 12 | 30 | - |  |  | LNCC | A/T on R&Y Ph. to ph fault, F/L - Mundra- 235KM & Limdi-98.6KM. Top Phase Conductor Snapped between location 592-593. Restoration was delayed due to poor visibility. Outage from 18:30 hrs / 26.02.14 to 07:00 hrs / 27.02.14 may not be attributed to POWERGRID. |  | LD 02/3004
|  | SUBTOTAL |  |  |  |  | 0.75069 | 18 | 1 | 0 | 0 | 0 | 0.52083 | 12 | 30 | 0.28611 | 6 | 52
|  | Element Availability= | [6 empty] | 18.0167 |  |  | 0 |  |  | 12.5 |  |  | 6.8667 |  |  |  |  | 314.053 | 3 | 18.0167 | 16974.5647 | 659.5 | 942.159 | 621353.8605 | 0.027319 | 97.27%
86 | 902024 | MUNDRA-LIMBDI II 400kV | 2014-02-04 | 09:34 | 2014-02-04 | 19:03 | - |  |  | - |  |  | - |  |  | 0.39514 | 9 | 29 | OSPD | Line H/T to avail OCC approved S/D by CGPL for AMP. | LD 02/333 | LD 02/382
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39514 | 9 | 29
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.4833 |  |  |  |  | 314.053 | 3 | 0 | 0 | 672 | 942.159 | 633130.848 | 0 | 100%
87 | 902039 | SATNA-BINA(PG ) I 765kV | 2014-02-07 | 08:23 | 2014-02-08 | 19:00 | - |  |  | - |  |  | - |  |  | 1899-12-31 10:37 | 34 | 37 | LCSD | H/T to avail OCC S/D by M/s Starlite (JTCL) to facilitate Line crossing work of 765kV Jabalpur Pooling - Bina # 3 Line. PTW returned by M/S JTCL by 18:45hrs/08.02.14. | LD 02/527 LD 02/109
| 902052 | SATNA-BINA(PG ) I 765kV | 2014-02-08 | 18:45 | 2014-02-09 | 17:16 | - |  |  | - |  |  | - |  |  | 0.93819 | 22 | 31 | LVRD | After Completion of Stringing work by M/S JTCl line kept out for volatge regulation on WRLDC Instruction. |  | LD 02/914
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-01 09:08 | 56 | 68
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 57.1333 |  |  |  |  | 274.164 | 4 | 0 | 0 | 672 | 1096.656 | 736952.832 | 0 | 100%
88 | 902027 | SATNA-BINA (PG) II 765kV | 2014-02-04 | 19:43 | 2014-02-05 | 00:43 | 0.20833 | 5 | 0 | - |  |  | - |  |  | - |  |  | OSFT | Line H/T to avail Emergency S/D for attending hot spot in B-ph wave trap at Satna. | LD 02/388 NLD 02/64 | LD 02/407 NLD 02/70
|  | SUBTOTAL |  |  |  |  | 0.20833 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 5 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 275.635 | 4 | 5 | 5512.7 | 672 | 1102.54 | 740906.88 | 0.0074405 | 99.26%
89 | 902133 | BINA-INDORE 765kV | 2014-02-26 | 11:40 | 2014-02-26 | 11:40 | 0 | 0 | 0 | - |  |  | - |  |  | - |  |  | LART | Line A/R successfully at both ends on R-ph to E/F, F/L - 27.6kms
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 311.81 | 4 | 0 | 0 | 672 | 1247.24 | 838145.28 | 0 | 100%
90 | 902032 | GANDHAR-NAVSARI (PG GIS) II 400kV | 2014-02-06 | 10:26 | 2014-02-07 | 19:18 | - |  |  | - |  |  | - |  |  | 1899-12-31 08:52 | 32 | 52 | OSPD | Line H/T to avail OCC Approved S/D by NTPC Gandhar for maintenance work. | LD 02/537 | LD 02/712
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 08:52 | 32 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 32.8667 |  |  |  |  | 102.152 | 2 | 0 | 0 | 672 | 204.304 | 137292.288 | 0 | 100%
91 | 902025 | GANDHAR-NAVSARI (PG GIS) I 400kV | 2014-02-04 | 10:05 | 2014-02-05 | 19:58 | - |  |  | - |  |  | - |  |  | 1899-12-31 09:53 | 33 | 53 | OSPD | Line H/T to avail OCC Approved S/D by NTPC Gandhar for maintenance work. | LD 02/335 | LD 02/505
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 09:53 | 33 | 53
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 33.8833 |  |  |  |  | 102.152 | 2 | 0 | 0 | 672 | 204.304 | 137292.288 | 0 | 100%
92 |  | MUNDRA-JETPUR I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337 | 3 | 0 | 0 | 672 | 1011 | 679392 | 0 | 100%
93 |  | MUNDRA-JETPUR II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 337 | 3 | 0 | 0 | 672 | 1011 | 679392 | 0 | 100%
94 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) I 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 672 | 114.2 | 76742.4 | 0 | 100%
95 |  | VINDHYACHAL (PG)-VINDHYACHAL (NTPC) II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 28.55 | 4 | 0 | 0 | 672 | 114.2 | 76742.4 | 0 | 100%
96 |  | V'CHAL-SASAN I 400 KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 672 | 10.886 | 7315.392 | 0 | 100%
97 |  | V'CHAL - SASAN II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 5.443 | 2 | 0 | 0 | 672 | 10.886 | 7315.392 | 0 | 100%
98 | 902084 | SASAN-SATNA I 765kV | 2014-02-16 | 10:27 | 2014-02-16 | 12:33 | - |  |  | 0.0875 | 2 | 6 | - |  |  | - |  |  | OMSU | H/T to avail S/D taken by Sasan for Line Reactor relay testing. | LD 02/1667 | LD 02/1671 LD 02/249
| 902091 | SASAN-SATNA I 765kV | 2014-02-17 | 12:32 | 2014-02-17 | 13:43 | - |  |  | 0.049306 | 1 | 11 | - |  |  | - |  |  | OMSU | Line A/T due to LBB operated at Sasan end and DT received at Satna end. |  | LD 02/1776 LD 02/266
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0.13681 | 3 | 17 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 3.2833 |  |  | 0 |  |  | 0 |  |  |  |  | 245.7 | 4 | 0 | 0 | 668.7167 | 982.8 | 657214.74 | 0 | 100%
99 |  | BINA(PG)-BINA(MPEB) III 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.62 | 2 | 0 | 0 | 672 | 1.24 | 833.28 | 0 | 100%
100 |  | VAPI - NAVASARI (GIS) I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 672 | 233.7 | 157046.4 | 0 | 100%
101 |  | VAPI - NAVASARI (GIS) II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 116.85 | 2 | 0 | 0 | 672 | 233.7 | 157046.4 | 0 | 100%
102 | 901202 | SASAN-SATNA II 765kV | 2014-01-26 | 03:10 | 2014-02-06 | 13:29 | - |  |  | - |  |  | - |  |  | 1900-01-10 10:19 | 274 | 19 | LVRD | After Tripping on over voltage, line kept out for volatge regulation on WRLDC Instruction. |  | WR 02/563 NLD 02/99
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-10 10:19 | 274 | 19
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 274.3167 |  |  |  |  | 242.23 | 4 | 0 | 0 | 672 | 968.92 | 651114.24 | 0 | 100%
103 |  | BINA(PG)-BINA(MPEB) IV 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 0.62 | 2 | 0 | 0 | 672 | 1.24 | 833.28 | 0 | 100%
104 | 902003 | INDORE (PG)-INDORE (MP) I 400kV | 2014-02-01 | 11:09 | 2014-02-01 | 21:00 | - |  |  | - |  |  | - |  |  | 0.41042 | 9 | 51 | LCSD | Line H/T to avail S/D for OPGW stringing for ULDC Work, After Completion of Work by Powergrid PTW returned by 21:00hrs, Line kept out due to prevailing high volatge as per WRLDC Instruction. | LD 02/48 | LD 02/103
| 902004 | INDORE (PG)-INDORE (MP) I 400kV | 2014-02-01 | 21:00 | 2014-02-01 | 22:56 | - |  |  | - |  |  | - |  |  | 0.080556 | 1 | 56 | LVRD | After Completion of Work by POWERGRID, Line Kept out for volatge regulation on WRLDC Instruction. | LD 02/103 | LD 02/109
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49097 | 10 | 107
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 11.7833 |  |  |  |  | 49.726 | 4 | 0 | 0 | 672 | 198.904 | 133663.488 | 0 | 100%
105 |  | INDORE (PG)-INDORE (MP) II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 49.726 | 4 | 0 | 0 | 672 | 198.904 | 133663.488 | 0 | 100%
106 |  | 400kV Jabalpur - Jabalpur Pooling#1
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 15.456 | 4 | 0 | 0 | 672 | 61.824 | 41545.728 | 0 | 100%
107 | 902116 | JABALPUR - JABALPUR (POOLING) II 400kV | 2014-02-22 | 18:09 | 2014-02-22 | 18:22 | 0.0090278 | 0 | 13 | - |  |  | - |  |  | - |  |  | LEFT | Line A/T on B-Ph to E/F. F/L 7.6Km from Jablapur 400kV S/S.
|  | SUBTOTAL |  |  |  |  | 0.0090278 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0.21667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 15.456 | 4 | 0.21667 | 13.3952 | 672 | 61.824 | 41545.728 | 0.00032242 | 99.97%
108 | 901244 | JABALPUR (POOLING) - BINA I 765kV | 2014-01-30 | 21:58 | 2014-02-12 | 09:52 | - |  |  | - |  |  | - |  |  | 1900-01-10 09:52 | 273 | 52 | LVRD | After Tripping on over voltage, line kept out for volatge regulation on WRLDC Instruction. |  | WR 02/1205 NLD 02/184
| 902137 | JABALPUR(POOLING)-BINA I 765kV | 2014-02-26 | 18:24 | 2014-02-26 | 18:34 | - |  |  | - |  |  | 0.0069444 | 0 | 10 | - |  |  | LNCC | Line A/T on B-ph to E/F, F/L - 77.8kms from Bina ( 6kAmp), 140kms from Jabalpur(1.9kamp), Charging code delayed by WRLDC. During tripping time, heavy lightening & thunderstrom were persisting in that area.
| 902138 | JABALPUR(POOLING)-BINA I 765kV | 2014-02-26 | 18:34 | 2014-02-26 | 20:05 | - |  |  | - |  |  | - |  |  | 0.063194 | 1 | 31 | LVRD | Line Kept out on WRLDC instruction due to preveiling high voltage. |  | LD 02/2900 NLD 02/379
| 902139 | JABALPUR(POOLING)-BINA I 765kV | 2014-02-26 | 22:04 | 2014-02-26 | 22:14 | 0.0069444 | 0 | 10 | - |  |  | - |  |  | - |  |  | OMST | Line A/T at Bina end only due to operation of PRV at Bina end. |  | LD 02/2931 NLD 02/381
| 902140 | JABALPUR(POOLING)-BINA I 765kV | 2014-02-26 | 22:14 | 2014-02-27 | 07:31 | - |  |  | - |  |  | - |  |  | 0.38681 | 9 | 17 | LVRD | After tripping line kept out on voltage regulation on WRLDC instructions. | LD 02/2931 NLD 02/381 | WR 02/2951 NLD 02/387
| 902149 | JABALPUR(POOLING)-BINA I 765kV | 2014-02-27 | 18:39 | 2014-02-27 | 20:40 | 0.084028 | 2 | 1 | - |  |  | - |  |  | - |  |  | OMST | Line A/T at due to operation of Reactor PRV at Bina during heavy rain.
| 902152 | JABALPUR(POOLING)-BINA I 765kV | 2014-02-27 | 20:40 |  |  | - |  |  | - |  |  | - |  |  | 1899-12-31 03:20 | 27 | 20 | LVRD | Reactor PRV problem at Bina rectified and Line made ready since 20:40Hrs/27.02.14, Due prevailing system high voltage, line kept out for voltage regulation on WRLDC Instruction.
|  | SUBTOTAL |  |  |  |  | 0.090972 | 2 | 11 | 0 | 0 | 0 | 0.0069444 | 0 | 10 | 1900-01-12 | 310 | 120
|  | Element Availability= | [6 empty] | 2.1833 |  |  | 0 |  |  | 0.16667 |  |  | 312 |  |  |  |  | 229.74 | 4 | 2.1833 | 2006.396 | 671.8333 | 918.96 | 617387.96 | 0.0032498 | 99.68%
109 | 902033 | JABALPUR (POOLING) - BINA II 765kV | 2014-02-06 | 12:07 | 2014-02-06 | 18:02 | - |  |  | - |  |  | - |  |  | 0.24653 | 5 | 55 | SCSD | Line H/T to facilitate movment of 765kV ICT # 2 units at Jabalpur pooling SS. | LD 02/555 LD 02/96
| 902036 | JABALPUR (POOLING) - BINA II 765kV | 2014-02-06 | 18:02 | 2014-02-08 | 15:08 | - |  |  | - |  |  | - |  |  | 1899-12-31 21:06 | 45 | 6 | LVRD | Kept out on High system voltage as per WRLDC instructions. |  | WR 02/807 NLD 02/132
| 902063 | JABALPUR (POOLING) - BINA II 765kV | 2014-02-11 | 23:54 | 2014-02-27 | 20:59 | - |  |  | - |  |  | - |  |  | 1900-01-14 21:05 | 381 | 5 | LVRD | Line H/T for Voltage regulation on WRLDC Instruction. | LD 02/1194 LD 02/182 | WR 02/3053 NLD 02/402
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-17 00:06 | 431 | 66
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 432.1 |  |  |  |  | 229.74 | 4 | 0 | 0 | 672 | 918.96 | 617541.12 | 0 | 100%
[20 empty] | TRANSMISSION LINE AVAILABILITY | [5 empty] | 38156.7179 |  |  | 28053704.8643
0.0013601
99.86%
106 |  | AGRA-GWALIOR I 765KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 129.435 | 4 | 0 | 0 | 672 | 517.74 | 347921.28 | 0 | 100%
107 | 902159 | AGRA-GWALIOR II 765KV | 2014-02-28 | 15:44 | 2014-02-28 | 20:36 | - |  |  | - |  |  | 0.20278 | 4 | 52 | - |  |  | LNCC | A/T due to conduction of LA at Agra (NRTS#1) during heavy rains and lightening. |  | WR 02/3191 NLD 02/420 NR 02/2987
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.20278 | 4 | 52 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 4.8667 |  |  | 0 |  |  |  |  | 127.934 | 4 | 0 | 0 | 667.1333 | 511.736 | 341396.1435 | 0 | 100%
ICTs
1 |  | ICT1 JABALPUR 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
2 |  | ICT II JABALPUR 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
3 |  | ICT1 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
4 |  | ICT2 DEHGAM 400/220kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
5 | 902043 | ICT1 SATNA 400/220kV | 2014-02-07 | 14:30 | 2014-02-07 | 16:03 | 0.064583 | 1 | 33 | - |  |  | - |  |  | - |  |  | OSPT | ICT H/T to avail OCC approved S/D by POWERGRID for measurement of C & Tan delta of R & Y phase bushings. | LD 02/675 | LD 02/686
|  | SUBTOTAL |  |  |  |  | 0.064583 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 1.55 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 1.55 | 1220.625 | 672 | 787.5 | 529200 | 0.0023065 | 99.77%
6 |  | ICT2 SATNA 400/220KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
7 |  | ICT1 KHANDWA 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
8 |  | ICT2 KHANDWA 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
9 |  | ICT1 VAPI 400/220KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
10 |  | ICT2 VAPI 400/220KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
11 |  | ICT1 GWALIOR 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
12 | 902147 | ICT1 RAJGARH 400/220kV | 2014-02-27 | 10:25 | 2014-02-27 | 14:17 | 0.16111 | 3 | 52 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail OCC S/D for AMP. | LD 02/2978 | LD 02/3008
|  | SUBTOTAL |  |  |  |  | 0.16111 | 3 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.8667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 3.8667 | 3045 | 672 | 787.5 | 529200 | 0.005754 | 99.42%
13 | 902122 | ICT2 GWALIOR 400/220kV | 2014-02-25 | 09:17 | 2014-02-25 | 13:15 | 0.16528 | 3 | 58 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail OCC approved S/D for AMP | LD 02/2689 | LD 02/2716
|  | SUBTOTAL |  |  |  |  | 0.16528 | 3 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 3.9667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 3.9667 | 3123.75 | 672 | 787.5 | 529200 | 0.0059028 | 99.41%
14 |  | ICT I ITARSI 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
15 |  | ICT1 DAMOH 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
16 |  | ICT2 DAMOH 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
17 | 902158 | ICT2 RAJGARH 400/220kV | 2014-02-28 | 09:55 | 2014-02-28 | 12:35 | 0.11111 | 2 | 40 | - |  |  | - |  |  | - |  |  | OSPT | H/T to avail OCC S/D for AMP. | LD 02/3118 | LD 02/3137
|  | SUBTOTAL |  |  |  |  | 0.11111 | 2 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 2.6667 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 2.6667 | 2100 | 672 | 787.5 | 529200 | 0.0039683 | 99.6%
18 | 902112 | ICT1 BINA 400/220/33kV | 2014-02-22 | 10:10 | 2014-02-22 | 19:56 | - |  |  | - |  |  | - |  |  | 0.40694 | 9 | 46 | SCSD | ICT H/T to avail OCC approved S/D for installation of online dry out system. | LD 02/2347 | LD 02/2406
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40694 | 9 | 46
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 9.7667 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
19 | 901206 | ICT 1 PIRANA 400/220/33kV | 2014-01-26 | 11:25 | 2014-02-10 | 13:40 | - |  |  | - |  |  | - |  |  | 1900-01-08 13:40 | 229 | 40 | SCSD | ICT H/T for replacing existing ICT with spare ICT in view of failure of short circuit test of existing ICT. | LD 01/2800 | LD 02/1029
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 13:40 | 229 | 40
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 229.6667 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
20 |  | ICT2 PIRANA 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
21 |  | ICT3 GWALIOR 400/220/33kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
22 |  | ICT1 SHUJALPUR 400/220/33kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
23 |  | ICT1 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
24 |  | ICT2 BHACHAU 400/220/33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
25 |  | ICT2, SHUJALPUR 400/220kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
26 |  | ICT1 SATNA 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 672 | 2500 | 1680000 | 0 | 100%
27 |  | ICT 2 NAVSARI 400/220/33kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
28 |  | ICT 1 NAVSARI 400/220/33kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
29 |  | ICT2 SATNA 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 672 | 2500 | 1680000 | 0 | 100%
30 |  | ICT1 BINA 765/400KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 672 | 2500 | 1680000 | 0 | 100%
31 |  | ICT3 VAPI 400/220/33kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 315 | 2.5 | 0 | 0 | 672 | 787.5 | 529200 | 0 | 100%
32 |  | ICT2 BINA 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1000 | 2.5 | 0 | 0 | 672 | 2500 | 1680000 | 0 | 100%
33 |  | ICT 1 GWALIOR 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 672 | 3750 | 2520000 | 0 | 100%
34 |  | ICT2 GWALIOR 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 672 | 3750 | 2520000 | 0 | 100%
35 | 902029 | ICT2 INDORE 765/400KV | 2014-02-05 | 10:50 | 2014-02-05 | 19:28 | - |  |  | - |  |  | - |  |  | 0.35972 | 8 | 38 | SCSD | H/T to avail OCC Approved S/D for completion of balance construction works. | LD 02/453 NLD 02/78 | LD 02/504 NLD 02/83
| 902073 | ICT2 INDORE 765/400KV | 2014-02-14 | 11:25 | 2014-02-14 | 19:35 | - |  |  | - |  |  | - |  |  | 0.34028 | 8 | 10 | SCSD | H/T to avail OCC S/D by POWERGRID for construction related works. | LD 02/1461 LD 02/217 | LD 02/1497 LD 02/222
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35972 | 8 | 38
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 8.6333 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 672 | 3750 | 2520000 | 0 | 100%
36 |  | ICT1 INDORE 765/400KV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 672 | 3750 | 2520000 | 0 | 100%
37 | 902034 | ICT1 JABALPUR 765/400KV | 2014-02-06 | 12:18 | 2014-02-06 | 13:10 | - |  |  | - |  |  | - |  |  | 0.036111 | 0 | 52 | SCSD | H/T to facilitate movment of 765kV ICT # 2 units at Jabalpur pooling SS. | LD 02/556 LD 02/97 | LD 02/564 LD 02/100
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036111 | 0 | 52
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0.86667 |  |  |  |  | 1500 | 2.5 | 0 | 0 | 672 | 3750 | 2520000 | 0 | 100%
[20 empty] | ICT AVAILABILITY | [5 empty] | 9489.375 |  |  | 34137600
0.00027797
99.97%
Bus Reactors
1 |  | BUS REACTOR DEHGAM I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
2 |  | BUS REACTOR JABALPUR I 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 672 | 100 | 67200 | 0 | 100%
3 |  | BUS REACTOR JABALPUR II 33kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 25 | 4 | 0 | 0 | 672 | 100 | 67200 | 0 | 100%
4 |  | BUS REACTOR ITARSI I 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 672 | 200 | 134400 | 0 | 100%
5 |  | BUS REACTOR ITARSI II 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 672 | 200 | 134400 | 0 | 100%
6 |  | BUS REACTOR ITARSI III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 672 | 200 | 134400 | 0 | 100%
7 |  | BUS REACTOR JABALPUR III 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
8 | 902002 | BUS REACTOR DHULE 400kV | 2014-02-01 | 10:26 | 2014-02-01 | 18:00 | - |  |  | - |  |  | - |  |  | 0.31528 | 7 | 34 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/44 | LD 02/75
| 902010 | BUS REACTOR DHULE 400kV | 2014-02-02 | 11:08 | 2014-02-02 | 17:45 | - |  |  | - |  |  | - |  |  | 0.27569 | 6 | 37 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/143 | LD 02/163
| 902017 | BUS REACTOR DHULE 400kV | 2014-02-03 | 07:51 | 2014-02-03 | 18:02 | - |  |  | - |  |  | - |  |  | 0.42431 | 10 | 11 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/204 | LD 02/270
| 902021 | BUS REACTOR DHULE 400kV | 2014-02-04 | 08:30 | 2014-02-04 | 18:03 | - |  |  | - |  |  | - |  |  | 0.39792 | 9 | 33 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/324 | LD 02/376
| 902028 | BUS REACTOR DHULE 400kV | 2014-02-05 | 07:51 | 2014-02-05 | 21:34 | - |  |  | - |  |  | - |  |  | 0.57153 | 13 | 43 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/434 | LD 02/514
| 902031 | BUS REACTOR DHULE 400kV | 2014-02-06 | 09:45 | 2014-02-06 | 18:05 | - |  |  | - |  |  | - |  |  | 0.34722 | 8 | 20 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/536
| 902038 | BUS REACTOR DHULE 400kV | 2014-02-07 | 08:20 | 2014-02-07 | 18:08 | - |  |  | - |  |  | - |  |  | 0.40833 | 9 | 48 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/638 | LD 02/704
| 902045 | BUS REACTOR DHULE 400kV | 2014-02-08 | 08:01 | 2014-02-08 | 18:02 | - |  |  | - |  |  | - |  |  | 0.41736 | 10 | 1 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/761 | LD 02/831
| 902053 | BUS REACTOR DHULE 400kV | 2014-02-09 | 06:45 | 2014-02-09 | 17:16 | - |  |  | - |  |  | - |  |  | 0.43819 | 10 | 31 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/879 | LD 02/914
| 902054 | BUS REACTOR DHULE 400kV | 2014-02-10 | 08:40 | 2014-02-10 | 20:36 | - |  |  | - |  |  | - |  |  | 0.49722 | 11 | 56 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/998 | LD 02/1069
| 902060 | BUS REACTOR DHULE 400kV | 2014-02-11 | 07:47 | 2014-02-11 | 21:34 | - |  |  | - |  |  | - |  |  | 0.57431 | 13 | 47 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1106 | LD 02/1185
| 902064 | BUS REACTOR DHULE 400kV | 2014-02-12 | 08:50 | 2014-02-12 | 17:43 | - |  |  | - |  |  | - |  |  | 0.37014 | 8 | 53 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1219 | LD 02/1280
| 902067 | BUS REACTOR DHULE 400kV | 2014-02-13 | 09:46 | 2014-02-13 | 18:31 | - |  |  | - |  |  | - |  |  | 0.36458 | 8 | 45 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1334 | LD 02/1391
| 902070 | BUS REACTOR DHULE 400kV | 2014-02-14 | 06:09 | 2014-02-14 | 17:54 | - |  |  | - |  |  | - |  |  | 0.48958 | 11 | 45 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1426 | LD 02/1491
| 902078 | BUS REACTOR DHULE 400kV | 2014-02-15 | 07:32 | 2014-02-15 | 19:08 | - |  |  | - |  |  | - |  |  | 0.48333 | 11 | 36 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1537 | LD 02/1598
| 902096 | BUS REACTOR DHULE 400kV | 2014-02-18 | 07:24 | 2014-02-18 | 19:11 | - |  |  | - |  |  | - |  |  | 0.49097 | 11 | 47 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1851 | LD 02/1938
| 902106 | BUS REACTOR DHULE 400kV | 2014-02-19 | 10:56 | 2014-02-19 | 16:43 | - |  |  | - |  |  | - |  |  | 0.24097 | 5 | 47 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2014 | LD 02/2047
| 902111 | BUS REACTOR DHULE 400kV | 2014-02-22 | 08:50 | 2014-02-22 | 18:32 | - |  |  | - |  |  | - |  |  | 0.40417 | 9 | 42 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2337 | LD 02/2393
| 902119 | BUS REACTOR DHULE 400kV | 2014-02-23 | 10:06 | 2014-02-23 | 18:01 | - |  |  | - |  |  | - |  |  | 0.32986 | 7 | 55 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2460 | LD 02/2500
| 902120 | BUS REACTOR DHULE 400kV | 2014-02-24 | 09:32 | 2014-02-24 | 18:57 | - |  |  | - |  |  | - |  |  | 0.39236 | 9 | 25 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2577 | LD 02/2634
| 902132 | BUS REACTOR DHULE 400kV | 2014-02-26 | 09:43 | 2014-02-26 | 18:22 | - |  |  | - |  |  | - |  |  | 0.36042 | 8 | 39 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2813 | LD 02/2892
| 902145 | BUS REACTOR DHULE 400kV | 2014-02-27 | 09:55 | 2014-02-27 | 16:20 | - |  |  | - |  |  | - |  |  | 0.26736 | 6 | 25 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2974 | LD 02/3022
| 902157 | BUS REACTOR DHULE 400kV | 2014-02-28 | 07:46 | 2014-02-28 | 22:05 | - |  |  | - |  |  | - |  |  | 0.59653 | 14 | 19 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/3102 | LD 02/3203
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900-01-08 10:59 | 213 | 839
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 226.9833 |  |  |  |  | 80 | 4 | 0 | 0 | 672 | 320 | 215040 | 0 | 100%
9 |  | BUS REACTOR SATNA I 400kV
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 50 | 4 | 0 | 0 | 672 | 200 | 134400 | 0 | 100%
10 | 902040 | BUS REACTOR BINA 400kV | 2014-02-07 | 09:02 | 2014-02-08 | 13:37 | - |  |  | - |  |  | - |  |  | 1899-12-31 04:35 | 28 | 35 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/644 | LD 02/803
| 902087 | BUS REACTOR BINA 400kV | 2014-02-17 | 09:34 | 2014-02-17 | 12:17 | - |  |  | - |  |  | - |  |  | 0.11319 | 2 | 43 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1746 | LD 02/1769
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1899-12-31 07:18 | 30 | 78
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 31.3 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
11 |  | Bus Reactor / Damoh |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
12 | 902163 | BUS REACTOR GWALIOR I 50MVAR, 400kV | 2014-02-28 | 21:22 | 2014-02-28 | 23:25 | - |  |  | - |  |  | - |  |  | 0.085417 | 2 | 3 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/3195 | LD 02/3209
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.085417 | 2 | 3
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 2.05 |  |  |  |  | 50 | 4 | 0 | 0 | 672 | 200 | 134400 | 0 | 100%
13 |  | BUS REACTOR KHANDWA 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
14 |  | BUS REACTOR DEHGAM II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
15 | 902130 | BUS REACTOR, BHACHAU 400kV | 2014-02-26 | 08:26 | 2014-02-26 | 18:27 | - |  |  | - |  |  | - |  |  | 0.41736 | 10 | 1 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/2797 | LD 02/2893
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41736 | 10 | 1
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 10.0167 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
16 | 902047 | BUS REACTOR SHUJALPUR 400kV | 2014-02-08 | 09:17 | 2014-02-08 | 13:34 | - |  |  | - |  |  | - |  |  | 0.17847 | 4 | 17 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/777 | LD 02/803
| 902088 | BUS REACTOR SHUJALPUR 400kV | 2014-02-17 | 09:36 | 2014-02-17 | 12:20 | - |  |  | - |  |  | - |  |  | 0.11389 | 2 | 44 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/1746 | LD 02/1769
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11389 | 2 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 2.7333 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
17 |  | BUS REACTOR RAJGARH 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
18 |  | BUS REACTOR SATNA 765kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
19 |  | BUS REACTOR NAVSARI 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
20 |  | Switchable Satna-I Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
21 |  | Switchable Satna-II Line Reactor / Satna 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
22 |  | BUS REACTOR SATNA II 400kV
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
23 |  | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
24 |  | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
25 |  | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
26 |  | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
27 | 902162 | BUS REACTOR GWALIOR II125MVAR, 400kV | 2014-02-28 | 21:18 | 2014-02-28 | 21:59 | - |  |  | - |  |  | - |  |  | 0.028472 | 0 | 41 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/3195 | LD 02/3199
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028472 | 0 | 41
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0.68333 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
28 | 902161 | BUS REACTOR GWALIOR III 125MVAR, 400kV | 2014-02-28 | 21:15 | 2014-02-28 | 21:59 | - |  |  | - |  |  | - |  |  | 0.030556 | 0 | 44 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/3195 | LD 02/3199
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030556 | 0 | 44
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0.73333 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
29 | 902041 | BUS REACTOR INDORE 400kV | 2014-02-07 | 09:18 | 2014-02-07 | 23:06 | - |  |  | - |  |  | - |  |  | 0.575 | 13 | 48 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | LD 02/647 | LD 02/738
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.575 | 13 | 48
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 13.8 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
30 |  | Switchable Indore - Line Reactor / Bina 765KV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
31 |  | Switchable Shujalpur-II Line Reactor / Bina 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
32 |  | Switchable Shujalpur-I Line Reactor / Bina 400kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 63 | 4 | 0 | 0 | 672 | 252 | 169344 | 0 | 100%
33 | 902048 | BUS REACTOR INDORE 765kV | 2014-02-08 | 09:18 | 2014-02-08 | 13:16 | - |  |  | - |  |  | - |  |  | 0.16528 | 3 | 58 | SVRD | Bus Reactor H/T for voltage regulation on WRLDC instruction | WR 02/775 NLD 02/125 | WR 02/801 NLD 02/130
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
34 |  | Switchable Bina - I Line Reactor / Jabalpur Pooling 765kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
35 |  | Bus Reactor 400kV / Jabalpur Pool 765kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 125 | 4 | 0 | 0 | 672 | 500 | 336000 | 0 | 100%
36 |  | Bus Reactor-I / Bina 765kV |  |  |  |  | - |  |  | - |  |  | - |  |  | -
|  | SUBTOTAL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Element Availability= | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  |  | 240 | 4 | 0 | 0 | 672 | 960 | 645120 | 0 | 100%
[20 empty] | BUS REACTOR AVAILABILITY | [5 empty] | 0 |  |  | 11211648
0
100%
[20 empty] | SYSTEM AVAILABILITY | [5 empty] | 47646.0929 |  |  | 73402952.8643
0.0006491
99.94%
Formulas:
OUTAGE DEEMED AVAILABLE = IF((RIGHT([Outage Category],1)="D"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE DEEMED AVAILABLE = SUM([OUTAGE DEEMED AVAILABLE, row above])
OUTAGE HOURS ATTRIBUTED TO = IF((RIGHT([Outage Category],1)="T"),([RESTORATION DATE]+[RESTORATION TIME])-([TRIPPING DATE]+[TRIPPING TIME]),"-")
OUTAGE HOURS ATTRIBUTED TO = SUM(H5:[OUTAGE HOURS ATTRIBUTED TO, row above])
SYSTEM CONSTR. = SUM([SYSTEM CONSTR., row above])
SYSTEM CONSTR. = SUM([SYSTEM CONSTR., row above]:[SYSTEM CONSTR., row above])
OTHERS = SUM(K78:[OTHERS, row above])
OTHERS = SUM([OTHERS, row above])

## Feb14 Availability sheet
POWERGRID - WRTS - II
OUTAGE DATA OF TRANSMISSION SYSTEM FOR FEBRUARY -2014
Sl. | Name of transmission lines | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Line length | [6 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual
[6 empty] | POWERGRID | OTHERS | THM | kms | [NSC] | [ OH*CktKm*NSC] | [CktKm*NSC] | THM *Cktkm1 * NSC1 | NAFM | Availability
|  | Hours | Mints | Hours | Mints | Hours | OH2 | =28*24-OH2 | [6 empty] | =100-100*O
Hours
1 | 400kV Satpura-Itarsi |  |  |  |  | 0 | 0 | 672 | 79 | 2 | 0 | 158 | 106176 | 0 | 100 | 100%
2 | 400kV Itarsi-Indore # 1 |  |  |  |  | 0 | 0 | 672 | 207 | 2 | 0 | 414 | 278208 | 0 | 100 | 100%
3 | 400kV Itarsi-Indore # 2 |  |  |  |  | 0 | 0 | 672 | 214 | 2 | 0 | 428 | 287616 | 0 | 100 | 100%
4 | 400kV Indore-Asoj # 1 |  |  |  |  | 0 | 0 | 672 | 289 | 2 | 0 | 578 | 388416 | 0 | 100 | 100%
5 | 400kV Indore-Asoj # 2 |  |  |  |  | 0 | 0 | 672 | 273 | 2 | 0 | 546 | 366912 | 0 | 100 | 100%
6 | 400 KV V'chal - Jabalpur # 1 |  |  |  |  | 0 | 0 | 672 | 360 | 2 | 0 | 720 | 483840 | 0 | 100 | 100%
7 | 400 KV V'chal - Jabalpur # 2 |  |  |  |  | 0 | 0 | 672 | 360 | 2 | 0 | 720 | 483840 | 0 | 100 | 100%
8 | 400 KV Jabalpur - Itarsi # 1 | 3 | 2 |  |  | 3.0333 | 0 | 672 | 232 | 2 | 1407.4667 | 464 | 311808 | 0.0045139 | 99.5486 | 99.55%
9 | 400 KV Jabalpur - Itarsi # 2 |  |  |  |  | 0 | 0 | 672 | 232 | 2 | 0 | 464 | 311808 | 0 | 100 | 100%
10 | 400kV Jhanor-Dehgam#1 |  |  |  |  | 0 | 0 | 672 | 157 | 2 | 0 | 314 | 211008 | 0 | 100 | 100%
11 | 400kV Jhanor-Dehgam#2 |  |  |  |  | 0 | 0 | 672 | 157 | 2 | 0 | 314 | 211008 | 0 | 100 | 100%
12 | 400 KV Jabalpur-Sasan |  |  | 0 | 53 | 0 | 0.88333 | 671.1167 | 376 | 2 | 0 | 752 | 504679.7333 | 0 | 100 | 100%
13 | 400kV Sasan-Vindhyachal |  |  |  |  | 0 | 0 | 672 | 21 | 2 | 0 | 42 | 28224 | 0 | 100 | 100%
14 | 400 KV V'chal - Jabalpur # 4 | 7 | 56 | 10 | 76 | 7.9333 | 11.2667 | 660.7333 | 389 | 2 | 6172.1333 | 778 | 514050.5333 | 0.012007 | 98.7993 | 98.8%
15 | 400 KV Jabalpur - Itarsi # 3 |  |  |  |  | 0 | 0 | 672 | 234 | 2 | 0 | 468 | 314496 | 0 | 100 | 100%
16 | 400 KV Jabalpur - Itarsi # 4 | 0 | 10 | 0 | 6 | 0.16667 | 0.1 | 671.9 | 234 | 2 | 78 | 468 | 314449.2 | 0.00024805 | 99.9752 | 99.98%
17 | 400 KV Itarsi - Khandwa # 1 |  |  |  |  | 0 | 0 | 672 | 196.64 | 2 | 0 | 393.28 | 264284.16 | 0 | 100 | 100%
18 | 400 KV Itarsi - Khandwa # 2 |  |  |  |  | 0 | 0 | 672 | 196.64 | 2 | 0 | 393.28 | 264284.16 | 0 | 100 | 100%
19 | 400 KV Khandwa - Dhule # 1 |  |  |  |  | 0 | 0 | 672 | 261.78 | 2 | 0 | 523.56 | 351832.32 | 0 | 100 | 100%
20 | 400 KV Khandwa - Dhule # 2 | 6 | 52 | 12 | 0 | 6.8667 | 12 | 660 | 261.78 | 2 | 3595.112 | 523.56 | 345549.6 | 0.010404 | 98.9596 | 98.96%
21 | 400 KV Jhanor - Sugen(PGCIL portion) |  |  |  |  | 0 | 0 | 672 | 57 | 2 | 0 | 114 | 76608 | 0 | 100 | 100%
22 | 400 KV Sugen - Vapi (PGCIL portion) |  |  | 0 | 55 | 0 | 0.91667 | 672 | 110 | 2 | 0 | 220 | 147840 | 0 | 100 | 100%
23 | 400 KV Jhanor - Jhanor(GPEC) |  |  |  |  | 0 | 0 | 672 | 13 | 2 | 0 | 26 | 17472 | 0 | 100 | 100%
24 | 220kV Jhanor-Haldarwa ckI # 1 |  |  |  |  | 0 | 0 | 672 | 13 | 1 | 0 | 13 | 8736 | 0 | 100 | 100%
25 | 200kV Jhanor-Haldarwa ckt # 2 |  |  |  |  | 0 | 0 | 672 | 13 | 1 | 0 | 13 | 8736 | 0 | 100 | 100%
26 | 220kV Kawas-Navsari (GIS)#1 |  |  |  |  | 0 | 0 | 672 | 58.149 | 1 | 0 | 58.149 | 39076.128 | 0 | 100 | 100%
27 | 220kV Kawas-Navsari (GIS)#2 |  |  |  |  | 0 | 0 | 672 | 58.149 | 1 | 0 | 58.149 | 39076.128 | 0 | 100 | 100%
28 | 220kV Navsari (GIS)- Navsari (GETCO)#1 |  |  |  |  | 0 | 0 | 672 | 31.334 | 1 | 0 | 31.334 | 21056.448 | 0 | 100 | 100%
29 | 220kV Navsari (GIS)- Navsari (GETCO)#2 |  |  |  |  | 0 | 0 | 672 | 31.334 | 1 | 0 | 31.334 | 21056.448 | 0 | 100 | 100%
30 | 220kV Kawas-Vav#1 |  |  |  |  | 0 | 0 | 672 | 37 | 1 | 0 | 37 | 24864 | 0 | 100 | 100%
31 | 220kV Kawas-Vav#2 |  |  |  |  | 0 | 0 | 672 | 37 | 1 | 0 | 37 | 24864 | 0 | 100 | 100%
32 | 220kV Kawas - Haldarwa # 1 | 0 | 10 | 1 | 47 | 0.16667 | 1.7833 | 670.2167 | 81 | 1 | 13.5 | 81 | 54287.55 | 0.00024868 | 99.9751 | 99.98%
33 | 220kV Kawas-Haldarwa # 2 |  |  |  |  | 0 | 0 | 672 | 81 | 1 | 0 | 81 | 54432 | 0 | 100 | 100%
34 | 220 kV Kakrapar - Haldarwa # 1 |  |  |  |  | 0 | 0 | 672 | 74 | 1 | 0 | 74 | 49728 | 0 | 100 | 100%
35 | 220 KV Kakrapar - Haldarwa # 2 |  |  |  |  | 0 | 0 | 672 | 74 | 1 | 0 | 74 | 49728 | 0 | 100 | 100%
36 | 220 KV Kakrapar - Vav # 1 |  |  |  |  | 0 | 0 | 672 | 43 | 1 | 0 | 43 | 28896 | 0 | 100 | 100%
37 | 220 KV Kakrapar - Vav # 2 |  |  |  |  | 0 | 0 | 672 | 43 | 1 | 0 | 43 | 28896 | 0 | 100 | 100%
38 | 220kV Kakrapar-Vapi ckt # 1 |  |  |  |  | 0 | 0 | 672 | 117 | 1 | 0 | 117 | 78624 | 0 | 100 | 100%
39 | 220kV Kakrapar-Vapi ckt # 2 |  |  |  |  | 0 | 0 | 672 | 117 | 1 | 0 | 117 | 78624 | 0 | 100 | 100%
40 | 400kV V'chal - Satna # 1 |  |  |  |  | 0 | 0 | 672 | 267 | 2 | 0 | 534 | 358848 | 0 | 100 | 100%
41 | 400kV V'chal - Satna # 2 |  |  |  |  | 0 | 0 | 672 | 267 | 2 | 0 | 534 | 358848 | 0 | 100 | 100%
42 | 400kV V'chal - Satna # 3 |  |  | 11 | 10 | 0 | 11.1667 | 660.8333 | 258.31 | 2 | 0 | 516.62 | 341399.7167 | 0 | 100 | 100%
43 | 400kV V'chal -Nigrie |  |  |  |  | 0 | 0 | 672 | 100.32 | 2 | 0 | 200.64 | 134830.08 | 0 | 100 | 100%
44 | 400kV Nigrie-Satna |  |  |  |  | 0 | 0 | 672 | 161.11 | 2 | 0 | 322.22 | 216531.84 | 0 | 100 | 100%
45 | 400kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 672 | 276 | 2 | 0 | 552 | 370944 | 0 | 100 | 100%
46 | 400kV Satna - Bina # 2 |  |  |  |  | 0 | 0 | 672 | 276 | 2 | 0 | 552 | 370944 | 0 | 100 | 100%
47 | 400kV Bina(PG) - Bina(MPPTCL) # 1 |  |  |  |  | 0 | 0 | 672 | 0.742 | 2 | 0 | 1.484 | 997.248 | 0 | 100 | 100%
48 | 400kV Bina(PG) - Bina(MPPTCL) # 2 |  |  |  |  | 0 | 0 | 672 | 0.742 | 2 | 0 | 1.484 | 997.248 | 0 | 100 | 100%
49 | 765 kV Gwalior-Bina # 1 |  |  | 0 | 55 | 0 | 0.91667 | 671.0833 | 234.931 | 4 | 0 | 939.724 | 630633.1143 | 0 | 100 | 100% | Upgraded to 765kV level w.e.f 01.04.2013
50 | 400KV Satna-Bina # 4 |  |  |  |  | 0 | 0 | 672 | 272.586 | 2 | 0 | 545.172 | 366355.584 | 0 | 100 | 100%
51 | 400KV Satna-Bina # 3 |  |  | 8 | 21 | 0 | 8.35 | 663.65 | 272.586 | 2 | 0 | 545.172 | 361803.3978 | 0 | 100 | 100%
52 | 400KV Bina - Sujalpur # 1 |  |  |  |  | 0 | 0 | 672 | 199.936 | 2 | 0 | 399.872 | 268713.984 | 0 | 100 | 100%
53 | 400KV Bina - Sujalpur # 2 |  |  |  |  | 0 | 0 | 672 | 199.936 | 2 | 0 | 399.872 | 268713.984 | 0 | 100 | 100%
54 | 400KV Sujalpur - Nagda # 1 |  |  |  |  | 0 | 0 | 672 | 152.229 | 2 | 0 | 304.458 | 204595.776 | 0 | 100 | 100%
55 | 400KV Sujalpur - Nagda # 2 |  |  |  |  | 0 | 0 | 672 | 152.229 | 2 | 0 | 304.458 | 204595.776 | 0 | 100 | 100%
56 | 400KV Nagda - Dehgam # 2 |  |  |  |  | 0 | 0 | 672 | 331.442 | 2 | 0 | 662.884 | 445458.048 | 0 | 100 | 100%
57 | 400KV Nagda - Dehgam # 1 |  |  |  |  | 0 | 0 | 672 | 331.442 | 2 | 0 | 662.884 | 445458.048 | 0 | 100 | 100%
58 | 400KV Seoni - Khandwa # 1 | 1 | 3 |  |  | 1.05 | 0 | 672 | 351.729 | 4 | 1477.2618 | 1406.916 | 945447.552 | 0.0015625 | 99.8438 | 99.84%
59 | 400KV Seoni - Khandwa # 2 |  |  |  |  | 0 | 0 | 672 | 351.729 | 4 | 0 | 1406.916 | 945447.552 | 0 | 100 | 100%
60 | 400KV Khandwa - Rajgarh # 2 |  |  |  |  | 0 | 0 | 672 | 220.588 | 2 | 0 | 441.176 | 296470.272 | 0 | 100 | 100%
61 | 400KV Rajgarh - SSP (LILO portion) # 1 |  |  |  |  | 0 | 0 | 672 | 4.01 | 2 | 0 | 8.02 | 5389.44 | 0 | 100 | 100%
62 | 400KV Rajgarh - SSP (LILO portion) # 2 |  |  |  | 10 | 0 | 0.16667 | 671.8333 | 4.01 | 2 | 0 | 8.02 | 5388.1033 | 0 | 100 | 100%
63 | 400KV Rajgarh - Nagda (LILO portion) # 1 |  |  | 51 | 29 | 0 | 51.4833 | 620.5167 | 4.12 | 2 | 0 | 8.24 | 5113.0573 | 0 | 100 | 100%
64 | 400KV Rajgarh - Nagda (LILO portion) # 2 |  |  |  |  | 0 | 0 | 672 | 4.12 | 2 | 0 | 8.24 | 5537.28 | 0 | 100 | 100%
65 | 400KV Khandwa - Rajgarh # 1 |  |  |  |  | 0 | 0 | 672 | 220.588 | 2 | 0 | 441.176 | 296470.272 | 0 | 100 | 100%
66 | 220 KV Vapi - Magarwada # 1 | 5 | 21 |  |  | 5.35 | 0 | 672 | 25.71 | 1 | 137.5485 | 25.71 | 17277.12 | 0.0079613 | 99.2039 | 99.2%
67 | 220 KV Vapi - Magarwada # 2 | 3 | 21 |  |  | 3.35 | 0 | 672 | 25.71 | 1 | 86.1285 | 25.71 | 17277.12 | 0.0049851 | 99.5015 | 99.5%
68 | 220 KV Vapi - Karadpada # 1 |  |  |  |  | 0 | 0 | 672 | 29.66 | 1 | 0 | 29.66 | 19931.52 | 0 | 100 | 100%
69 | 220 KV Vapi - Karadpada # 2 |  |  |  |  | 0 | 0 | 672 | 29.66 | 1 | 0 | 29.66 | 19931.52 | 0 | 100 | 100%
70 | 765 kV Gwalior-Bina # 2 | 0 | 42 |  |  | 0.7 | 0 | 672 | 233.652 | 4 | 654.2256 | 934.608 | 628056.576 | 0.0010417 | 99.8958 | 99.9% | Upgraded to 765kV level w.e.f 01.04.2013
71 | 765 kV Seoni - Bina |  |  |  |  | 0 | 0 | 672 | 292.046 | 4 | 0 | 1168.184 | 785019.648 | 0 | 100 | 100%
72 | 400kV Damoh - Bhopal # 1 |  |  | 0 | 10 | 0 | 0.16667 | 671.8333 | 214.471 | 2 | 0 | 428.942 | 288177.5337 | 0 | 100 | 100%
73 | 400kV Damoh - Bhopal # 2 |  |  |  |  | 0 | 0 | 672 | 213.8 | 2 | 0 | 427.6 | 287347.2 | 0 | 100 | 100%
74 | 220 KV Vapi - Khadoli # 1 |  |  |  |  | 0 | 0 | 672 | 28.549 | 1 | 0 | 28.549 | 19184.928 | 0 | 100 | 100%
75 | 220 KV Vapi - Sayali |  |  |  |  | 0 | 0 | 672 | 18.3 | 1 | 0 | 18.3 | 12297.6 | 0 | 100 | 100%
76 | 220kV Sayali-Khadoli |  |  |  |  | 0 | 0 | 672 | 12.235 | 1 | 0 | 12.235 | 8221.92 | 0 | 100 | 100%
77 | 400kV Damoh-Birsinghpur#1 |  |  |  |  | 0 | 0 | 672 | 228.474 | 2 | 0 | 456.948 | 307069.056 | 0 | 100 | 100%
78 | 400kV Damoh-Birsinghpur#2 |  |  | 0 | 10 | 0 | 0.16667 | 671.8333 | 228.474 | 2 | 0 | 456.948 | 306992.898 | 0 | 100 | 100%
79 | 400kV Dehgam-Pirana#1 |  |  |  |  | 0 | 0 | 672 | 46.67 | 2 | 0 | 93.34 | 62724.48 | 0 | 100 | 100%
80 | 400kV Dehgam-Pirana#2 |  |  |  |  | 0 | 0 | 672 | 46.67 | 2 | 0 | 93.34 | 62724.48 | 0 | 100 | 100%
81 | 400kV Mundra - Bhachau # 1 |  |  |  |  | 0 | 0 | 672 | 99.468 | 3 | 0 | 298.404 | 200527.488 | 0 | 100 | 100%
82 | 400kV Mundra - Bhachau # 2 |  |  |  |  | 0 | 0 | 672 | 99.468 | 3 | 0 | 298.404 | 200527.488 | 0 | 100 | 100%
83 | 400kV Bhachau - Ranchodpura # 1 | 0 | 2 |  |  | 0.033333 | 0 | 672 | 282.856 | 3 | 28.2856 | 848.568 | 570237.696 | 4.9603e-05 | 99.995 | 100%
84 | 400kV Bhachau - Ranchodpura # 2 |  |  |  |  | 0 | 0 | 672 | 282.856 | 3 | 0 | 848.568 | 570237.696 | 0 | 100 | 100%
85 | 400kV Mundra - Limbdi # 1 | 18 | 1 | 12 | 30 | 18.0167 | 12.5 | 659.5 | 314.053 | 3 | 16974.5647 | 942.159 | 621353.8605 | 0.027319 | 97.2681 | 97.27%
86 | 400kV Mundra - Limbdi # 2 |  |  |  |  | 0 | 0 | 672 | 314.053 | 3 | 0 | 942.159 | 633130.848 | 0 | 100 | 100%
87 | 765kV Satna - Bina # 1 |  |  |  |  | 0 | 0 | 672 | 274.164 | 4 | 0 | 1096.656 | 736952.832 | 0 | 100 | 100%
88 | 765kV Satna - Bina # 2 | 5 | 0 |  |  | 5 | 0 | 672 | 275.635 | 4 | 5512.7 | 1102.54 | 740906.88 | 0.0074405 | 99.256 | 99.26%
89 | 765kV Bina - Indore |  |  |  |  | 0 | 0 | 672 | 311.81 | 4 | 0 | 1247.24 | 838145.28 | 0 | 100 | 100% | upgraded to 765kV level w.e.f. 01.07.2013
90 | 400kV Gandhar - Navsari # 2 |  |  |  |  | 0 | 0 | 672 | 102.152 | 2 | 0 | 204.304 | 137292.288 | 0 | 100 | 100%
91 | 400kV Gandhar - Navsari # 1 |  |  |  |  | 0 | 0 | 672 | 102.152 | 2 | 0 | 204.304 | 137292.288 | 0 | 100 | 100%
92 | 400kV Mundra-Jetpur#1 |  |  |  |  | 0 | 0 | 672 | 337 | 3 | 0 | 1011 | 679392 | 0 | 100 | 100%
93 | 400kV Mundra-Jetpur#2 |  |  |  |  | 0 | 0 | 672 | 337 | 3 | 0 | 1011 | 679392 | 0 | 100 | 100%
94 | 400kV V'chal (NTPC) - V'chal (PG) #1 |  |  |  |  | 0 | 0 | 672 | 28.55 | 4 | 0 | 114.2 | 76742.4 | 0 | 100 | 100%
95 | 400kV V'chal (NTPC) - V'chal (PG) #2 |  |  |  |  | 0 | 0 | 672 | 28.55 | 4 | 0 | 114.2 | 76742.4 | 0 | 100 | 100%
96 | 400kV V'chal (Pooling) - Sasan #1 |  |  |  |  | 0 | 0 | 672 | 5.443 | 2 | 0 | 10.886 | 7315.392 | 0 | 100 | 100%
97 | 400k V'chal (Pooling) - Sasan # 2 |  |  |  |  | 0 | 0 | 672 | 5.443 | 2 | 0 | 10.886 | 7315.392 | 0 | 100 | 100%
98 | 765kV Sasan - Satna # 1 |  |  | 3 | 17 | 0 | 3.2833 | 668.7167 | 245.7 | 4 | 0 | 982.8 | 657214.74 | 0 | 100 | 100%
99 | 400kV Bina (PG)-Bina (MPPTCL)#3 |  |  |  |  | 0 | 0 | 672 | 0.62 | 2 | 0 | 1.24 | 833.28 | 0 | 100 | 100% | Commercial operation w.e.f. 01.03.2013
100 | 400kV Vapi-Navsari#1 |  |  |  |  | 0 | 0 | 672 | 116.85 | 2 | 0 | 233.7 | 157046.4 | 0 | 100 | 100% | Commercial operation w.e.f. 01.04.2013
101 | 400kV Vapi-Navsari#2 |  |  |  |  | 0 | 0 | 672 | 116.85 | 2 | 0 | 233.7 | 157046.4 | 0 | 100 | 100%
102 | 765kV Sasan - Satna # 2 |  |  |  |  | 0 | 0 | 672 | 242.23 | 4 | 0 | 968.92 | 651114.24 | 0 | 100 | 100% | Commercial operation w.e.f. 01.05.2013
103 | 400kV Bina (PG)-Bina (MPPTCL)#4 |  |  |  |  | 0 | 0 | 672 | 0.62 | 2 | 0 | 1.24 | 833.28 | 0 | 100 | 100% | Commercial operation w.e.f. 01.06.2013
104 | 400kV Indore (MP)-Indore (PG)#1 |  |  |  |  | 0 | 0 | 672 | 49.726 | 4 | 0 | 198.904 | 133663.488 | 0 | 100 | 100% | Commercial operation w.e.f. 01.07.2013
105 | 400kV Indore (MP)-Indore (PG)#2 |  |  |  |  | 0 | 0 | 672 | 49.726 | 4 | 0 | 198.904 | 133663.488 | 0 | 100 | 100%
106 | 400kV Jabalpur - Jabalpur Pooling#1 |  |  |  |  | 0 | 0 | 672 | 15.456 | 4 | 0 | 61.824 | 41545.728 | 0 | 100 | 100% | Commercial operation w.e.f. 01.01.2014
107 | 400kV Jabalpur - Jabalpur Pooling#2 | 0 | 13 |  |  | 0.21667 | 0 | 672 | 15.456 | 4 | 13.3952 | 61.824 | 41545.728 | 0.00032242 | 99.9678 | 99.97%
108 | 765kV Jabalpur Pooling - Bina # 1 | 2 | 11 | 0 | 10 | 2.1833 | 0.16667 | 671.8333 | 229.74 | 4 | 2006.396 | 918.96 | 617387.96 | 0.0032498 | 99.675 | 99.68%
109 | 765kV Jabalpur Pooling - Bina # 2 |  |  |  |  | 0 | 0 | 672 | 229.74 | 4 | 0 | 918.96 | 617541.12 | 0 | 100 | 100%
| Total Sr.No. 1 to 109 | 50 | 244 | 108 | 439 |  |  |  | 16922.689 |  | 38156.7179 |  | 28016195.4623
* | Lines charged with 400kV level
|  | 54.0667 |  | 115.3167
[10 empty] | NAFM | 0.001362
Availability of ( Sl no 1 to 109) transmission lines during FEBRUARY -2014 = | [9 empty] | TAFM | 99.8638
1 | 765 kV Gwalior -Agra # 1 | 0 | 0 | 4 | 52 | 0 | 4.8667 | 667.1333 | 129.435 | 4 | 0 | 517.74 | 345401.612 | 0 | 100 | 100%
1 | 765 kV Gwalior -Agra # 2 | 0 | 0 | 0 | 0 | 0 | 0 | 672 | 127.934 | 4 | 0 | 511.736 | 343886.592 | 0 | 100 | 100%
Availability of ICTs
Sl. | Name of ICTs | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | ICT | WEIGHT FACTOR |  |  | [THM*MVA*2.5] |  |  | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVA*2.5] | [MVA*2.5]
[6 empty] | POWERGRID | OTHERS | THM | MVA | 2.5 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =28*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | 400/220kV ICT # 1 / Jabalpur. |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
2 | 400/220kV ICT # 2 /Jabalpur. |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
3 | 400/220 KV ICT # 1 / Dehgam |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
4 | 400/220 KV ICT # 2/ Dehgam |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% |  | 0.83333
5 | 400/220kV ICT # 1 / Satna | 1 | 33 |  |  | 1.55 | 0 | 672 | 315 | 2.5 | 1220.625 | 787.5 | 529200 | 0.0023065 | 99.7693 | 99.77%
6 | 400/220kV ICT # 2 / Satna |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
7 | 400/220kV ICT # 1 / Khandwa |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
8 | 400/220kV ICT # 2 / Khandwa |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
9 | 400/220kV ICT # 1 / Vapi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
10 | 400/220kV ICT # 2 / Vapi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
11 | 400/220kV ICT # 1 / Gwalior |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
12 | 400/220 KV ICT # 1 / Rajgarh | 3 | 52 |  |  | 3.8667 | 0 | 672 | 315 | 2.5 | 3045 | 787.5 | 529200 | 0.005754 | 99.4246 | 99.42%
13 | 400/220kV ICT # 2 / Gwalior | 3 | 58 |  |  | 3.9667 | 0 | 672 | 315 | 2.5 | 3123.75 | 787.5 | 529200 | 0.0059028 | 99.4097 | 99.41%
14 | 400/220kV ICT # 1 / Itarsi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
15 | 400/220kV ICT # 1 / Damoh |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
16 | 400/220kV ICT # 2 / Damoh |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
17 | 400/220 KV ICT # 2 / Rajgarh | 2 | 40 |  |  | 2.6667 | 0 | 672 | 315 | 2.5 | 2100 | 787.5 | 529200 | 0.0039683 | 99.6032 | 99.6%
18 | 400/220 KV ICT / Bina |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
19 | 400/220 KV ICT # 1 / Pirana |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
20 | 400/220 KV ICT # 2 / Pirana |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
21 | 400/220 KV ICT # 3 / Gwalior |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
22 | 400/220 KV ICT # 1 / Shujalpur |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
23 | 400/220 KV ICT # 1 / Bhachau |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
24 | 400/220 KV ICT # 2 / Bhachau |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
25 | 400/220 KV ICT # 2 / Shujalpur |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
26 | 765/400KV ICT# 1 / Satna |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100%
27 | 400/220 KV ICT # 2 / Navsari |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
28 | 400/220 KV ICT # 1 / Navsari |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100%
29 | 765/400KV ICT# 2 / Satna |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100%
30 | 765/400KV ICT# 1 / Bina |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.03.2013
31 | 400kV ICT#3/Vapi |  |  |  |  | 0 | 0 | 672 | 315 | 2.5 | 0 | 787.5 | 529200 | 0 | 100 | 100% | Commercial operation w.e.f. 01.04.2013
32 | 765/400KV ICT# 2 / Bina |  |  |  |  | 0 | 0 | 672 | 1000 | 2.5 | 0 | 2500 | 1680000 | 0 | 100 | 100%
33 | 765/400KV ICT# 1 / Gwalior |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100%
34 | 765/400KV ICT# 2 / Gwalior |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100%
35 | 765/400KV ICT# 2 / INDORE |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.07.2013
36 | 765/400KV ICT# 1 / INDORE |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.10.2013
37 | 765/400KV ICT# 1 / JABALPUR POOL |  |  |  |  | 0 | 0 | 672 | 1500 | 2.5 | 0 | 3750 | 2520000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.01.2014
| Total Sr.No. 1 to 37 | 9 | 183 | 0 | 0 |  |  |  | 20320 |  | 9489.375 |  | 34137600
|  | 12.05 |  | 0 | [5 empty] | NAFM | 0.00027797
Availability of 37 ( Sl no 1 to 37) ICTs in FEBRUARY -2014 = | [9 empty] | TAFM | 99.9722
Availability of BUS REACTORS
Sl. | Name of Bus Reactors | Attributed to PGCIL |  | Attributed to Others & Sys. Constraints |  | Outage Hrs | Outage Hrs |  | Bus Reactor | WEIGHT FACTOR | [5 empty] | Element_wise_availability Achieved
No. | [5 empty] | attr. to | attr. to | Individual | Capacity |  | [OH*MVAR*4] | [MVAR *4] | [THM*MVAR *4]
[6 empty] | POWERGRID | OTHERS | THM | MVAR | 4 |  |  |  | NAFM | Availability
|  | Hours | Mints | Hours | Mints |  | OH2 | =28*24-OH2 | [6 empty] | =100-100*O
[6 empty] | Hours | Hours
1 | Bus reactor / Dehgam |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
2 | 25 MVAR reactor # 1 / Jabalpur |  |  |  |  | 0 | 0 | 672 | 25 | 4 | 0 | 100 | 67200 | 0 | 100 | 100%
3 | 25 MVAR reactor # 2 / Jabalpur |  |  |  |  | 0 | 0 | 672 | 25 | 4 | 0 | 100 | 67200 | 0 | 100 | 100%
4 | Bus reactor # 1 / Itarsi |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100%
5 | Bus reactor # 2 / Itarsi |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100%
6 | Bus Reactor # 3 / Itarsi |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100%
7 | Bus Reactor # 3 / Jabalpur |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
8 | Bus Reactor / Dhule |  |  |  |  | 0 | 0 | 672 | 80 | 4 | 0 | 320 | 215040 | 0 | 100 | 100%
9 | Bus Reactor-I (50 MVAR) / Satna |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100%
10 | Bus Reactor # 1 (63 MVAR) / Bina |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
11 | Bus Reactor / Damoh |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
12 | Bus Reactor-I / Gwalior |  |  |  |  | 0 | 0 | 672 | 50 | 4 | 0 | 200 | 134400 | 0 | 100 | 100%
13 | Bus Reactor / Khandwa |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100%
14 | Bus Reactor / Dehgam |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100%
15 | Bus Reactor / Bhachau |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
16 | Bus Reactor / Shujalpur |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
17 | Bus Reactor/ Rajgarh |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100%
18 | Bus Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100%
19 | Bus Reactor / Navsari |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
20 | Switchable Bina-I Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100%
21 | Switchable Bina-II Line Reactor / Satna 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | Commercial operation w.e.f. 01.04.2013
22 | Bus Reactor-II (63 MVAR)/Satna |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
23 | Switchable Bina-I Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100%
24 | Switchable Bina-II Line Reactor / Gwalior 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100%
25 | Switchable Shujalpur-I Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100% | Commercial operation w.e.f. 01.06.2013
26 | Switchable Shujalpur-II Line Reactor / Nagda (MPPTCL) 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
27 | Bus Reactor-II/Gwalior |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100% | Commercial operation w.e.f. 01.10.2013
28 | Bus Reactor-III/Gwalior |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100%
29 | Bus Reactor-I/Indore |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100%
30 | Switchable Indore - Line Reactor / Bina 765KV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100%
31 | Switchable Shujalpur-II Line Reactor / Bina 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
32 | Switchable Shujalpur-I Line Reactor / Bina 400kV |  |  |  |  | 0 | 0 | 672 | 63 | 4 | 0 | 252 | 169344 | 0 | 100 | 100%
33 | Bus Reactor-I / Indore 765kV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | Commercial operation w.e.f. 01.11.2013
34 | Switchable Bina - I Line Reactor / Jabalpur Pooling 765kV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100% | Commercial operation w.e.f. 01.01.2014
35 | Bus Reactor 400kV / Jabalpur Pool 765kV |  |  |  |  | 0 | 0 | 672 | 125 | 4 | 0 | 500 | 336000 | 0 | 100 | 100%
36 | Bus Reactor-I / Bina 765kV |  |  |  |  | 0 | 0 | 672 | 240 | 4 | 0 | 960 | 645120 | 0 | 100 | 100%
| Total of sl no 1 to 36 | 0 | 0 | 0 | 0 |  |  |  | 4171 |  | 0 |  | 11211648
|  | 0 |  | 0
[8 empty] | NAFM | 0
Availability of 36 ( Sl no 1 to 36) Bus Reactors in FEBRUARY -2014 = | [7 empty] | TAFM | 100
[11 empty] | 47646.0929 |  | 73365443.4623
[8 empty] | NAFM = | 0.00064944
% System Availability for FEBRUARY -2014 = | [5 empty] | TAFM= (100-100*NAFM) = |  |  | 99.9351
Note on B26: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B27: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B28: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B29: kdomewale: LILO AT KHANDWA ON 17.12.04
Note on B142: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004
Note on B143: kdomewale: 315 MVA ICT # 1 CHARGED ON 17/12/2004

## ANX-II
MONTH : FEBRUARY 2014
II. Elements where restoration time has exceeeded the standards specified in Regulation 5 (b).
SN | Element Name | Rstoration time as specified in Regulation 5(b) ( In Days) | Actual Restoration time
NIL

## Anx-III
MONTH : FEBRUARY 2014
III. Details of compensation paid by the inter-State transmission licensee.
Element Name | Violation of Regulation 5(a) |  | Violation of Regulation 5(b) |  | Compensation paid (in Rs)
| % Availability prescribed | Actual % Availability | Restoration time prescribed (in Days) | Actual restoration time ( in Days)
Total=

## ANX-V
V. Data to be complied by the inter-State Transmission Licensees
FEBRUARY 2014
Sl. No. | Name of Elements | Type of failures | Restoration Time (Days) |  |  | Remarks
A |  | Elements of transmission line for Single, Double and Multi circuit towers for each JV class seperately.
1 |  | Insualtor Failure | Terrain Type
|  |  | Plain | River bed | Hilly
i | KHANDWA-DHULE II 400kV | Insualtor Failure in single phase | Less than 1 day
ii |  | Insualtor Failure in two phases
ii |  | Insualtor Failure in three phases
2 |  | Tower after collapse by Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
3 |  | Tower after collapse without Emergency Restoration System (ERS) for S/C,D/C & M/C seperately.
4 |  | Tower Damage ( not collapse)
i |  | One arm damage
ii |  | Two arm damage
5 |  | Snapping of phase conductor
i | MUNDRA-LIMBDI I 400kV | Conductor snapping in single phase | Less than 1 day
ii |  | Conductor snapping in two phases
iii |  | Conductor snapping in three phases
6 |  | Failure of Earth wire
7 |  | Insulator failure with conductor snapping
8 |  | Any other combination of failures
B |  | Elements of sub-station for each KV class seperately
1 |  | Failure of Inter Connecting Transformers (ICTs)
Restoration of failed ICT
|  | Other major failures in ICTs | Single phase Unit |  | Three phase Unit
|  | (i) Replacement of faulty bushings | NIL
(ii) Replacement of failed/blasted bushings
(iii) Replacement of faulty tap changers
2 |  | Failures of Reactors
Restoration of failed Reactors

## Supporting Annex V
Supporting Annex V
TRIPPING DETAILS OF WRTS-II FOR THE MONTH OF FEBRUARY 2014
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | Outage Category | Details | WRLDC CODE FOR |  | Outage in Days |  |  | REMARKS
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING | Flashover | Snapping | Collapes of Tower
1 | 902035 | KHANDWA-DHULE II 400kV | 2014-02-06 | 17:46 | 2014-02-07 | 12:38 | 0.28611 | - | - | - | LHWT | A/T on R-ph to E/F, F/L - 147.5kM from Khandwa SS due to failure of R-ph inner V-string at Loc-768. The outage period from 19:00 hrs / 06.02.14 to 07:00 hrs / 07.02.14 may not be attributed to Powergrid due to poor visibility & rainy site condition. Fault jurisdiction comes under WRTS#1 portion. |  | LD 02/663 | 0.28611
2 | 902130 | MUNDRA-LIMBDI I 400kV | 2014-02-26 | 07:19 | 2014-02-27 | 13:50 | 0.75069 | - | - | - | LHWT | A/T on R&Y Ph. to ph fault, F/L - Mundra- 235KM & Limdi-98.6KM. Top Phase Conductor Snapped between location 592-593. Restoration was delayed due to poor visibility. Outage from 18:30 hrs / 26.02.14 to 07:00 hrs / 27.02.14 may not be attributed to POWERGRID. |  | LD 02/3004 |  | 0.75069