## Tripping details JULY (hidden)
TRIPPING DETAILS OF WR-II FOR THE MONTH OF JULY' 2011
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | CAT. CODE | Details | WRLDC CODE FOR
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING
1 | 904070 | DAMOH-BHOPAL I 400KV | 2011-04-25 | 16:51 | 2011-04-25 | 16:51 | - | - | - | 9.7022e-13 | LVRD | Line H/T for Voltage Regulation as per WRLDC instruction. | LD 04/1432
2 | 904078 | DAMOH-BHOPAL II 400KV | 2011-04-26 | 17:54 | 2011-04-26 | 17:54 | - | - | - | -3.2337e-12 | LVRD | Line H/T for Voltage Regulation. | LD 04/1494
3 | 905010 | DAMOH BIRSINGHPUR II 400kV | 2011-05-02 | 15:05 | 2011-05-02 | 15:05 | - | - | - | -3.2337e-12 | LVRD | Line Kept out for voltage regulation on WRLDC Instruction. | LD 05 /83
4 | 905019 | DAMOH BIRSINGHPUR I 400kV | 2011-05-07 | 9:41 | 2011-05-07 | 9:41 | - | - | - | -1.7786e-12 | LVRD | Line H/T for Voltage Regulation. | LD/ 05/342
5 | 905114 | RAJGARH-NAGDA I 400kV | 2011-05-30 | 11:30 | 2011-05-30 | 11:30 | - | - | - | -2.4253e-12 | LVRD | Line H/T for Voltage Regulation. | LD 05/1718
6 | 906020 | NAGDA-DEHGAM II 400kV | 2011-06-04 | 5:07 | 2011-06-04 | 5:07 | - | - | - | -3.5571e-12 | LVRD | Line H/T for Voltage Regulation. | LD 06/189
7 | 906042 | SATNA-BINA(PG) I 400kV | 2011-06-08 | 18:17 | 2011-06-08 | 18:17 | - | - | 2.1019e-12 | - | LNCC | A/T on R- Ph to E/F due to Tower collapse at Loc No. 565 (A Type) due to heavy wind F/L - 57kM (Bina) & 78.9% (Satna)
8 | 906048 | KHANDWA-RAJGARH I 400kV | 2011-06-09 | 3:32 | 2011-06-09 | 3:32 | - | - | - | -3.2338e-13 | LVRD | Line kept out on O/V on WRLDC instruction. | LD 06/491
9 | 906068 | BINA-SHUJALPUR#1 400kV | 2011-06-15 | 6:00 | 2011-06-15 | 6:00 | - | - | 0 | - | GOVC | A/T on operation of O/V Protection at Shujalpur.Line kept out on O/V from 06:05hrs/15.06.11 vide ,WRLDC CODE LD 06/839
10 | 906069 | SHUJALPUR - NAGDA I 400kV | 2011-06-15 | 6:50 | 2011-06-15 | 6:50 | - | - | - | -3.2337e-12 | LVRD | Line H/T for Voltage regulation | LD 06/841
11 | 906072 | ITARSI-KHANDWA II 400kV | 2011-06-16 | 4:10 | 2011-06-16 | 4:10 | - | - | - | -1.6169e-12 | LVRD | Line H/T for Voltage regulation | LD 06/894
12 | 906089 | SHUJALPUR-NAGDA II 400kV | 2011-06-18 | 8:20 | 2011-06-18 | 8:20 | - | - | - | -3.2338e-12 | LVRD | Line H/T for voltage regulation | LD 06/1043
13 | 906093 | 220 kV KAWAS-HALDARWA # 1 | 2011-06-20 | 16:29 | 2011-06-20 | 16:29 | - | - | - | -2.2636e-12 | LPRD | H/T to control overloading of 220KV Kawas-icchapur line. | LD 06/1168
14 | 906095 | JABALPUR-ITARSI IV 400kV | 2011-06-21 | 17:38 | 2011-06-21 | 17:38 | - | - | - | 1.1319e-12 | LVRD | Line H/T for voltage regulation | LD 06/1225
15 | 906104 | 400/220 kV ICT BINA | 2011-06-24 | 8:20 | 2011-06-24 | 8:20 |  |  |  |  | SPRD | ICT H/T for Power Regulation due to non availibility of load . | LD 06/1364
16 | 906109 | VINDHYACHAL-JABALPUR III 400kV | 2011-06-24 | 22:07 | 2011-06-24 | 22:07 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1409
17 | 906121 | VINDHYACHAL-SATNA IV 400KV | 2011-06-26 | 7:04 | 2011-06-26 | 7:04 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1489
18 | 906124 | SEONI-BINA I(400kV) 765kV | 2011-06-26 | 8:04 | 2011-06-26 | 8:04 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1494
19 | 906125 | KHANDWA-RAJGARH II 400kV | 2011-06-27 | 0:11 | 2011-06-27 | 0:11 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1536
20 | 906133 | SARDAR SAROVAR-RAJGARH I 400kV | 2011-06-29 | 8:15 | 2011-06-29 | 8:15 |  |  |  |  | OSPD | H/T to avail S/D by GETCO. | LD 06/1649
21 | 906141 | KAWAS-ICHCHAPUR 220kV | 2011-06-30 | 17:30 | 2011-06-30 | 17:30 |  |  |  |  | OSPD | Line H/T to avail outage by NTPC for attending Hot Point at Kawas S/s. | LD 06/1740
22
23
24
25
26
27
28
29
30
31
32
33
34
34
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
Formulas:
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT. CODE, row below],1)="D"),[RESTORATION DATE, row below]+[RESTORATION TIME, row below]-[TRIPPING DATE, row below]-[TRIPPING TIME, row below],"-")
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT. CODE],1)="D"),[RESTORATION DATE]+[RESTORATION TIME]-[TRIPPING DATE]-[TRIPPING TIME],"-")

## List (hidden)
220 kV GANDHAR-HALDARWA # 1
220 kV GANDHAR-HALDARWA # 2
220 kV ICHCHAPUR-VAV
220 kV KAKRAPAR-HALDARWA # 1
220 kV KAKRAPAR-HALDARWA # 2
220 kV KAKRAPAR-VAPI # 1
220 kV KAKRAPAR-VAPI # 2
220 kV KAKRAPAR-VAV # 1
220 kV KAKRAPAR-VAV # 2
220 kV KAWAS-HALDARWA # 1
220 kV KAWAS-HALDARWA # 2
220 kV KAWAS-ICHCHAPUR
220 kV KAWAS-NAVSARI # 1
220 kV KAWAS-NAVSARI # 2
220 kV KAWAS-VAV # 1
220 kV VAPI-KHADOLI # 1
220 kV VAPI-KHADOLI#2
220 kV VAPI-KHARADPARA # 1
220 kV VAPI-KHARADPARA # 2
220 kV VAPI-MAGARWADA # 1
220 kV VAPI-MAGARWADA # 2
33 kV BUS REACTOR JABALPUR # 1
33 kV BUS REACTOR JABALPUR # 2
400 kV BINA(PG)-BINA(MPEB) # 1
400 kV BINA(PG)-BINA(MPEB) # 2
400 kV BINA-NAGDA # 1
400 kV BINA-NAGDA # 2
400 kV BUS REACTOR, BINA
400 kV BUS REACTOR, DAMOH
400 kV BUS REACTOR, DEHGAM
400 kV BUS REACTOR, GWALIOR
400 kV BUS REACTOR, ITARSI # 1
400 kV BUS REACTOR, ITARSI # 2
400 kV BUS REACTOR, ITARSI # 3
400 kV BUS REACTOR, JABALPUR # 3
400 kV BUS REACTOR, SATNA
400 kV DAMOH-BHOPAL # 1
400 kV DAMOH-BHOPAL # 2
400 kV GANDHAR(NTPC)-GANDHAR(GTEC)
400 kV GANDHAR-DEHGAM # 1
400 kV GANDHAR-DEHGAM # 2
400 kV GANDHAR-SUGEN # 1
400 kV GANDHAR-SUGEN # 2
400 kV INDORE-ASOJ # 1
400 kV INDORE-ASOJ # 2
400 kV JABALPUR-ITARSI # 1
400 kV JABALPUR-ITARSI#2
400 kV JABALPUR-ITARSI#3
400 kV JABALPUR-ITARSI#4
400 kV KHANDWA-DHULE#1
400 kV KHANDWA-DHULE#2
400 kV KHANDWA-RAJGARH#1
400 kV KHANDWA-RAJGARH#2
400 kV NAGDA-DEHGAM#1
400 kV NAGDA-DEHGAM#2
400 kV RAJGARH-NAGDA#1
400 kV RAJGARH-NAGDA#2
400 kV SARDAR SAROVAR-RAJGARH#1
400 kV SARDAR SAROVAR-RAJGARH#2
400 kV SATNA-BINA(PG)#1
400 kV SATNA-BINA(PG)#2
400 kV SATNA-BINA(PG)#3
400 kV SATNA-BINA(PG)#4
400 kV SATPURA-ITARSI
400 kV SEONI-KHANDWA#1
400 kV SEONI-KHANDWA#2
400 kV VAPI-SUGEN
400 kV VINDHYACHAL-JABALPUR#1
400 kV VINDHYACHAL-JABALPUR#2
400 kV VINDHYACHAL-JABALPUR#3
400 kV VINDHYACHAL-JABALPUR#4
400 kV VINDHYACHAL-SATNA#1
400 kV VINDHYACHAL-SATNA#2
400 kV VINDHYACHAL-SATNA#3
400 kV VINDHYACHAL-SATNA#4
400 kV#1TARSI-INDORE#1
400 kV#1TARSI-INDORE#2
400 kV#1TARSI-KHANDWA#1
400 kV#1TARSI-KHANDWA#2
400/220 kV ICT ITARSI
400/220 kV ICT#1 DAMOH
400/220 kV ICT#1 DEHGAM
400/220 kV ICT#1 GWALIOR
400/220 kV ICT#1 JABALPUR
400/220 kV ICT#1 KHANDWA
400/220 kV ICT#1 RAJGARH
400/220 kV ICT#1 SATNA
400/220 kV ICT#1 VAPI
400/220 kV ICT#2 DAMOH
400/220 kV ICT#2 DEHGAM
400/220 kV ICT#2 GWALIOR
400/220 kV ICT#2 JABALPUR
400/220 kV ICT#2 KHANDWA
400/220 kV ICT#2 RAJGARH
400/220 kV ICT#2 SATNA
400/220 kV ICT#2 VAPI
765 kV AGRA-GWALIOR#1 (400 kV)
765 kV AGRA-GWALIOR#2 (400 kV)
765 kV BINA-GWALIOR#1 (400 kV)
765 kV BINA-GWALIOR#2 (400 kV)
765 kV SEONI-BINA (400 kV)

## code (hidden)
POWER GRID CORPORATION OF INDIA LIMITED
400 / 220 kV SUB-STATION, JABALPUR
STANDARD LIST OF ELEMENT OUTAGE CATEGORIES
CATEGORY | Paertaining to | TYPE OF OUTAGE
GGDC | SYSTEM CONSTRAINTS | Power swings / trippings due to Grid disturbance / Under frequency islanding trippings / Reverse power flow blocking related tripping / Hand tripping due to loss of voltage
GOFC | SYSTEM CONSTRAINTS | ICT tripping on over fluxing
GOLC | SYSTEM CONSTRAINTS | ICT tripping on over loading / over-current
GOMD | SYSTEM CONSTRAINTS | Unable to restore after any outage ( other than grid disturbance ), due to system constraint
GOVC | SYSTEM CONSTRAINTS | Tripping on Over Voltage protection
LART | LINE FAULTS ON LINES OWNED BY POWERGRID | Auto Re-closure due to Earth faults
LCSD | OUTAGE OF ELEMENTS UNDER O&M TO FASCILITATE THE CONSTRUCTION ACTIVITIES OF NEW SYSTEM EXECUTED BY POWERGRID | Line shutdown taken to fascilitate construction activities of new system being executed by POWERGRID
LEFT | LINE FAULTS ON LINES OWNED BY POWERGRID | Tripping due to Earth faults
LHWT | LINE FAULTS ON LINES OWNED BY POWERGRID | Faults due to snapping of conductors, earth wire, jumper, insulator failure, failure of tower due to design & material deficiency etc.
LMAC | SYSTEM OUTAGE CAUSED BY MISCREANTS / MILITANT ACTIVITIES | Line breakdown caused by miscreants / militant activities
LNCC | OUTAGE OF SYSTEM DUE TO NATURAL CALAMITIES | Line outage due to Natural calamities
LPPT | LINE FAULTS ON LINES OWNED BY POWERGRID | Phase to phase faults, double line to Earth faults, 3-ph and 3-ph reath faults, but not due to Power Swings.
LPRD | SYSTEM CONSTRAINTS | Line hand tripped for Power Regulation on RLDC instruction
LVRD | SYSTEM CONSTRAINTS | Line hand tripped for Voltage Regulation on RLDC instruction
OMST | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Miscellaneous outages attributable to POWERGRID
OMSU | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Miscellaneous outages attributable to Other agency or force majeure condition.
OSFD | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Forced shutdown availed by other agency / agencies causing outage of POWERGRID element.
OSFT | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Forced shutdown ( e.g. E/W snapping / hotspots )
OSPD | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Planned shutdown availed by other agency / agencies for maintenance or construction of their transmission system causing outage of POWERGRID element.
OSPT | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Planned shutdown for maintenance work of POWERGRID elements
SBBT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Busbar protection operation (POWERGRID Substation only including the fault initiated in POWERGRID owned by other agency
SBBU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Busbar protection operation
SCSD | OUTAGE OF ELEMENTS UNDER O&M TO FASCILITATE THE CONSTRUCTION ACTIVITIES OF NEW SYSTEM EXECUTED BY POWERGRID | Substation equipment shutdown taken to fascilitate construction activities of new system being executed by POWERGRID
SEFT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Equipment failure
SEFU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Equipment failure
SEMT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Equipment Mal-operation
SEMU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Equipment Mal-operation
SICT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | REF, Differential, Buchholz protection operation, PRV, OTI, WTI on ICT
SICU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | REF, Differential, Buchholz protection operation, PRV, OTI, WTI on ICT
SMAC | SYSTEM OUTAGE CAUSED BY MISCREANTS / MILITANT ACTIVITIES | Substation equipment failure caused by miscreants / militant activities
SNCC | OUTAGE OF SYSTEM DUE TO NATURAL CALAMITIES | Substation equipment outage due to Natural calamities
SPLT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Line tripped due to PLCC mal-operation
SPLU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Line tripped due to PLCC mal-operation of other agency
SPRD | SYSTEM CONSTRAINTS | Transformer hand tripped for Power Regulation on RLDC instruction
SRET | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Reactor Differential, REF, Backup impedance, Buchholz protection including NGR protections
SREU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Reactor Differential, REF, Backup impedance, Buchholz protection including NGR protections
SRMT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Relay Mal-operation
SRMU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Relay Mal-operation
SVRD | SYSTEM CONSTRAINTS | Bus reactor hand tripped for Voltage Regulation on RLDC instruction

## Tripping Report
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., WETSTERN REGION - II
Month: NOVEMBER 2014
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  |  |  |  | Total outage in days (1) | Durationn of outage attributable to (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (in days) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | no. of insulator failed | No. of towers damaged | Snapping of phase conductor | Failure of earth wire | Failure of Bushing |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | WR2L1 | SATPURA-ITARSI 400kV | 79 | WR-II | -- | 2014-11-27 | 09:41 | 2014-11-27 | 21:42 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.02 | -- | -- | -- | Line H/T to avail OCC approved S/D by MPPTCL for crossing work of Sarni - Astha Line. | Agency: WRPC Mumbai | 100%
2 | WR2L2 | ITARSI-INDORE I 400kV | 207 | WR-II | -- | 2014-11-26 | 10:37 | 2014-11-26 | 10:49 | -- | -- | -- | -- | -- | -- | 0.2 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D by Power Grid for isolation of Line Reactor at Indore(MP) for DGA & Bushing oil sampling. |  | 99.95%
| WR2L2 | ITARSI-INDORE I 400kV | 207 | WR-II | -- | 2014-11-26 | 16:01 | 2014-11-26 | 16:11 | -- | -- | -- | -- | -- | -- | 0.17 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D by Power Grid to take into service Line Reactor at Indore(MP) which was taken out for DGA & Bushing oil sampling.
3 | WR2L3 | ITARSI-INDORE II 400kV | 214 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
4 | WR2L4 | INDORE-ASOJ I 400kV | 289 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
5 | WR2L5 | INDORE-ASOJ II 400kV | 273 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
6 | WR2L6 | VINDHYACHAL-JABALPUR I 400kV | 360 | WR-II | -- | 2014-11-13 | 12:08 | 2014-11-13 | 17:24 | -- | -- | -- | -- | -- | -- | 5.27 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for rectification of Hot Spot. |  | 99.27%
7 | WR2L7 | VINDHYACHAL-JABALPUR II 400kV | 360 | WR-II | -- | 2014-11-19 | 10:31 | 2014-11-19 | 13:52 | -- | -- | -- | -- | -- | -- | 3.35 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for rectification of hot spot observed during Thermo-vision scanning. |  | 98.74%
| WR2L7 | VINDHYACHAL-JABALPUR II 400kV | 360 | WR-II | -- | 2014-11-23 | 20:03 | 2014-11-24 | 01:45 | -- | -- | -- | -- | -- | -- | 5.7 | 0 | 0 | 0 | -- | -- | -- | Line A/T on B-ph to R-ph Fault. F/L:0.5Km from Jabalpur S/S. B-ph jumper snapped and fell on R-ph at dead end tower of Jabalpur SS.
8 | WR2L8 | JABALPUR-ITARSI I 400kV | 232 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
9 | WR2L9 | JABALPUR-ITARSI II 400kV | 232 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
10 | WR2L10 | GANDHAR-DEHGAM I 400kV | 157 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
11 | WR2L11 | GANDHAR-DEHGAM II 400kV | 157 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
13 | WR2L13 | VINDHYACHAL-SASAN III 400kV | 21 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
14 | WR2L14 | SASAN-JABALPUR 400kV | 368 | WR-II | -- | 2014-11-23 | 10:34 | 2014-11-24 | 18:46 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.2 | -- | -- | -- | Line H/T for OCC approved S/D for line crossing work of 765kV V'chal Pooling -Satna # 1,2. |  | 100%
15 | WR2L15 | VINDHYACHAL-JABALPUR IV 400kV | 389 | WR-II | -- | 2014-11-23 | 10:08 | 2014-11-24 | 18:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.4 | -- | -- | -- | Line H/T for OCC approved S/D for line crossing work of 765kV V'chal Pooling -Satna # 1,2. |  | 100%
16 | WR2L16 | JABALPUR-ITARSI III 400kV | 234 | WR-II | -- | 2014-11-03 | 12:13 | 2014-11-03 | 12:18 | -- | -- | -- | -- | -- | -- | 0.08 | 0 | 0 | 0 | -- | -- | -- | S/D availed by Jabalpur S/S to take out L/R for arresting oil Leakage from Neutral CT. Line taken into service without line reactor at Jabalpur. |  | 99.99%
17 | WR2L17 | JABALPUR-ITARSI IV 400kV | 234 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
18 | WR2L18 | ITARSI-KHANDWA I 400kV | 196.64 | WR-II | -- | 2014-11-05 | 09:32 | 2014-11-05 | 18:47 | -- | -- | -- | -- | -- | -- | 9.25 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for attending Hot spot in Y & B phase isolator connector at Khandwa end. |  | 98.72%
| WR2L18 | ITARSI-KHANDWA I 400kV | 196.64 | WR-II | -- | 2014-11-25 | 10:54 | 2014-11-25 | 20:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.67 | -- | -- | -- | Line H/T to avail OCC approved S/D by MPPTCL for crossing work of Sarni - Astha Line.
19 | WR2L19 | ITARSI-KHANDWA II 400kV | 196.64 | WR-II | -- | 2014-11-14 | 09:32 | 2014-11-14 | 17:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.92 | -- | -- | -- | Line H/T for rectification work of OPGW strand cut. |  | 100%
| WR2L19 | ITARSI-KHANDWA II 400kV | 196.64 | WR-II | -- | 2014-11-25 | 11:38 | 2014-11-25 | 20:49 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.18 | -- | -- | -- | Line H/T to avail OCC approved S/D by MPPTCL for crossing work of Sarni - Astha Line.
20 | WR2L20 | KHANDWA-DHULE I 400kV | 261.78 | WR-II | -- | 2014-11-08 | 12:49 | 2014-11-08 | 14:01 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.2 | -- | -- | -- | Line A/T on Y-ph to E/F during OPGW stringing near Khandwa SS due to slippage of earthwire from the OPGW suspension clamp . F/L - 0.9kMs from Khandwa. |  | 100%
21 | WR2L21 | KHANDWA-DHULE II 400kV | 261.78 | WR-II | -- | 2014-11-11 | 17:22 | 2014-11-11 | 17:22 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Auto-reclosed successfully at both ends on B ph to E/F, F/L 66.7km from Khandwa F/C:4.24kA. |  | 99.02%
| WR2L21 | KHANDWA-DHULE II 400kV | 261.78 | WR-II | -- | 2014-11-28 | 14:38 | 2014-11-28 | 21:40 | -- | -- | -- | -- | -- | -- | 7.03 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for replacement of broken insulator string at location no. 553.
22 | WR2L22 | GANDHAR-SUGEN 400kV | 57 | WR-II | -- | 2014-11-17 | 09:04 | 2014-11-19 | 17:54 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 56.83 | -- | -- | -- | Line H/T to avail OCC Approved S/D by NTPC. |  | 100%
23 | WR2L23 | SUGEN-VAPI 400kV | 110 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
24 | WR2L24 | GANDHAR(NTPC)-GANDHAR(GTEC) 400kV | 13 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
25 | WR2L25 | GANDHAR-HALDARWA I 220kV | 13 | WR-II | -- | 2014-11-24 | 09:00 | 2014-11-26 | 20:50 | -- | -- | -- | -- | -- | -- | 0 | 59.83 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by NTPC. |  | 100%
26 | WR2L26 | GANDHAR-HALDARWA II 220kV | 13 | WR-II | -- | 2014-11-20 | 09:10 | 2014-11-22 | 18:40 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 57.5 | -- | -- | -- | Line H/T to avail S/D by NTPC for CVT replacement. |  | 100%
27 | WR2L27 | KAWAS-NAVSARI(GIS) I 220kV | 58.15 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
28 | WR2L28 | KAWAS-NAVSARI(GIS) II 220kV | 58.15 | WR-II | -- | 2014-11-25 | 10:14 | 2014-11-25 | 13:35 | -- | -- | -- | -- | -- | -- | 3.35 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Y & B Ph to Ph fault, 20.89km from Navsari, F/C: 7.1kA. No abnormality found duirng patrolling |  | 99.53%
29 | WR2L29 | NAVSARI(GIS)-NAVSARI I 220kV | 31.33 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
30 | WR2L30 | NAVSARI(GIS)-NAVSARI II 220kV | 31.33 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
31 | WR2L31 | KAWAS-VAV I 220kV | 37 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
32 | WR2L32 | KAWAS-VAV II 220kV | 37 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
33 | WR2L33 | KAWAS-HALDARWA I 220kV | 81 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
34 | WR2L34 | KAWAS-HALDARWA II 220kV | 81 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
35 | WR2L35 | KAKRAPAR-HALDARWA I 220kV | 74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
36 | WR2L36 | KAKRAPAR-HALDARWA II 220kV | 74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
37 | WR2L37 | KAKRAPAR-VAV I 220kV | 43 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
38 | WR2L38 | KAKRAPAR-VAV II 220kV | 43 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
39 | WR2L39 | KAKRAPAR-VAPI I 220kV | 117 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
40 | WR2L40 | KAKRAPAR-VAPI II 220kV | 117 | WR-II | -- | 2014-11-15 | 16:03 | 2014-11-15 | 17:40 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.62 | -- | -- | -- | Line H/T to avail S/D by GETCO. |  | 100%
41 | WR2L41 | VINDHYACHAL-SATNA I 400kV | 267 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
42 | WR2L42 | VINDHYACHAL-SATNA II 400kV | 267 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
43 | WR2L43 | VINDHYACHAL-SATNA III 400kV | 258.31 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
44 | WR2L44 | VINDHYACHAL-SATNA IV 400kV | 258.31 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
47 | WR2L45 | SATNA-BINA I 400kV | 276 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
48 | WR2L46 | SATNA-BINA II 400kV | 276 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
49 | WR2L47 | BINA-BINA(MP) I 400kV | 0.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
50 | WR2L48 | BINA-BINA(MP) II 400kV | 0.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
51 | WR2L49 | BINA-GWALIOR I 765kV | 234.931 | WR-II | -- | 2014-11-04 | 10:11 | 2014-11-06 | 17:43 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 55.53 | -- | -- | -- | Line H/T to avail OCC Approved S/D for commissioning of Spare Reactor at Gwalior. |  | 100%
52 | WR2L50 | AGRA-GWALIOR I 765kV | 129.435 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
53 | WR2L51 | SATNA-BINA IV 400kV | 272.586 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
54 | WR2L52 | SATNA-BINA III 400kV | 272.586 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
55 | WR2L53 | BINA-SHUJALPUR I 400kV | 199.936 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
56 | WR2L54 | BINA-SHUJALPUR II 400kV | 199.936 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
57 | WR2L55 | SHUJALPUR-NAGDA I 400kV | 152.229 | WR-II | -- | 2014-11-24 | 12:24 | 2014-11-24 | 14:42 | -- | -- | -- | -- | -- | -- | 0 | 0 | 2.3 | 0 | -- | -- | -- | Line Auto tripped as Polythene was Entangled Between R & Y Ph at location no. 508/1 near Shujalpur Sub-Station. |  | 100%
58 | WR2L56 | SHUJALPUR-NAGDA II 400kV | 152.229 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
59 | WR2L57 | NAGDA-DEHGAM II 400KV | 331.442 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
60 | WR2L58 | NAGDA-DEHGAM I 400KV | 331.442 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
61 | WR2L59 | SEONI-KHANDWA I 400kV | 351.729 | WR-II | -- | 2014-11-10 | 10:17 | 2014-11-10 | 17:49 | -- | -- | -- | -- | -- | -- | 7.53 | 0 | 0 | 0 | -- | -- | -- | H/T to avail S/D by PG for rectification of damaged condutor. |  | 98.93%
| WR2L59 | SEONI-KHANDWA I 400kV | 351.729 | WR-II | -- | 2014-11-11 | 21:02 | 2014-11-11 | 21:10 | -- | -- | -- | -- | -- | -- | 0.13 | 0 | 0 | 0 | -- | -- | -- | Line H/T for isolation of Line reactor at Khandwa end due to DGA violation in Y phase Bushing.
62 | WR2L60 | SEONI-KHANDWA II 400kV | 351.729 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
63 | WR2L61 | KHANDWA-RAJGARH II 400kV | 220.588 | WR-II | -- | 2014-11-16 | 17:43 | 2014-11-17 | 09:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 15.73 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
64 | WR2L62 | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 4.01 | WR-II | -- | 2014-10-27 | 07:01 | 2014-11-04 | 00:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 72.25 | -- | -- | -- | H/T to avail emergency S/D for rectification of snapped OPGW E/W at Loc no. 477-478 which broken during installation of OPGW. PTW returned by POWERGRID by 14:04hrs/28.10.14. Further line kept out for voltage regulation as per WRLDC Instructions. |  | 100%
|  | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-09 | 12:41 | 2014-11-09 | 22:08 | -- | -- | -- | -- | -- | -- | 0 | 9.45 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by MPPTCL.
|  | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-10 | 08:04 | 2014-11-10 | 19:20 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.27 | -- | -- | -- | S/D availed by MPPTCL for line maintenance works.
|  | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-10 | 19:20 | 2014-11-13 | 20:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 72.67 | -- | -- | -- | Line kept out on Voltage regulation as per instruction of WRLDC.
|  | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-15 | 07:10 | 2014-11-18 | 09:08 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 73.97 | -- | -- | -- | S/D availed by MPPTCL for line maintenance works.
|  | SARDAR SAROVAR-RAJGARH I 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-29 | 10:25 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 37.58 | -- | -- | -- | Line H/T to avail S/D by MPPTCL.
65 | WR2L63 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-02 | 18:01 | 2014-11-02 | 19:29 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.47 | 0 | -- | -- | -- | A/T on operation of O/V stage - I Protection at Rajgarh S/S. |  | 100%
| WR2L63 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-10 | 20:06 | 2014-11-10 | 21:57 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.85 | 0 | -- | -- | -- | Line A/T on operation of O/V stage - I protection at SSP end.
| WR2L63 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-13 | 19:38 | 2014-11-13 | 19:48 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.17 | 0 | -- | -- | -- | Line A/T on Operation of O/V stage-I protection at SSP end.
| WR2L63 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-13 | 19:48 | 2014-11-15 | 06:55 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 35.12 | -- | -- | -- | After tripping on O/V Line kept out on Voltage regulation as per WRLDC instruction.
| WR2L63 | SARDAR SAROVAR-RAJGARH II 400kV(LILO) | 4.01 | WR-II | -- | 2014-11-18 | 09:34 | 2014-11-29 | 08:49 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 263.25 | -- | -- | -- | Line H/T to avail OCC approved S/D by MPPTCL.
66 | WR2L64 | RAJGARH-NAGDA I 400kV(LILO) | 4.12 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
67 | WR2L65 | RAJGARH-NAGDA II 400kV(LILO) | 4.12 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
68 | WR2L66 | KHANDWA-RAJGARH I 400kV | 220.588 | WR-II | -- | 2014-11-11 | 20:42 | 2014-11-12 | 05:47 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.08 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
| WR2L66 | KHANDWA-RAJGARH I 400kV | 220.588 | WR-II | -- | 2014-11-20 | 21:37 | 2014-11-22 | 11:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 37.68 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions.
| WR2L66 | KHANDWA-RAJGARH I 400kV | 220.588 | WR-II | -- | 2014-11-28 | 23:54 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 48.1 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions.
69 | WR2L67 | VAPI-MAGARWADA I 220kV | 25.71 | WR-II | -- | 2014-11-18 | 09:02 | 2014-11-20 | 13:56 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 52.9 | -- | -- | -- | Line H/T to avail OCC approved S/D by DD Magarwada for Bay shifting of Vapi-I &II feeders at Magarwada. |  | 100%
|  |  | 25.71 | WR-II | -- | 2014-11-20 | 14:59 | 2014-11-20 | 16:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.58 | -- | -- | -- | Line H/T to avail OCC approved S/D by DD Magarwada for Bay shifting of Vapi-I &II feeders at Magarwada.
|  |  | 25.71 | WR-II | -- | 2014-11-28 | 07:26 | 2014-11-28 | 18:51 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.42 | -- | -- | -- | H/T to avail OCC Approved S/D by DD for Bay Shifting work at 220kV Magarwada S/S.
70 | WR2L68 | VAPI-MAGARWADA II 220kV | 25.71 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
71 | WR2L69 | VAPI-KHARADPARA I 220kV | 29.66 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
72 | WR2L70 | VAPI-KHARADPARA II 220kV | 29.66 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
73 | WR2L71 | BINA-GWALIOR II 765kV | 233.652 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
74 | WR2L72 | AGRA-GWALIOR II 765kV | 127.934 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
75 | WR2L73 | SEONI-BINA I 765kV | 292.046 | WR-II | -- | 2014-11-21 | 15:08 | 2014-11-21 | 15:29 | -- | -- | -- | -- | -- | -- | 0.35 | 0 | 0 | 0 | -- | -- | -- | Line A/T at Seoni end only due to DT sent from Bina end. |  | 99.95%
76 | WR2L74 | DAMOH-BHOPAL I 400KV | 214.471 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
77 | WR2L75 | DAMOH-BHOPAL II 400KV | 213.8 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
78 | WR2L76 | VAPI-KHADOLI I 220kV | 28.549 | WR-II | Insulator Flash over | 2014-11-13 | 20:52 | 2014-11-14 | 11:32 | Insulator Flash over at loc. No.56. | -- | -- | -- | -- | 0.61125 | 14.67 | 0 | 0 | 0 | 1 | N | -- | Line A/T on R-ph to E/F due to insulator string flashover at location no. 58 , F/L- 15.47 km, F/C-6.6 kA from Vapi end. |  | 97.96%
80 | WR2L77.1 | VAPI-SAYALI 220kV | 18.3 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
81 | WR2L77.2 | SAYALI-KHADOLI 220kV | 12.235 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
82 | WR2L78 | DAMOH-BIRSINGHPUR I 400kV | 228.474 | WR-II | -- | 2014-11-13 | 12:46 | 2014-11-13 | 15:44 | -- | -- | -- | -- | -- | -- | 0 | 0 | 2.97 | 0 | -- | -- | -- | Line A/T on operation of O/V stage-I protection at Birsinghpur, on loss of Generation due to blasting of 220kV CT at Birsinghpur end. |  | 98.77%
|  |  | 228.474 | WR-II | -- | 2014-11-14 | 10:23 | 2014-11-14 | 19:13 | -- | -- | -- | -- | -- | -- | 8.83 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D for AMP work.
83 | WR2L79 | DAMOH-BIRSINGHPUR II 400kV | 228.474 | WR-II | -- | 2014-11-13 | 12:46 | 2014-11-13 | 12:56 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.17 | 0 | -- | -- | -- | Line A/T on operation of O/V stage-I protection at Birsinghpur, on loss of Generation due to blasting of 220kV CT at Birsinghpur end. After tripping on O/V Line kept out on Voltage regulation as per WRLDC instruction. |  | 98.74%
|  |  | 228.474 | WR-II | -- | 2014-11-13 | 12:56 | 2014-11-14 | 10:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 21.3 | -- | -- | -- | Line A/T on operation of O/V stage-I protection at Birsinghpur, on loss of Generation due to blasting of 220kV CT at Birsinghpur end. After tripping on O/V Line kept out on Voltage regulation as per WRLDC instruction.
|  |  | 228.474 | WR-II | -- | 2014-11-16 | 09:51 | 2014-11-16 | 18:54 | -- | -- | -- | -- | -- | -- | 9.05 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D for line and bay AMP work.
|  |  | 228.474 | WR-II | -- | 2014-11-19 | 13:36 | 2014-11-22 | 06:02 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 64.43 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions.
84 | WR2L80 | DEHGAM-PIRANA I 400kV | 46.656 | WR-II | -- | 2014-11-26 | 10:14 | 2014-11-27 | 20:51 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34.62 | -- | -- | -- | Line H/T to avail OCC approved S/D for NTAMC work. |  | 100%
85 | WR2L81 | DEHGAM-PIRANA II 400kV | 46.656 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
86 | WR2L82 | MUNDRA-BHACHAU I 400kV | 99.468 | WR-II | -- | 2014-11-11 | 17:26 | 2014-11-11 | 19:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.67 | -- | -- | -- | To avail emergency S/D for removal of Stuck up Traction machine during OPGW laying work. |  | 100%
87 | WR2L83 | MUNDRA-BHACHAU II 400kV | 99.468 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
88 | WR2L84 | BHACHAU-RANCHHODPURA I 400kV | 282.856 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
89 | WR2L85 | BHACHAU-RANCHHODPURA II 400kV | 282.856 | WR-II | -- | 2014-11-30 | 21:42 | 2014-11-30 | 22:02 | -- | -- | -- | -- | -- | -- | 0 | 0.33 | 0 | 0 | -- | -- | -- | Line A/T at Ranchodpura end only due to CB maleoperation. Line remained charged from Bhachau end. |  | 100%
90 | WR2L86 | MUNDRA-LIMBDI I 400kV | 314.053 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
91 | WR2L87 | MUNDRA-LIMBDI II 400kV | 314.053 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
92 | WR2L88 | SATNA-BINA I 765kV | 274.164 | WR-II | -- | 2014-11-19 | 09:25 | 2014-11-19 | 20:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.9 | -- | -- | -- | Line H/T to avail OCC approved S/D for Erection of new TC & TE tower for NHPTL. |  | 100%
93 | WR2L89 | SATNA-BINA II 765kV | 275.635 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
94 | WR2L90 | BINA-INDORE I 765kV | 311.81 | WR-II | -- | 2014-11-17 | 09:27 | 2014-11-18 | 20:58 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 35.52 | -- | -- | -- | Line H/T to avail OCC approved S/D for NGR replacement wokrs. |  | 100%
95 | WR2L91 | GANDHAR-NAVSARI(GIS) II 400kV | 102.152 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
96 | WR2L92 | GANDHAR-NAVSARI(GIS) I 400kV | 102.152 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
97 | WR2L93 | MUNDRA-JETPUR I 400kV | 336.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
98 | WR2L94 | MUNDRA-JETPUR II 400kV | 336.742 | WR-II | -- | 2014-11-22 | 18:37 | 2014-11-22 | 18:50 | -- | -- | -- | -- | -- | -- | 0.22 | 0 | 0 | 0 | -- | -- | -- | Line A/T on R & Y ph to Ph due to snapping of one of subconductor jumper at loc.no. 404 Fault. F/L - 163.3kms from Mundra & 194.07kms from Jetpur end. Line Charging delayed due to CB problem at Jetpur end. |  | 99.39%
| WR2L94 |  | 336.742 | WR-II | -- | 2014-11-22 | 18:50 | 2014-11-22 | 21:49 | -- | -- | -- | -- | -- | -- | 0 | 2.98 | 0 | 0 | -- | -- | -- | Line A/T on R & Y ph to Ph due to snapping of one of subconductor jumper at loc.no. 404 Fault. F/L - 163.3kms from Mundra & 194.07kms from Jetpur end. Line Charging delayed due to CB problem at Jetpur end.
| WR2L94 |  | 336.742 | WR-II | -- | 2014-11-30 | 10:24 | 2014-11-30 | 14:34 | -- | -- | -- | -- | -- | -- | 4.17 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D by Powergrid to attend hot spot.
99 | WR2L95 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) I 400kV | 28.55 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
100 | WR2L96 | VINDHYACHAL(NTPC)-VINDHYACHAL(PG) II 400kV | 28.55 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
101 | WR2L97 | VINDHYACHAL(POOLING)-SASAN I 400kV | 5.443 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
102 | WR2L98 | VINDHYACHAL(POOLING)-SASAN II 400kV | 5.443 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
103 | WR2L99 | SASAN-SATNA I 765kV | 245.7 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
104 | WR2L100 | BINA-BINA(MP) III 400kV | 0.62 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
106 | WR2L101.1 | NAVSARI(GIS)-KALA I 400kV | 140 | WR-II | -- | 2014-11-02 | 08:37 | 2014-11-02 | 23:28 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.85 | -- | -- | -- | H/T to avail OCC S/D by PG for making of LILO of line for Commissioning of 400/220kV Magarwada GIS S/S. |  | 100%
107 | WR2L101.1.1 | NAVSARI(GIS)-MAGARWADA 400kV | 125.8 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
108 | WR2L101.1.2 | KALA-MAGARWADA 400kV | 52.9 | WR-II | -- | 2014-11-15 | 09:42 | 2014-11-15 | 18:09 | -- | -- | -- | -- | -- | -- | 8.45 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by WRTS - I for line maintenance work |  | 98.4%
109 | WR2L101.2 | KALA-VAPI I 400kV | 49 | WR-II | -- | 2014-11-02 | 08:36 | 2014-11-02 | 19:05 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.48 | -- | -- | -- | H/T to avail OCC S/D by PG for making LILO of line for Commissioning of 400/220kV Magarwada GIS S/S. |  | 100%
110 | WR2L102 | VAPI-NAVASARI(GIS) II 400kV | 116.879 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
111 | WR2L103 | SASAN-SATNA II 765kV | 242.23 | WR-II | -- | 2014-11-15 | 08:13 | 2014-11-15 | 20:47 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.57 | -- | -- | -- | Line H/T to avail OCC approved S/D By Relaince Power for construction work at Sasan. |  | 100%
112 | WR2L104 | BINA-BINA(MP) IV 400kV | 0.62 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
113 | WR2L105 | INDORE(MP)-INDORE I 400kV | 49.73 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
114 | WR2L106 | INDORE(MP)-INDORE II 400kV | 49.73 | WR-II | -- | 2014-11-17 | 15:38 | 2014-11-17 | 16:57 | -- | -- | -- | -- | -- | -- | 1.32 | 0 | 0 | 0 | -- | -- | -- | Line A/T at Indore(PG) end only due to operation of Master trip relay 86 A & B. |  | 99.82%
115 | WR2L107 | JABALPUR-JABALPUR(POOLING) I 400kV | 15.456 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
116 | WR2L108 | JABALPUR-JABALPUR(POOLING) II 400kV | 15.456 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
117 | WR2L109 | JABALPUR(POOLING)-BINA I 765kV | 229.74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
118 | WR2L110 | JABALPUR(POOLING)-BINA II 765kV | 229.74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
119 | WR2L111 | SATNA-GWALIOR I 765kV | 336.63 | WR-II | -- | 2014-11-08 | 21:13 | 2014-11-08 | 21:39 | -- | -- | -- | -- | -- | -- | 0.43 | 0 | 0 | 0 | -- | -- | -- | Line A/T at Satna end only due to Mal-operation of Main - I Relay at Satna on Through Fault. |  | 99.94%
120 | WR2L112 | PIRANA-ASOJ I 400KV | 143.539 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
121 | WR2L113 | PIRANA-ASOJ II 400KV | 143.539 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
122 | WR2L114 | INDORE-ASOJ III 400kV | 321.203 | WR-II | -- | 2014-11-11 | 20:57 | 2014-11-11 | 22:33 | -- | -- | -- | -- | -- | -- | 0 | 1.6 | 0 | 0 | -- | -- | -- | Line A/T at Indore(MP) end only due to reciept of D/T from Asoj. Line was charged from Asoj end, Charging code was delayed by WRLDC. |  | 100%
123 | WR2L115 | BINA-GWALIOR III 765kV | 231.27 | WR-II | -- | 2014-11-12 | 08:35 | 2014-11-13 | 19:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34.87 | -- | -- | -- | Line H/T to avail OCC approved S/D for Spare reactor commissioning at Gwalior. |  | 100%
124 | WR2L116 | SATNA-GWALIOR II 765kV | 342.15 | WR-II | -- | 2014-10-31 | 12:30 | 2014-11-01 | 02:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 2.32 | -- | -- | -- | Line H/T to avail OCC Approved S/D for SCADA testing at Gwalior. |  | 100%
124 | WR2L116 | SATNA-GWALIOR II 765kV | 342.15 | WR-II | -- | 2014-11-01 | 10:34 | 2014-11-03 | 21:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 59.18 | -- | -- | -- | Line H/T to avail OCC Approved S/D for commissioning of Spare Reactor at Gwalior. |  | 100%
124 | WR2L116 | SATNA-GWALIOR II 765kV | 342.15 | WR-II | -- | 2014-11-26 | 09:47 | 2014-11-27 | 21:56 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.15 | -- | -- | -- | H/T to avail OCC approved S/D for spare reactor commissioning at Gwalir end. |  | 100%
125 | WR2L117 | ANUPPUR-JABALPUR(POOLING) I 400kV | 246.409 | WR-II | -- | 2014-09-11 | 10:58 |  |  | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 720 | -- | -- | -- | After tripping on O/V Line kept out on Voltage regulation as per WRLDC instruction. |  | 100%
126 | WR2L118 | ANUPPUR-JABALPUR(POOLING) II 400kV | 246.409 | WR-II | -- | 2014-08-08 | 10:40 |  |  | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 720 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
127 | WR2T1 | ICT1 JABALPUR 400/220kV | 315 | WR-II | -- | 2014-11-20 | 11:10 | 2014-11-20 | 14:49 | -- | -- | -- | -- | -- | -- | 3.65 | 0 | 0 | 0 | -- | -- | -- | H/T for rectification of oil leakage from inspection chamber. |  | 99.49%
128 | WR2T2 | ICT2 JABALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
129 | WR2T3 | ICT1 DEHGAM 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
130 | WR2T4 | ICT2 DEHGAM 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
131 | WR2T5 | ICT1 SATNA 400/220kV | 315 | WR-II | -- | 2014-11-18 | 20:56 | 2014-11-18 | 22:36 | -- | -- | -- | -- | -- | -- | 1.67 | 0 | 0 | 0 | -- | -- | -- | H/T to avail S/D for attending broken 220kV side Y phase Tension string. |  | 99.77%
132 | WR2T6 | ICT2 SATNA 400/220KV | 315 | WR-II | -- | 2014-11-19 | 12:40 | 2014-11-22 | 21:55 | -- | -- | -- | -- | -- | -- | 81.25 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D for rectification of oil mixing problem of OLTC with main Tank. |  | 88.72%
133 | WR2T7 | ICT1 KHANDWA 400/220kV | 315 | WR-II | -- | 2014-11-03 | 12:04 | 2014-11-03 | 16:13 | -- | -- | -- | -- | -- | -- | 4.15 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D for taking oil sample of L/R Bushings for DGA testing. |  | 99.42%
134 | WR2T8 | ICT2 KHANDWA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
135 | WR2T9 | ICT1 VAPI 400/220KV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
136 | WR2T10 | ICT2 VAPI 400/220KV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
137 | WR2T11 | ICT1 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
138 | WR2T12 | ICT1 RAJGARH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
139 | WR2T13 | ICT2 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
140 | WR2T14 | ICT ITARSI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
141 | WR2T15 | ICT1 DAMOH 400/220kV | 315 | WR-II | -- | 2014-11-12 | 13:24 | 2014-11-12 | 16:33 | -- | -- | -- | -- | -- | -- | 3.15 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D for bushing oil sampling. |  | 99.56%
142 | WR2T16 | ICT2 DAMOH 400/220kV | 315 | WR-II | -- | 2014-11-12 | 10:24 | 2014-11-12 | 13:05 | -- | -- | -- | -- | -- | -- | 2.68 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D for bushing oil sampling. |  | 99.63%
143 | WR2T17 | ICT2 RAJGARH 400/220KV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
144 | WR2T18 | ICT1 BINA 400/220kV | 315 | WR-II | -- | 2014-11-05 | 10:50 | 2014-11-05 | 17:55 | -- | -- | -- | -- | -- | -- | 7.08 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D for AMP works. |  | 99.02%
145 | WR2T19 | ICT1 PIRANA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
146 | WR2T20 | ICT2 PIRANA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
147 | WR2T21 | ICT3 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
148 | WR2T22 | ICT1 SHUJALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
149 | WR2T23 | ICT1 BHACHAU 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
150 | WR2T24 | ICT2 BHACHAU 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
151 | WR2T25 | ICT2 SHUJALPUR 400/220kV | 315 | WR-II | -- | 2014-11-28 | 13:37 | 2014-11-28 | 18:04 | -- | -- | -- | -- | -- | -- | 4.45 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC Approved S/D for AMP. |  | 99.38%
152 | WR2T26 | ICT1 SATNA 765/400KV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
153 | WR2T27 | ICT2 NAVSARI(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
154 | WR2T28 | ICT1 NAVSARI(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
155 | WR2T29 | ICT2 SATNA 765/400KV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
156 | WR2T30 | ICT1 BINA 765/400KV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
157 | WR2T31 | ICT3 VAPI 400/220KV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
158 | WR2T32 | ICT2 BINA 765/400KV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
159 | WR2T33 | ICT1 GWALIOR 765/400KV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
160 | WR2T34 | ICT2 GWALIOR 765/400KV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
161 | WR2T35 | ICT2 INDORE 765/400KV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
162 | WR2T36 | ICT1 INDORE 765/400KV | 1500 | WR-II | -- | 2014-11-05 | 10:55 | 2014-11-05 | 17:58 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.05 | -- | -- | -- | H/T to avail OCC approved S/D for rerouting of MCB cable for commissioning of spare unit. |  | 100%
163 | WR2T37 | ICT1 JABALPUR 765/400KV | 1500 | WR-II | -- | 2014-11-21 | 10:45 | 2014-11-21 | 22:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.57 | -- | -- | -- | H/T H/T to avail OCC approved S/D for Erection of 765KV & 400KV Auxiliary Bus for Spare ICT Phase. |  | 100%
164 | WR2T38 | ICT2 JABALPUR 765/400KV | 1500 | WR-II | -- | 2014-11-22 | 10:43 | 2014-11-22 | 23:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.03 | -- | -- | -- | H/T to avail OCC approved S/D for Erection of 765KV & 400KV Auxiliary Bus for Spare ICT Phase. |  | 100%
165 | WR2T39 | ICT1 KALA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
166 | WR2T40 | ICT2 KALA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
167 | WR2T41 | ICT3 NAVSARI(GIS) 400/220kV | 500 | WR-II | -- | 2014-11-22 | 10:20 | 2014-11-23 | 17:56 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 31.6 | -- | -- | -- | OCC Approved S/D availed for rectification of construction defects. |  | 100%
168 | WR2T42 | ICT1 MAGARWADA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
169 | WR2T43 | ICT2 MAGARWADA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
170 | WR2R1 | BUS REACTOR I DEHGAM 400kV | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
171 | WR2R2 | BUS REACTOR I JABALPUR 33kV | 25 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
172 | WR2R3 | BUS REACTOR II JABALPUR 33kV | 25 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
173 | WR2R4 | BUS REACTOR I ITARSI 400kV | 125 | WR-II | -- | 2014-11-03 | 14:24 | 2014-11-03 | 18:08 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.73 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
174 | WR2R5 | BUS REACTOR II ITARSI 400kV | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
175 | WR2R6 | BUS REACTOR III ITARSI 400kV | 50 | WR-II | -- | 2014-11-21 | 10:18 | 2014-11-21 | 15:12 | -- | -- | -- | -- | -- | -- | 4.9 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC Approved S/D for AMP works. |  | 99.32%
176 | WR2R7 | BUS REACTOR I JABALPUR 400kV | 63 | WR-II | -- | 2014-11-14 | 10:35 | 2014-11-15 | 21:05 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34.5 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
177 | WR2R8 | BUS REACTOR DHULE 400kV | 80 | WR-II | -- | 2014-11-01 | 11:02 | 2014-11-01 | 17:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.55 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  |  | 80 | WR-II | -- | 2014-11-02 | 06:40 | 2014-11-02 | 21:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.57 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-03 | 05:23 | 2014-11-03 | 17:26 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.05 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-04 | 05:05 | 2014-11-04 | 17:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.37 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-05 | 09:33 | 2014-11-05 | 18:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.75 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-06 | 10:14 | 2014-11-06 | 17:44 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.5 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-07 | 10:03 | 2014-11-07 | 18:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.27 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-09 | 14:47 | 2014-11-09 | 16:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.47 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-10 | 06:44 | 2014-11-10 | 17:33 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.82 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-11 | 06:35 | 2014-11-11 | 20:16 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.68 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-12 | 09:13 | 2014-11-12 | 17:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.1 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-13 | 09:35 | 2014-11-13 | 17:41 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.1 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-14 | 11:22 | 2014-11-14 | 16:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 5.03 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-24 | 09:28 | 2014-11-24 | 17:17 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.82 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-26 | 10:36 | 2014-11-26 | 17:23 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.78 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-27 | 10:54 | 2014-11-27 | 18:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.2 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-28 | 11:19 | 2014-11-28 | 19:21 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.03 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 80 | WR-II | -- | 2014-11-30 | 10:35 | 2014-11-30 | 17:47 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.2 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
178 | WR2R9 | BUS REACTOR I SATNA 400kV | 50 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
179 | WR2R10 | BUS REACTOR I BINA 400kV | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
180 | WR2R11 | BUS REACTOR I DAMOH 400kV | 63 | WR-II | -- | 2014-11-25 | 11:52 | 2014-11-27 | 20:33 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 56.68 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
181 | WR2R12 | BUS REACTOR I GWALIOR 400kV | 125 | WR-II | -- | 2014-11-22 | 09:25 | 2014-11-24 | 00:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 38.98 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
182 | WR2R13 | BUS REACTOR I KHANDWA 400kV | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
183 | WR2R14 | BUS REACTOR II DEHGAM 400kV | 125 | WR-II | -- | 2014-11-10 | 11:23 | 2014-11-27 | 19:53 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 416.5 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
184 | WR2R15 | BUS REACTOR I BHACHAU 400kV | 63 | WR-II | -- | 2014-11-10 | 11:19 | 2014-11-15 | 21:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 129.92 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
185 | WR2R16 | BUS REACTOR I SHUJALPUR 400kV | 63 | WR-II | -- | 2014-11-11 | 06:50 | 2014-11-19 | 21:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 206.62 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  |  | 63 | WR-II | -- | 2014-11-22 | 08:56 | 2014-11-22 | 12:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.32 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 63 | WR-II | -- | 2014-11-23 | 11:55 | 2014-11-27 | 20:33 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 104.63 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 63 | WR-II | -- | 2014-11-30 | 09:20 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.67 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
186 | WR2R17 | BUS REACTOR I RAJGARH 400kV | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
187 | WR2R18 | BUS REACTOR I NAVSARI 400kV | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
188 | WR2R19 | BUS REACTOR II SATNA 400kV | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
189 | WR2R20 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT NAGDA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
190 | WR2R21 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT NAGDA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
191 | WR2R22 | BUS REACTOR II GWALIOR 400kV | 125 | WR-II | -- | 2014-11-14 | 11:32 | 2014-11-15 | 19:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.05 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  |  | 125 | WR-II | -- | 2014-11-22 | 08:45 | 2014-11-23 | 00:46 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 16.02 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
192 | WR2R23 | BUS REACTOR III GWALIOR 400kV | 125 | WR-II | -- | 2014-11-14 | 11:32 | 2014-11-15 | 19:44 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.2 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
193 | WR2R24 | BUS REACTOR I INDORE 400kV | 125 | WR-II | -- | 2014-11-03 | 12:26 | 2014-11-10 | 21:57 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 177.52 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  |  | 125 | WR-II | -- | 2014-11-12 | 06:48 | 2014-11-14 | 17:48 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 59 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 125 | WR-II | -- | 2014-11-21 | 09:53 | 2014-11-22 | 18:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.37 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 125 | WR-II | -- | 2014-11-27 | 12:14 | 2014-11-27 | 16:42 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 4.47 | -- | -- | -- | Reactor H/T for volatge Regulation on WRLDC Instruction
|  |  | 125 | WR-II | -- | 2014-11-29 | 08:42 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 39.3 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
194 | WR2R25 | SWITCHABLE LINE REACTOR SHUJALPUR II 400kV AT BINA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
195 | WR2R26 | SWITCHABLE LINE REACTOR SHUJALPUR I 400kV AT BINA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
196 | WR2R27 | BUS REACTOR I JABALPUR(POOLING) 400kV | 125 | WR-II | -- | 2014-11-29 | 09:52 | 2014-11-29 | 17:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.32 | -- | -- | -- | Reactor H/T to avail OCC Approved S/D for construction work of new BR # 2. |  | 100%
197 | WR2R28 | BUS REACTOR II KHANDWA 400kV | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
198 | WR2R29 | BUS REACTOR II JABALPUR 400kV | 125 | WR-II | -- | 2014-11-02 | 10:36 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 685.4 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
199 | WR2R30 | BUS REACTOR I SATNA 765kV | 240 | WR-II | -- | 2014-11-27 | 10:36 | 2014-11-27 | 18:29 | -- | -- | -- | -- | -- | -- | 7.88 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC Approved S/D for AMP. |  | 98.91%
200 | WR2R31 | SWITCHABLE LINE REACTOR BINA I 765kV AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
201 | WR2R32 | SWITCHABLE LINE REACTOR BINA II 765kV AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
202 | WR2R33 | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-03 | 06:50 | 2014-11-03 | 18:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.27 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-04 | 07:18 | 2014-11-04 | 21:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.1 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-05 | 10:05 | 2014-11-05 | 20:55 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.83 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-06 | 09:19 | 2014-11-09 | 17:25 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 80.1 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-10 | 10:10 | 2014-11-10 | 20:55 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.75 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-11 | 05:10 | 2014-11-11 | 12:38 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.47 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-12 | 06:26 | 2014-11-12 | 16:42 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.27 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-13 | 07:07 | 2014-11-13 | 18:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.47 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-14 | 09:17 | 2014-11-14 | 20:10 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.88 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-15 | 10:49 | 2014-11-15 | 19:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.75 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-16 | 06:55 | 2014-11-16 | 16:16 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.35 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-17 | 15:16 | 2014-11-18 | 19:26 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 28.17 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-18 | 23:24 | 2014-11-21 | 20:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 68.9 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-22 | 06:44 | 2014-11-22 | 21:13 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.48 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-23 | 07:42 | 2014-11-23 | 21:02 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.33 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-24 | 06:29 | 2014-11-24 | 20:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.08 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-25 | 06:56 | 2014-11-25 | 20:53 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.95 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-26 | 07:20 | 2014-11-27 | 20:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.97 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  | BUS REACTOR I INDORE 765kV | 240 | WR-II | -- | 2014-11-28 | 06:54 | 2014-11-29 | 18:26 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 35.53 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
203 | WR2R34 | SWITCHABLE LINE REACTOR BINA I 765kV AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
204 | WR2R35 | SWITCHABLE LINE REACTOR BINA II 765kV AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
205 | WR2R36 | SWITCHABLE LINE REACTOR INDORE 765kV AT BINA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
206 | WR2R37 | SWITCHABLE LINE REACTOR BINA I 765kV AT JABALPUR (POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
207 | WR2R38 | BUS REACTOR I BINA 765kV | 240 | WR-II | -- | 2014-11-12 | 06:59 | 2014-11-12 | 19:17 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.3 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  |  | 240 | WR-II | -- | 2014-11-15 | 12:56 | 2014-11-15 | 16:30 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.57 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 240 | WR-II | -- | 2014-11-20 | 07:55 | 2014-11-21 | 20:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.7 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 240 | WR-II | -- | 2014-11-23 | 07:34 | 2014-11-23 | 20:48 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.23 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 240 | WR-II | -- | 2014-11-30 | 09:49 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 14.18 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
208 | WR2R39 | SWITCHABLE LINE REACTOR BINA II 765kV AT JABALPUR (POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
209 | WR2R40 | BUS REACTOR II JABALPUR POOLING 765kV | 240 | WR-II | -- | 2014-11-01 | 08:10 | 2014-11-03 | 21:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 61.37 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
| WR2R40 | BUS REACTOR II JABALPUR POOLING 765kV | 240 | WR-II | -- | 2014-11-04 | 07:37 | 2014-11-05 | 20:17 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.67 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R40 | BUS REACTOR II JABALPUR POOLING 765kV | 240 | WR-II | -- | 2014-11-06 | 09:19 | 2014-11-06 | 20:21 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.03 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R40 | BUS REACTOR II JABALPUR POOLING 765kV | 240 | WR-II | -- | 2014-11-10 | 14:44 | 2014-11-10 | 20:26 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 5.7 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R40 | BUS REACTOR II JABALPUR POOLING 765kV | 240 | WR-II | -- | 2014-11-11 | 07:10 | 2014-11-29 | 20:12 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 445.03 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R40 | BUS REACTOR II JABALPUR POOLING 765kV | 240 | WR-II | -- | 2014-11-30 | 08:20 | 2014-11-30 | 20:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.85 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
210 | WR2R41 | SWITCHABLE LINE REACTOR GWALIOR III 765kV AT BINA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
211 | WR2R42 | SWITCHABLE LINE REACTOR GWALIOR I 765kV AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
212 | WR2R43 | SWITCHABLE LINE REACTOR JAIPUR I 765kV AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
213 | WR2R44 | BUS REACTOR I KALA(GIS) 400kV | 80 | WR-II | -- | 2014-11-02 | 11:12 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 684.8 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
214 | WR2R45 | BUS REACTOR II INDORE 400kV | 63 | WR-II | -- | 2014-11-03 | 12:02 | 2014-11-08 | 20:52 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 128.83 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
|  |  | 63 | WR-II | -- | 2014-11-09 | 07:08 | 2014-11-14 | 17:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 130.7 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 63 | WR-II | -- | 2014-11-17 | 09:44 | 2014-11-22 | 18:23 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 128.65 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 63 | WR-II | -- | 2014-11-24 | 10:28 | 2014-11-26 | 19:58 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 57.5 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
|  |  | 63 | WR-II | -- | 2014-11-30 | 06:56 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 17.07 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
215 | WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-02 | 09:01 | 2014-11-02 | 19:41 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.67 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-03 | 07:13 | 2014-11-03 | 18:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.37 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-06 | 11:10 | 2014-11-06 | 21:12 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.03 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-07 | 09:31 | 2014-11-07 | 19:54 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.38 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-08 | 09:35 | 2014-11-10 | 17:31 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 55.93 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-11 | 06:40 | 2014-11-17 | 19:49 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 157.15 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-18 | 13:48 | 2014-11-18 | 20:03 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.25 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-19 | 07:48 | 2014-11-20 | 18:20 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34.53 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-22 | 08:16 | 2014-11-23 | 18:16 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-24 | 06:40 | 2014-11-24 | 18:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.9 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R46 | BUS REACTOR II INDORE 765kV | 240 | WR-II | -- | 2014-11-27 | 07:30 | 2014-11-30 | 18:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 83.12 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
216 | WR2R47 | BUS REACTOR II SHUJALPUR 400kV | 125 | WR-II | -- | 2014-11-03 | 06:48 | 2014-11-12 | 19:20 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 228.53 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
| WR2R47 | BUS REACTOR II SHUJALPUR 400kV | 125 | WR-II | -- | 2014-11-17 | 09:37 | 2014-11-23 | 20:22 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 154.75 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R47 | BUS REACTOR II SHUJALPUR 400kV | 125 | WR-II | -- | 2014-11-26 | 06:50 | 2014-11-27 | 19:38 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.8 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
| WR2R47 | BUS REACTOR II SHUJALPUR 400kV | 125 | WR-II | -- | 2014-11-28 | 06:59 | 2014-11-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 65.02 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction.
217 | WR2R48 | SWITCHABLE LINE REACTOR GWALIOR II 765kV AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
218 | WR2R49 | BUS REACTOR I GWALIOR 765kV | 240 | WR-II | -- | 2014-11-22 | 08:50 | 2014-11-23 | 00:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 15.57 | -- | -- | -- | Reactor H/T for voltage regulation as per WRLDC Instruction. |  | 100%
219 | WR2R50 | BUS REACTOR II DAMOH 400kV | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
220 | WR2R51 | BUS REACTOR I PIRANA 400kV | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
221 | WR2R52 | SWITCHABLE LINE REACTOR BINA III (IPTC) 765kV AT JABALPUR (POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
222 | WR2R53 | SWITCHABLE LINE REACTOR BHOPAL I 765kV AT JABALPUR (POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
223 | WR2R54 | SWITCHABLE LINE REACTOR JAIPUR II 765kV AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%