## 1504 WR 2
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., WETSTERN REGION - II
Month: APRIL 2015
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  |  |  |  | Total outage in days (1) | Durationn of outage attributable to (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (in days) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | no. of insulator failed | No. of towers damaged | Snapping of phase conductor | Failure of earth wire | Failure of Bushing |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | WR2L1 | 400kV SATPURA-ITARSI | 79 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Agency: WRPC Mumbai | 100%
2 | WR2L2 | 400kV ITARSI-INDORE(MP) 1 | 207 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
3 | WR2L3 | 400kV ITARSI-INDORE(MP) 2 | 214 | WR-II | -- | 2015-04-30 | 16:15 | 2015-04-30 | 16:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R successfully from both ends on Y-ph to E/F, F/L Itarsi -77.98kms & Indore -131.8kms. |  | 100%
4 | WR2L4 | 400kV INDORE(MP)-ASOJ 1 | 289 | WR-II | -- | 2015-04-01 | 9:33 | 2015-04-01 | 15:57 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.4 | -- | -- | -- | H/T to avail S/D by GETCO. |  | 100%
5 | WR2L5 | 400kV INDORE(MP)-ASOJ 2 | 273 | WR-II | -- | 2015-04-02 | 08:25 | 2015-04-02 | 15:42 | -- | -- | -- | -- | -- | -- | 0 | 7.28 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by GETCO. |  | 98.05%
5 | WR2L5 | 400kV INDORE(MP)-ASOJ 2 | 273 | WR-II | Insulator Failure | 2015-04-28 | 12:56 | 2015-04-29 | 02:50 | 01 no. insulator failure at loc. No. 206. | -- | -- | -- | -- | 0.57917 | 13.9 | 0 | 0 | 0 | 1 | N | -0.42083 | Line A/T on B phase to E/F, F/L - 70.5km from Indore due to failure of insulator string at Location no: 206. |  | 98.05%
6 | WR2L6 | 400kV VINDHYACHAL-JABALPUR 1 | 360 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
7 | WR2L7 | 400kV VINDHYACHAL-JABALPUR 2 | 360 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
8 | WR2L8 | 400kV JABALPUR-ITARSI 1 | 232 | WR-II | -- | 2015-04-06 | 09:24 | 2015-04-08 | 0:49 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 39.42 | -- | -- | -- | Line H/T for construction works by JTCL. |  | 97.69%
8 | WR2L8 | 400kV JABALPUR-ITARSI 1 | 232 | WR-II | -- | 2015-04-11 | 16:29 | 2015-04-11 | 17:56 | -- | -- | -- | -- | -- | -- | 1.45 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Y & B ph-ph fault. F/L-162kms from Jabalpur. F/C - 3.2kAmp(Y-ph) & 3.09kAmp(B-ph). |  | 97.69%
8 | WR2L8 | 400kV JABALPUR-ITARSI 1 | 232 | WR-II | -- | 2015-04-20 | 20:15 | 2015-04-21 | 11:27 | -- | -- | -- | -- | -- | -- | 15.2 | 0 | 0 | 0 | -- | -- | -- | Line A/T on B-ph to E/F, F/L - 109.2kms from Itarsi & 101.5km from Jabalpur. Line test charged at 20:30Hrs but A/T on SOTF, again test charged at 23:32hrs but A/T on Y&B phase to phase fault, F/L-164.3km from Jabalpur. Special patrolling carried out but no abnormality was found. |  | 97.69%
9 | WR2L9 | 400kV JABALPUR-ITARSI 2 | 232 | WR-II | -- | 2015-04-06 | 10:27 | 2015-04-08 | 0:54 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 38.45 | -- | -- | -- | Line H/T for construction works by JTCL. |  | 100%
9 | WR2L9 | 400kV JABALPUR-ITARSI 2 | 232 | WR-II | -- | 2015-04-27 | 8:25 | 2015-04-27 | 9:04 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.65 | 0 | -- | -- | -- | Line A/T on Y-ph to E/F, F/L- 94.8 kM from Itarsi & 117kms from Jabalpur due to Burning of sugarcane waste between location no. - 366-367. All formers are given strict instructions to avoid such thingsi n future. |  | 100%
10 | WR2L10 | 400kV GANDHAR-DEHGAM 1 | 157 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
11 | WR2L11 | 400kV GANDHAR-DEHGAM 2 | 157 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
13 | WR2L13 | 400kV VINDHYACHAL-SASAN | 21 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
14 | WR2L14 | 400kV SASAN-JABALPUR | 368 | WR-II | -- | 2015-04-29 | 11:51 | 2015-04-29 | 11:51 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R successfully on R phase to E/F, F/L - 16.1 km from Jabalpur, F/C: 9.9kA// 375km from Sasan. |  | 100%
15 | WR2L15 | 400kV VINDHYACHAL-JABALPUR 4 | 389 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
16 | WR2L16 | 400kV JABALPUR-ITARSI 3 | 234 | WR-II | -- | 2015-04-09 | 09:34 | 2015-04-11 | 0:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 38.68 | -- | -- | -- | Line H/T to avail OCC approved S/D by JPTL (Sterlite) for crossing work of 765kV Jabalpur-Bina Line. |  | 100%
17 | WR2L17 | 400kV JABALPUR-ITARSI 4 | 234 | WR-II | -- | 2015-04-09 | 09:51 | 2015-04-10 | 23:13 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 37.37 | -- | -- | -- | Line H/T to avail OCC approved S/D by JPTL (Sterlite) for crossing work of 765kV Jabalpur-Bina Line. |  | 100%
18 | WR2L18 | 400kV ITARSI-KHANDWA 1 | 196.64 | WR-II | -- | 2015-04-29 | 10:58 | 2015-04-29 | 18:28 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.5 | -- | -- | -- | H/T to avail OCC approved S/D for NTAMC works. Line charged without Line Reactor due to high Tan delta value of winding LR at Itarsi end. |  | 100%
19 | WR2L19 | 400kV ITARSI-KHANDWA 2 | 196.64 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
21 | WR2L21 | 400kV KHANDWA-DHULE 2 | 261.78 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
22 | WR2L22 | 400kV GANDHAR-SUGEN | 57 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
23 | WR2L23 | 400kV SUGEN-VAPI | 110 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
24 | WR2L24 | 400kV GANDHAR(NTPC)-GANDHAR(GTEC) | 13 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
25 | WR2L25 | 220kV GANDHAR-HALDARWA 1 | 13 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
26 | WR2L26 | 220kV GANDHAR-HALDARWA 2 | 13 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
27 | WR2L27 | 220kV KAWAS-NAVSARI(GIS) 1 | 58.15 | WR-II | -- | 2015-04-24 | 11:05 | 2015-04-24 | 17:07 | -- | -- | -- | -- | -- | -- | 6.03 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D for AMP works. |  | 99.16%
27 | WR2L27 | 220kV KAWAS-NAVSARI(GIS) 1 | 58.15 | WR-II | -- | 2015-04-27 | 12:50 | 2015-04-27 | 18:03 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 5.22 | -- | -- | -- | H/T to avail OCC approved S/D by NTPC for relay testing work. |  | 99.16%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-04-02 | 12:40 | 2015-04-02 | 19:17 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.62 | -- | -- | -- | Line H/T to avail S/D by NTPC. |  | 99.11%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-04-12 | 19:23 | 2015-04-12 | 20:48 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.42 | 0 | -- | -- | -- | Line A/T on B-ph to E/F due to burning of wild vegitation between location no. 34-35, F/L- 58kms( M 1)& 41kms(M2) at Navsari(PG) end F/C - 2.747kAmp. |  | 99.11%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-04-13 | 16:38 | 2015-04-13 | 19:10 | -- | -- | -- | -- | -- | -- | 0 | 0 | 2.53 | 0 | -- | -- | -- | Line A/T on Bph to E/F due to burning of wild vegitation between loc.no. 35-36 , Z1, F/L - 47kM from Kawas. |  | 99.11%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-04-25 | 10:12 | 2015-04-25 | 16:36 | -- | -- | -- | -- | -- | -- | 6.4 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC S/D to carry out AMP works. |  | 99.11%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-04-28 | 12:45 | 2015-04-28 | 17:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 4.83 | -- | -- | -- | Line H/T to Avail OCC approved S/D by NTPC. |  | 99.11%
29 | WR2L29 | 220kV NAVSARI(GIS)-NAVSARI 1 | 31.33 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
30 | WR2L30 | 220kV NAVSARI(GIS)-NAVSARI 2 | 31.33 | WR-II | -- | 2015-04-13 | 15:32 | 2015-04-13 | 16:17 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.75 | 0 | -- | -- | -- | Line A/T on Bph to E/F due to burning of sugarcane filed between loc.no. 134-315, Z1, F/L - 22kM from Navsari (PG). |  | 100%
31 | WR2L31 | 220kV KAWAS-VAV 1 | 37 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
32 | WR2L32 | 220kV KAWAS-VAV 2 | 37 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
33 | WR2L33 | 220kV KAWAS-HALDARWA 1 | 81 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
34 | WR2L34 | 220kV KAWAS-HALDARWA 2 | 81 | WR-II | -- | 2015-04-15 | 5:44 | 2015-04-15 | 12:05 | -- | -- | -- | -- | -- | -- | 6.35 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Yph to E/F, F/L: 6.6kM, F/C:17.64kA from Haldarwa. Powergrid sent mail for readiness at 12.05 hrs. Outage from 12:05 hrs to 12:49 hrs is not attributable to POWERGIRD. |  | 99.12%
34 | WR2L34 | 220kV KAWAS-HALDARWA 2 | 81 | WR-II | -- | 2015-04-15 | 12:05 | 2015-04-15 | 12:49 | -- | -- | -- | -- | -- | -- | 0 | 0.73 | 0 | 0 | -- | -- | -- | Line A/T on Yph to E/F, F/L: 6.6kM, F/C:17.64kA from Haldarwa. Powergrid sent mail for readiness at 12.05 hrs. Outage from 12:05 hrs to 12:49 hrs is not attributable to POWERGIRD. |  | 99.12%
35 | WR2L35 | 220kV KAKRAPAR-HALDARWA 1 | 74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
36 | WR2L36 | 220kV KAKRAPAR-HALDARWA 2 | 74 | WR-II | -- | 2015-04-07 | 11:20 | 2015-04-07 | 20:40 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.33 | -- | -- | -- | H/T to avail S/D by NPCIL. | Agency: WRPC Mumbai | 100%
36 | WR2L36 | 220kV KAKRAPAR-HALDARWA 2 | 74 | WR-II | -- | 2015-04-26 | 7:07 | 2015-04-26 | 19:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.33 | -- | -- | -- | Line H/T to avail S/D by Kakrapar. |  | 100%
37 | WR2L37 | 220kV KAKRAPAR-VAV 1 | 43 | WR-II | -- | 2015-04-08 | 9:02 | 2015-04-08 | 20:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.5 | -- | -- | -- | Line H/T to avail S/D by NPCIL for Maintenance work at NPCIL. |  | 100%
37 | WR2L37 | 220kV KAKRAPAR-VAV 1 | 43 | WR-II | -- | 2015-04-14 | 8:10 | 2015-04-16 | 20:10 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 60 | -- | -- | -- | H/T to avail S/D by NPCIL. |  | 100%
37 | WR2L37 | 220kV KAKRAPAR-VAV 1 | 43 | WR-II | -- | 2015-04-30 | 9:00 | 2015-04-30 | 20:30 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.5 | -- | -- | -- | H/T to avail OCC approved S/D by NPCIL. |  | 100%
38 | WR2L38 | 220kV KAKRAPAR-VAV 2 | 43 | WR-II | -- | 2015-04-27 | 07:02 | 2015-04-27 | 19:46 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.73 | -- | -- | -- | Line H/T to avail OCC approved S/D by Kakrapar. |  | 100%
39 | WR2L39 | 220kV KAKRAPAR-VAPI 1 | 117 | WR-II | -- | 2015-04-09 | 10:36 | 2015-04-10 | 02:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 15.4 | -- | -- | -- | Line H/T to avail OCC approved S/D by NPCIL. |  | 100%
39 | WR2L39 | 220kV KAKRAPAR-VAPI 1 | 117 | WR-II | -- | 2015-04-28 | 7:46 | 2015-04-28 | 20:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.33 | -- | -- | -- | Line H/T to avail OCC approved S/D by Kakrapar. |  | 100%
40 | WR2L40 | 220kV KAKRAPAR-VAPI 2 | 117 | WR-II | -- | 2015-04-11 | 8:01 | 2015-04-11 | 19:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.73 | -- | -- | -- | Line H/T to avail S/D by NPCIL. |  | 100%
40 | WR2L40 | 220kV KAKRAPAR-VAPI 2 | 117 | WR-II | -- | 2015-04-29 | 8:27 | 2015-04-29 | 19:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.87 | -- | -- | -- | H/T to avail OCC approved S/D by NPCIL. |  | 100%
41 | WR2L41 | 400kV VINDHYACHAL-SATNA 1 | 267 | WR-II | -- | 2015-04-14 | 0:23 | 2015-04-14 | 0:23 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R sucessfully at Satna and A/R failed at V'chal end on Bph to E/F, Z1, F/C:2.53kA, F/L:156kM from Satna. |  | 100%
41 | WR2L41 | 400kV VINDHYACHAL-SATNA 1 | 267 | WR-II | -- | 2015-04-14 | 0:23 | 2015-04-14 | 0:40 | -- | -- | -- | -- | -- | -- | 0 | 0.28 | 0 | 0 | -- | -- | -- | A/R failed at NTPC V'chal end due to some CB problem at NTPC end. |  | 100%
42 | WR2L42 | 400kV VINDHYACHAL-SATNA 2 | 267 | WR-II | -- | 2015-04-14 | 16:52 | 2015-04-14 | 17:07 | -- | -- | -- | -- | -- | -- | 0.25 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Yph to E/F, F/L: 45.7%, from Satna end, A/R successfull at V'Chal(NTPC) end. Tried to close CB but Hunting observed at V'chal end. Hence outage from 17:07 hrs to 17:56 hrs is not attributable to POWERGRID. |  | 99.97%
42 | WR2L42 | 400kV VINDHYACHAL-SATNA 2 | 267 | WR-II | -- | 2015-04-14 | 17:07 | 2015-04-14 | 17:56 | -- | -- | -- | -- | -- | -- | 0 | 0.82 | 0 | 0 | -- | -- | -- | Line A/T on Yph to E/F, F/L: 45.7%, from Satna end, A/R successfull at V'Chal(NTPC) end. Tried to close CB but Hunting observed at V'chal end. Hence outage from 17:07 hrs to 17:56 hrs is not attributable to POWERGRID. |  | 99.97%
43 | WR2L43 | 400kV VINDHYACHAL-SATNA 3 | 258.31 | WR-II | -- | 2015-04-24 | 13:18 | 2015-04-24 | 18:19 | -- | -- | -- | -- | -- | -- | 0 | 0 | 5.02 | 0 | -- | -- | -- | Line A/T on R ph to E/F, due to burning of wheat husk below the line between span 657-658 by formers. All formers along with line has been warned to avoid burning of wheat / sugar cane wastage below the line to aviold electrical accidents. |  | 100%
43 | WR2L43 | 400kV VINDHYACHAL-SATNA 3 | 258.31 | WR-II | -- | 2015-04-25 | 17:09 | 2015-04-25 | 17:09 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R Successfully at both ends on B ph to E/F, F/L:164km, F/C:2.9kA from Satna end. |  | 100%
44 | WR2L44 | 400kV VINDHYACHAL-SATNA 4 | 258.31 | WR-II | -- | 2015-04-25 | 18:15 | 2015-04-25 | 19:16 | -- | -- | -- | -- | -- | -- | 0 | 1.02 | 0 | 0 | -- | -- | -- | Line A/R Successfully at Satna end on B ph to E/F but got tripped due to DT received from V'çhal NTPC end.. F/L:230km from V'chal. |  | 100%
47 | WR2L45 | 400kV SATNA-BINA 1 | 276 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
48 | WR2L46 | 400kV SATNA-BINA 2 | 276 | WR-II | Insulator Failure | 2015-04-13 | 22:37 | 2015-04-14 | 15:04 | 01 no. insulator failure at loc. No. 343. | -- | -- | -- | -- | 0.68542 | 16.45 | 0 | 0 | 0 | 1 | N | -0.31458 | Line A/T on Yph to E/F due to insulator flashover at location no. 343. |  | 97.72%
49 | WR2L47 | 400kV BINA-BINA(MP) 1 | 0.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
50 | WR2L48 | 400kV BINA-BINA(MP) 2 | 0.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
51 | WR2L49 | 765kV BINA-GWALIOR 1 | 234.931 | WR-II | -- | 2015-04-06 | 10:20 | 2015-04-06 | 12:44 | -- | -- | -- | -- | -- | -- | 2.4 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for open conductor rectification work at Gwalior. |  | 99.67%
52 | WR2L50 | 765kV AGRA-GWALIOR 1 | 129.435 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
53 | WR2L51 | 400kV SATNA-BINA 4 | 272.586 | WR-II | -- | 2015-04-04 | 9:57 | 2015-04-04 | 19:00 | -- | -- | -- | -- | -- | -- | 9.05 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D by POWERGRID for Line maint work. |  | 98.74%
54 | WR2L52 | 400kV SATNA-BINA 3 | 272.586 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
55 | WR2L53 | 400kV BINA-SHUJALPUR 1 | 199.936 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
56 | WR2L54 | 400kV BINA-SHUJALPUR 2 | 199.936 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
57 | WR2L55 | 400kV SHUJALPUR-NAGDA 1 | 152.229 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
58 | WR2L56 | 400kV SHUJALPUR-NAGDA 2 | 152.229 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
59 | WR2L57 | 400kV NAGDA-DEHGAM 2 | 331.442 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
60 | WR2L58 | 400kV NAGDA-DEHGAM 1 | 331.442 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
61 | WR2L59 | 400kV SEONI-KHANDWA 1 | 351.729 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
62 | WR2L60 | 400kV SEONI-KHANDWA 2 | 351.729 | WR-II | -- | 2015-04-02 | 10:16 | 2015-04-03 | 00:01 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.75 | -- | -- | -- | Line H/T for NTAMC works. After completion of works line kept out on voltage regulation since 18:52Hrs/02.04.2015 as per WRLDC instructions. |  | 100%
62 | WR2L60 | 400kV SEONI-KHANDWA 2 | 351.729 | WR-II | -- | 2015-04-30 | 14:42 | 2015-04-30 | 14:42 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R successfully from both ends on Y-ph to E/F, F/L - Khnadwa-167kms & Seoni-187.7kms. |  | 100%
63 | WR2L61 | 400kV KHANDWA-RAJGARH 2 | 220.588 | WR-II | -- | 2015-03-31 | 18:13 | 2015-04-05 | 10:44 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 106.73 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
64 | WR2L62 | 400kV SARDAR SAROVAR-RAJGARH 1(LILO) | 4.01 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
65 | WR2L63 | 400kV SARDAR SAROVAR-RAJGARH 2(LILO) | 4.01 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
66 | WR2L64 | 400kV RAJGARH-NAGDA 1(LILO) | 4.12 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
67 | WR2L65 | 400kV RAJGARH-NAGDA 2(LILO) | 4.12 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-04-11 | 1:03 | 2015-04-19 | 7:05 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 198.03 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-04-26 | 18:13 | 2015-04-27 | 07:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.97 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-04-28 | 18:32 | 2015-04-29 | 10:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 15.65 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
69 | WR2L67 | 220kV VAPI-MAGARWADA 1 | 25.71 | WR-II | Failure of earth wire | 2015-04-23 | 10:32 | 2015-04-23 | 16:43 | -- | -- | -- | E/W damaged between loc. No. 63-64. | -- | 0.2575 | 6.18 | 0 | 0 | 0 | 2 | N | -1.7425 | Line H/T to replace damaged Earth wire between location no: 63 - 64 at Mumbai - Ahmedabad Railway crossing. | Agency: WRPC Mumbai | 99.14%
69 | WR2L67 | 220kV VAPI-MAGARWADA 1 | 25.71 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 99.14%
70 | WR2L68 | 220kV VAPI-MAGARWADA 2 | 25.71 | WR-II | Failure of earth wire | 2015-04-23 | 10:40 | 2015-04-23 | 16:44 | -- | -- | -- | E/W damaged between loc. No. 63-64. | -- | 0.25292 | 6.07 | 0 | 0 | 0 | 2 | N | -1.7471 | Line H/T to replace damaged Earth wire between location no: 63 - 64 at Mumbai - Ahmedabad Railway crossing. |  | 99.16%
71 | WR2L69 | 220kV VAPI-KHARADPARA 1 | 29.66 | WR-II | -- | 2015-04-07 | 15:04 | 2015-04-07 | 18:12 | -- | -- | -- | -- | -- | -- | 3.13 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved s/d to attend Hot spot in the line. |  | 99.57%
72 | WR2L70 | 220kV VAPI-KHARADPARA 2 | 29.66 | WR-II | -- | 2015-04-07 | 9:12 | 2015-04-07 | 14:38 | -- | -- | -- | -- | -- | -- | 5.43 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved s/d to attend Hot spot in the line. |  | 99.25%
73 | WR2L71 | 765kV BINA-GWALIOR 2 | 233.652 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
74 | WR2L72 | 765kV AGRA-GWALIOR 2 | 127.934 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
75 | WR2L73 | 765kV SEONI-BINA 1 | 292.046 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
76 | WR2L74 | 400kV DAMOH-BHOPAL 1 | 214.471 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
77 | WR2L75 | 400kV DAMOH-BHOPAL 2 | 213.8 | WR-II | -- | 2015-04-12 | 14:18 | 2015-04-12 | 14:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R successfully at both ends on B-ph to E/F, F/L- 158 kms from Damoh. F/C- 1.9kA |  | 100%
78 | WR2L76 | 220kV VAPI-KHADOLI 1 | 28.549 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
80 | WR2L77.1 | 220kV VAPI-SAYALI | 18.3 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
81 | WR2L77.2 | 220kV SAYALI-KHADOLI | 12.235 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
82 | WR2L78 | 400kV DAMOH-BIRSINGHPUR 1 | 228.474 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
83 | WR2L79 | 400kV DAMOH-BIRSINGHPUR 2 | 228.474 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
84 | WR2L80 | 400kV DEHGAM-PIRANA 1 | 46.656 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
85 | WR2L81 | 400kV DEHGAM-PIRANA 2 | 46.656 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | 2015-04-03 | 08:11 | 2015-04-03 | 19:56 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.75 | -- | -- | -- | H/T to avail OCC S/D by CGPL Mundra for insulator replacement work at Switchyrad. |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | 2015-04-04 | 9:10 | 2015-04-04 | 19:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.45 | -- | -- | -- | H/T to avail OCC S/D by CGPL Mundra for insulator replacement work at Switchyrad. |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | 2015-04-05 | 8:18 | 2015-04-05 | 19:10 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.87 | -- | -- | -- | Line H/T to avail OCC approved S/D by CGPL for Maintenance work at CGPL switchyard. |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | 2015-04-11 | 10:54 | 2015-04-11 | 19:02 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.13 | -- | -- | -- | Line H/T to avail S/D by CGPL Mundra. |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | 2015-04-26 | 11:54 | 2015-04-26 | 13:28 | -- | -- | -- | -- | -- | -- | 0 | 1.57 | 0 | 0 | -- | -- | -- | Line A/T Due to DT received from Mundra end. |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | 2015-04-26 | 14:00 | 2015-04-26 | 14:58 | -- | -- | -- | -- | -- | -- | 0 | 0.97 | 0 | 0 | -- | -- | -- | Line A/T Due to DT received from Mundra end. |  | 100%
87 | WR2L83 | 400kV MUNDRA-BHACHAU 2 | 99.468 | WR-II | -- | 2015-04-13 | 9:24 | 2015-04-13 | 21:26 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.03 | -- | -- | -- | Line H/T to avail S/D by CGPL. |  | 100%
87 | WR2L83 | 400kV MUNDRA-BHACHAU 2 | 99.468 | WR-II | -- | 2015-04-14 | 7:46 | 2015-04-14 | 17:51 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.08 | -- | -- | -- | H/T to avail OCC S/D by CGPL. |  | 100%
87 | WR2L83 | 400kV MUNDRA-BHACHAU 2 | 99.468 | WR-II | -- | 2015-04-28 | 6:55 | 2015-04-28 | 18:36 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.68 | -- | -- | -- | H/T to avail OCC approved S/D by CGPL Mundra for replacement of porcelain insulator with polymer at CGPL Gantry. |  | 100%
88 | WR2L84 | 400kV BHACHAU-RANCHHODPURA 1 | 282.856 | WR-II | -- | 2015-04-21 | 9:17 | 2015-04-27 | 17:05 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 151.8 | -- | -- | -- | Line H/T to avail OCC approved S/D by POWERGRID for Tower shifting for SSNL Canal crossing at two locations at two places to maintain electrical clearances. |  | 100%
89 | WR2L85 | 400kV BHACHAU-RANCHHODPURA 2 | 282.856 | WR-II | -- | 2015-04-21 | 9:21 | 2015-04-27 | 17:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 151.75 | -- | -- | -- | Line H/T to avail OCC approved S/D by POWERGRID for Tower shifting for SSNL Canal crossing at two locations at two places to maintain electrical clearances. |  | 100%
90 | WR2L86 | 400kV MUNDRA-LIMBDI 1 | 314.053 | WR-II | -- | 2015-04-15 | 8:44 | 2015-04-15 | 18:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.5 | -- | -- | -- | H/T to avail S/D by CGPL. |  | 100%
90 | WR2L86 | 400kV MUNDRA-LIMBDI 1 | 314.053 | WR-II | -- | 2015-04-16 | 8:12 | 2015-04-16 | 18:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.05 | -- | -- | -- | H/T to avail S/D by CGPL. |  | 100%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | 0 | -- | 2015-04-01 | 10:12 | 2015-04-01 | 13:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.25 | -- | -- | -- | H/T to avail S/D by GETCO. |  | 100%
93 | WR2L87.2 | 400kV HALVAD-LIMBDI | 92.13 | 0 | -- | 2015-04-02 | 10:55 | 2015-04-02 | 17:47 | -- | -- | -- | -- | -- | -- | 6.87 | 0 | 0 | 0 | -- | -- | -- | Line H/T for fixing of dislocated spacers and attending hot spot in line. |  | 99.05%
94 | WR2L88 | 765kV SATNA-BINA 1 | 274.164 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
95 | WR2L89 | 765kV SATNA-BINA 2 | 275.635 | WR-II | -- | 2015-04-26 | 9:07 | 2015-04-28 | 18:29 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 57.37 | -- | -- | -- | Line H/T to Avail OCC approved S/D to carry out crossing work of 800kV HVDC Champa - Kurukshetra Line. |  | 100%
96 | WR2L90 | 765kV BINA-INDORE(POOLING) 1 | 311.81 | WR-II | -- | 2015-04-20 | 10:25 | 2015-04-20 | 13:44 | -- | -- | -- | -- | -- | -- | 3.32 | 0 | 0 | 0 | -- | -- | -- | A/T on B-ph to E/F due to opening of B-ph dropper Jumper of Line isolator at Bina SS. |  | 99.54%
97 | WR2L91 | 400kV GANDHAR-NAVSARI(GIS) 2 | 102.152 | WR-II | -- | 2015-04-01 | 9:10 | 2015-04-01 | 20:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 11.4 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D for replacement of porcelain disc insulator strings with polymer insulator strings in all polluted sections of line to prevent undesirable tripping of line. |  | 100%
98 | WR2L92 | 400kV GANDHAR-NAVSARI(GIS) 1 | 102.152 | WR-II | -- | 2015-04-02 | 08:23 | 2015-04-02 | 20:05 | -- | -- | -- | -- | -- | -- | 0 | 0 | 11.7 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D for replacement of porcelain disc insulator strings with polymer insulator strings in all polluted sections of line to prevent undesirable tripping of line. |  | 98.8%
98 | WR2L92 | 400kV GANDHAR-NAVSARI(GIS) 1 | 102.152 | WR-II | -- | 2015-04-12 | 9:31 | 2015-04-12 | 10:45 | -- | -- | -- | -- | -- | -- | 1.23 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Y & B ph-ph fault. F/L- 84.3kms from Navsari & 3kms from Gandhar. |  | 98.8%
98 | WR2L92 | 400kV GANDHAR-NAVSARI(GIS) 1 | 102.152 | WR-II | -- | 2015-04-12 | 20:51 | 2015-04-12 | 23:31 | -- | -- | -- | -- | -- | -- | 2.67 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Y&B ph-ph fault. F/L- 84.69kms( M1)/94.0kms(M2) from Navsari & 3kms from Gandhar. F/C- 2.128kAmp( Y-ph) / 2.592kAmp(B-ph) at Navsari end . |  | 98.8%
98 | WR2L92 | 400kV GANDHAR-NAVSARI(GIS) 1 | 102.152 | WR-II | -- | 2015-04-13 | 10:54 | 2015-04-13 | 15:28 | -- | -- | -- | -- | -- | -- | 4.57 | 0 | 0 | 0 | -- | -- | -- | Line H/T to attend Hot spot in the line. |  | 98.8%
98 | WR2L92 | 400kV GANDHAR-NAVSARI(GIS) 1 | 102.152 | WR-II | -- | 2015-04-21 | 12:07 | 2015-04-22 | 18:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 30.63 | -- | -- | -- | H/T to avail OCC approved S/D by NTPC Gandhar. |  | 98.8%
99 | WR2L93 | 400kV MUNDRA-JETPUR 1 | 336.742 | WR-II | -- | 2015-04-17 | 8:06 | 2015-04-17 | 16:20 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.23 | -- | -- | -- | Line H/T to avail OCC Approved S/d by CGPL Mundra. | Agency: WRPC Mumbai | 100%
99 | WR2L93 | 400kV MUNDRA-JETPUR 1 | 336.742 | WR-II | -- | 2015-04-18 | 8:16 | 2015-04-18 | 18:58 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.7 | -- | -- | -- | Line H/T to avail OCC S/D by CGPL Mundra |  | 100%
99 | WR2L93 | 400kV MUNDRA-JETPUR 1 | 336.742 | WR-II | -- | 2015-04-29 | 7:31 | 2015-04-30 | 19:31 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36 | -- | -- | -- | H/T to avail OCC approved S/D by GETCO. |  | 100%
100 | WR2L94 | 400kV MUNDRA-JETPUR 2 | 336.742 | WR-II | -- | 2015-04-06 | 09:20 | 2015-04-06 | 17:47 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.45 | -- | -- | -- | Line H/T to avail S/D by CGPL. |  | 100%
100 | WR2L94 | 400kV MUNDRA-JETPUR 2 | 336.742 | WR-II | -- | 2015-04-29 | 7:10 | 2015-04-30 | 19:07 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 35.95 | -- | -- | -- | H/T to avail OCC approved S/D by GETCO. |  | 100%
101 | WR2L95 | 400kV VINDHYACHAL(NTPC)-VINDHYACHAL(POOLING) 1 | 28.55 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
102 | WR2L96 | 400kV VINDHYACHAL(NTPC)-VINDHYACHAL(POOLING) 2 | 28.55 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
103 | WR2L97 | 400kV VINDHYACHAL(POOLING)-SASAN 1 | 5.443 | WR-II | -- | 2015-04-15 | 11:23 | 2015-04-17 | 12:34 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 49.18 | -- | -- | -- | Line H/T to avail S/D for stringing work of 400KV V'chal(NTPC) - V'chal(Pooling). |  | 100%
104 | WR2L98 | 400kV VINDHYACHAL(POOLING)-SASAN 2 | 5.443 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
105 | WR2L99 | 765kV SASAN-SATNA 1 | 245.7 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
106 | WR2L100 | 400kV BINA-BINA(MP) 3 | 0.62 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
109 | WR2L101.1.1 | 400kV NAVSARI(GIS)-MAGARWADA(GIS) 1 | 125.8 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
110 | WR2L101.1.2 | 400kV KALA(GIS)-MAGARWADA(GIS) 1 | 52.9 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
111 | WR2L101.2 | 400kV KALA(GIS)-VAPI 1 | 49 | WR-II | -- | 2015-04-21 | 9:43 | 2015-04-21 | 18:31 | -- | -- | -- | -- | -- | -- | 8.8 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D by POWERGRID for fixing of spacers. |  | 98.78%
112 | WR2L102 | 400kV VAPI-NAVASARI(GIS) 2 | 116.879 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
113 | WR2L103 | 765kV SASAN-SATNA 2 | 242.23 | WR-II | -- | 2015-04-22 | 10:00 | 2015-04-22 | 16:40 | -- | -- | -- | -- | -- | -- | 6.67 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail outage for jumper rectification works at Location no: 207(D+25). |  | 99.07%
114 | WR2L104 | 400kV BINA-BINA(MP) 4 | 0.62 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
115 | WR2L105 | 400kV INDORE(MP)-INDORE(POOLING) 1 | 49.73 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
116 | WR2L106 | 400kV INDORE(MP)-INDORE(POOLING) 2 | 49.73 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
117 | WR2L107 | 400kV JABALPUR-JABALPUR(POOLING) 1 | 15.456 | WR-II | -- | 2015-04-28 | 18:46 | 2015-04-28 | 19:28 | -- | -- | -- | -- | -- | -- | 0.7 | 0 | 0 | 0 | -- | -- | -- | Line A/T on R & Y ph to ph fault, F/L - 14.96kM from Jabalpur, F/C: 6.57kA/6.99kA. |  | 99.9%
118 | WR2L108 | 400kV JABALPUR-JABALPUR(POOLING) 2 | 15.456 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
119 | WR2L109 | 765kV JABALPUR(POOLING)-BINA 1 | 229.74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
120 | WR2L110 | 765kV JABALPUR(POOLING)-BINA 2 | 229.74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-04-07 | 13:43 | 2015-04-07 | 16:51 | -- | -- | -- | -- | -- | -- | 3.13 | 0 | 0 | 0 | -- | -- | -- | H/T to avail S/D for attending oil leakage in Line reactor at Satna end. |  | 99.57%
122 | WR2L112 | 400kV PIRANA-ASOJ 1 | 143.539 | WR-II | -- | 2015-04-19 | 20:50 | 2015-04-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 267.17 | -- | -- | -- | Line made ready for antitheft charging of 765kV Dhule - Vadodara line M/s BDTCL as 400kV Dhule - Pirana line as contigency measures. Presently Pirana-Vadodara line was idle charged from Pirana end upto Vadodara gantry till readiness of BDTCL. |  | 100%
123 | WR2L113 | 400kV PIRANA-ASOJ 2 | 143.539 | WR-II | -- | 2015-04-18 | 8:50 | 2015-04-19 | 21:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.92 | -- | -- | -- | Line H/T to avail OCC Approved S/D for removing the bunching of Ckt.1 & Ckt.2 to facilitage Antitheft contingency charging of 765kV Dhule - Vadodara line of BDTCL as 400kV Dhule - Pirana Line.. |  | 100%
124 | WR2L114 | 400kV INDORE(POOLING)-ASOJ 3 | 321.203 | WR-II | -- | 2015-04-11 | 18:49 | 2015-04-12 | 0:51 | -- | -- | -- | -- | -- | -- | 6.03 | 0 | 0 | 0 | -- | -- | -- | Line A/T on R-ph to E/F. F/L - 357kms from Indore & 9 kms from Asoj end. Further test charging of line not permitted by WRLDC/GETCO untill patrolling of Line. Patrolling carried out but no abnormality was found. |  | 99.16%
124 | WR2L114 | 400kV INDORE(POOLING)-ASOJ 3 | 321.203 | WR-II | -- | 2015-04-17 | 8:19 | 2015-04-17 | 21:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 12.87 | -- | -- | -- | Line H/T to avail OCC Approved S/D by POWERGRID for testing of relay pertaining to upgradation of line from 400kV to 765kV Level. |  | 99.16%
124 | WR2L114 | 400kV INDORE(POOLING)-ASOJ 3 | 321.203 | WR-II | -- | 2015-04-18 | 8:39 | 2015-04-19 | 20:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.18 | -- | -- | -- | Line H/T to avail OCC Approved S/D by M/s BDTCL for making preparation for contingency charging arrangements for 400kV Dhule - Pirana Line. |  | 99.16%
125 | WR2L115 | 765kV BINA-GWALIOR 3 | 231.27 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
126 | WR2L116 | 765kV SATNA-GWALIOR 2 | 342.15 | WR-II | -- | 2015-04-08 | 15:02 | 2015-04-08 | 19:14 | -- | -- | -- | -- | -- | -- | 4.2 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail Shutdown for swapping of Y-ph Line Reactor with Spare unit due to heavy oil leakege from the Y-ph unit at Gwalior end. |  | 99.42%
127 | WR2L117 | 400kV ANUPPUR-JABALPUR(POOLING) 1 | 246.409 | WR-II | -- | 2015-04-04 | 14:09 | 2015-04-05 | 17:01 | -- | -- | -- | -- | -- | -- | 26.87 | 0 | 0 | 0 | -- | -- | -- | Line A/T from both ends on R-ph to E/F, F/L - 212kms from Jabalpur Pool. |  | 95.28%
127 | WR2L117 | 400kV ANUPPUR-JABALPUR(POOLING) 1 | 246.409 | WR-II | -- | 2015-04-06 | 13:32 | 2015-04-06 | 19:30 | -- | -- | -- | -- | -- | -- | 5.97 | 0 | 0 | 0 | -- | -- | -- | Line A/T on R ph to E/F, F/L - 208km from Jabalpur Pooling, F/C: 1.9kA. Line charged from Jabalpur at 19:30Hrs but synchronized by M B Power at 20:31Hrs. |  | 95.28%
127 | WR2L117 | 400kV ANUPPUR-JABALPUR(POOLING) 1 | 246.409 | WR-II | -- | 2015-04-07 | 14:04 | 2015-04-07 | 14:04 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R successfully at both ends. |  | 95.28%
127 | WR2L117 | 400kV ANUPPUR-JABALPUR(POOLING) 1 | 246.409 | WR-II | -- | 2015-04-08 | 12:30 | 2015-04-08 | 13:41 | -- | -- | -- | -- | -- | -- | 1.18 | 0 | 0 | 0 | -- | -- | -- | Shutdown availed for rectification of Hot Spot in the line. |  | 95.28%
128 | WR2L118 | 400kV ANUPPUR-JABALPUR(POOLING) 2 | 246.409 | WR-II | -- | 2015-04-04 | 14:15 | 2015-04-04 | 16:43 | -- | -- | -- | -- | -- | -- | 2.47 | 0 | 0 | 0 | -- | -- | -- | Line A/T from both ends on B-ph to E/F, F/L - 318kms from Jabalpur Pool. |  | 98.89%
128 | WR2L118 | 400kV ANUPPUR-JABALPUR(POOLING) 2 | 246.409 | WR-II | -- | 2015-04-07 | 13:52 | 2015-04-07 | 18:37 | -- | -- | -- | -- | -- | -- | 4.75 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail s/d to attend Hot spot in the line. |  | 98.89%
128 | WR2L118 | 400kV ANUPPUR-JABALPUR(POOLING) 2 | 246.409 | WR-II | -- | 2015-04-23 | 17:20 | 2015-04-23 | 18:06 | -- | -- | -- | -- | -- | -- | 0.77 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Y ph to E/F, F/L - 118'6km from Jabalpur Pooling, F/C: 2.57kA. |  | 98.89%
129 | WR2L119 | 400kV BHACHAU-VARSANA 1 | 9.3 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
130 | WR2L120 | 400kV BHACHAU-VARSANA 2 | 9.3 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
132 | WR2L122 | 400kV TARAPUR-PADGHE 1 | 91.119 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
133 | WR2L123 | 400kV TARAPUR-PADGHE 2 | 91.119 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
134 | WR2L124 | 400kV BOISAR-PADGHE | 101 | WR-II | -- | 2015-04-21 | 18:50 | 2015-04-21 | 20:27 | -- | -- | -- | -- | -- | -- | 0 | 1.62 | 0 | 0 | -- | -- | -- | Line A/T on reciept of D/T from Padghe due to blasting of CT of ICT-4 at Padghe MSETCL. |  | 100%
134 | WR2L124 | 400kV BOISAR-PADGHE | 101 | WR-II | -- | 2015-04-23 | 18:25 | 2015-04-23 | 19:46 | -- | -- | -- | -- | -- | -- | 0 | 1.35 | 0 | 0 | -- | -- | -- | Line A/T on reciept of D/T from Padghe due to blasting of R phase CT of ICT-4 at Padghe MSETCL. |  | 100%
135 | WR2L125 | 400kV TARAPUR-BOISAR 1 | 20.881 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Agency: WRPC Mumbai | 100%
136 | WR2L126 | 400kV TARAPUR-BOISAR 2 | 20.881 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
137 | WR2L127 | 400kV VAPI-BOISAR | 94 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
138 | WR2L128 | 400kV KALA(GIS)-VAPI 2 | 52.947 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
139 | WR2L129 | 400kV NAVSARI(GIS)-MAGARWADA(GIS) 2 | 125.8 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
140 | WR2L130 | 400kV KALA(GIS)-MAGARWADA(GIS) 2 | 53.33 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
141 | WR2L131 | 765kV VINDHYACHAL(POOLING)-SATNA 1 | 264 | WR-II | -- | 2015-04-11 | 17:32 | 2015-04-11 | 18:13 | -- | -- | -- | -- | -- | -- | 0.68 | 0 | 0 | 0 | -- | -- | -- | Line A/T at both ends on Y-ph to E/F, F/L - 123.19kms from Satna & 142kms from Vindhyachal. F/C- 5.1kAMp. Test charging code not permitted by WRLDC due to persisting High System Voltage. Outage from 18:13 hrs/11/04/15 to 20:20 hrs/12/04/15 is not attributable to POWERGRID |  | 99.9%
141 | WR2L131 | 765kV VINDHYACHAL(POOLING)-SATNA 1 | 264 | WR-II | -- | 2015-04-11 | 18:13 | 2015-04-12 | 20:20 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 26.12 | -- | -- | -- | Line A/T at both ends on Y-ph to E/F, F/L - 123.19kms from Satna & 142kms from Vindhyachal. F/C- 5.1kAMp. Test charging code not permitted by WRLDC due to persisting High System Voltage. Outage from 18:13 hrs/11/04/15 to 20:20 hrs/12/04/15 is not attributable to POWERGRID |  | 99.9%
141 | WR2L131 | 765kV VINDHYACHAL(POOLING)-SATNA 1 | 264 | WR-II | -- | 2015-04-23 | 12:22 | 2015-04-23 | 12:22 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R successfully on B phase to E/F, F/L - 243km from Vindhyachal Pooling, F/C: 2.7kA. |  | 99.9%
142 | WR2L132 | 765kV SASAN-VINDHYACHAL(POOLING) 1 | 10 | WR-II | -- | 2015-04-03 | 11:54 | 2015-04-03 | 15:43 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.82 | -- | -- | -- | H/T to avail emergency S/D by Sasan for attending Hotspot. |  | 97.2%
142 | WR2L132 | 765kV SASAN-VINDHYACHAL(POOLING) 1 | 10 | WR-II | -- | 2015-04-04 | 9:45 | 2015-04-04 | 19:34 | -- | -- | -- | -- | -- | -- | 9.82 | 0 | 0 | 0 | -- | -- | -- | H/T to avail S/D by POWERGRID for rectification of burnt female contact of B-ph Line isolator at Vindhyachal Pooling station. |  | 97.2%
142 | WR2L132 | 765kV SASAN-VINDHYACHAL(POOLING) 1 | 10 | WR-II | -- | 2015-04-13 | 10:29 | 2015-04-13 | 20:09 | -- | -- | -- | -- | -- | -- | 9.67 | 0 | 0 | 0 | -- | -- | -- | Line H/T to attend Hot spot in the line. |  | 97.2%
148 | WR2T1 | ICT1 JABALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
149 | WR2T2 | ICT2 JABALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
150 | WR2T3 | ICT1 DEHGAM 400/220kV | 315 | WR-II | -- | 2015-04-06 | 10:25 | 2015-04-06 | 16:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.17 | -- | -- | -- | H/T for NTAMC works. |  | 100%
151 | WR2T4 | ICT2 DEHGAM 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
152 | WR2T5 | ICT1 SATNA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
153 | WR2T6 | ICT2 SATNA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
154 | WR2T7 | ICT1 KHANDWA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
155 | WR2T8 | ICT2 KHANDWA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
156 | WR2T9 | ICT1 VAPI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
157 | WR2T10 | ICT2 VAPI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
158 | WR2T11 | ICT1 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
159 | WR2T12 | ICT1 RAJGARH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
160 | WR2T13 | ICT2 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
161 | WR2T14 | ICT1 ITARSI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
162 | WR2T15 | ICT1 DAMOH 400/220kV | 315 | WR-II | -- | 2015-04-07 | 10:16 | 2015-04-07 | 14:06 | -- | -- | -- | -- | -- | -- | 3.83 | 0 | 0 | 0 | -- | -- | -- | ICT H/T to avail s/d for AMP works. |  | 99.47%
163 | WR2T16 | ICT2 DAMOH 400/220kV | 315 | WR-II | -- | 2015-04-08 | 9:30 | 2015-04-08 | 13:29 | -- | -- | -- | -- | -- | -- | 3.98 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC Approved S/D for AMP Work. |  | 99.45%
163 | WR2T16 | ICT2 DAMOH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 99.45%
164 | WR2T17 | ICT2 RAJGARH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
165 | WR2T18 | ICT1 BINA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
166 | WR2T19 | ICT1 PIRANA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
167 | WR2T20 | ICT2 PIRANA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
168 | WR2T21 | ICT3 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
169 | WR2T22 | ICT1 SHUJALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
170 | WR2T23 | ICT1 BHACHAU 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
171 | WR2T24 | ICT2 BHACHAU 400/220kV | 315 | WR-II | -- | 2015-04-01 | 10:17 | 2015-04-01 | 16:15 | -- | -- | -- | -- | -- | -- | 5.97 | 0 | 0 | 0 | -- | -- | -- | H/T to avail S/D for AMP works. |  | 98.88%
171 | WR2T24 | ICT2 BHACHAU 400/220kV | 315 | WR-II | -- | 2015-04-28 | 15:32 | 2015-04-28 | 17:37 | -- | -- | -- | -- | -- | -- | 2.08 | 0 | 0 | 0 | -- | -- | -- | H/T to avail S/D to attend Hot spot in Y phase Bushing. |  | 98.88%
172 | WR2T25 | ICT2 SHUJALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
173 | WR2T26 | ICT1 SATNA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
174 | WR2T27 | ICT2 NAVSARI(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
175 | WR2T28 | ICT1 NAVSARI(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
176 | WR2T29 | ICT2 SATNA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
177 | WR2T30 | ICT1 BINA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
178 | WR2T31 | ICT3 VAPI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
179 | WR2T32 | ICT2 BINA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Agency: WRPC Mumbai | 100%
180 | WR2T33 | ICT1 GWALIOR 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
181 | WR2T34 | ICT2 GWALIOR 765/400kV | 1500 | WR-II | -- | 2015-04-13 | 10:52 | 2015-04-13 | 20:29 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.62 | -- | -- | -- | H/T to avail OCC approved S/D for commissioning of CSD relay. |  | 100%
182 | WR2T35 | ICT2 INDORE(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-04-06 | 10:08 | 2015-04-06 | 19:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.05 | -- | -- | -- | H/T to avail OCC approved S/D to intigrate spare unit. |  | 100%
183 | WR2T36 | ICT1 INDORE(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-04-04 | 12:04 | 2015-04-04 | 18:20 | -- | -- | -- | -- | -- | -- | 6.27 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D by POWERGRID for making spare ICT unit free. |  | 99.13%
184 | WR2T37 | ICT1 JABALPUR(POOLING) 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
185 | WR2T38 | ICT2 JABALPUR(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-04-13 | 12:32 | 2015-04-16 | 20:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 79.72 | -- | -- | -- | H/T to avail OCC approved S/D for commissioning of CSD relay. |  | 100%
185 | WR2T38 | ICT2 JABALPUR(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-04-28 | 10:17 | 2015-04-28 | 20:21 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.07 | -- | -- | -- | H/T to avail OCC approved S/D for spare unit commissioning at Jabalpur Pooling. |  | 100%
186 | WR2T39 | ICT1 KALA(GIS) 400/220kV | 315 | WR-II | -- | 2015-04-15 | 12:46 | 2015-04-15 | 20:59 | -- | -- | -- | -- | -- | -- | 8.22 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC Approved S/D for rectification of Oil leakage from PRV. |  | 98.86%
186 | WR2T39 | ICT1 KALA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 98.86%
187 | WR2T40 | ICT2 KALA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
188 | WR2T41 | ICT3 NAVSARI(GIS) 400/220kV | 500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
189 | WR2T42 | ICT1 MAGARWADA(GIS) 400/220kV | 315 | WR-II | -- | 2015-04-20 | 10:48 | 2015-04-20 | 13:15 | -- | -- | -- | -- | -- | -- | 2.45 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D by POWERGRID for checking of master / follower scheme for OLTC. |  | 99.66%
190 | WR2T43 | ICT2 MAGARWADA(GIS) 400/220kV | 315 | WR-II | -- | 2015-04-20 | 10:51 | 2015-04-20 | 13:16 | -- | -- | -- | -- | -- | -- | 2.42 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D by POWERGRID for checking of master / follower scheme for OLTC. |  | 99.66%
191 | WR2T44 | ICT1 BOISAR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
192 | WR2T45 | ICT2 BOISAR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
193 | WR2T46 | ICT3 BOISAR 400/220kV | 500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
194 | WR2T47 | ICT2 VINDHYACHAL(POOLING) 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
197 | WR2R1 | BUS REACTOR 1 DEHGAM 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
198 | WR2R2 | BUS REACTOR 1 JABALPUR 33kV 25MVAR | 25 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
199 | WR2R3 | BUS REACTOR 2 JABALPUR 33kV 25MVAR | 25 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
200 | WR2R4 | BUS REACTOR 1 ITARSI 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
201 | WR2R5 | BUS REACTOR 2 ITARSI 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
202 | WR2R6 | BUS REACTOR 3 ITARSI 400kV 50MVAR | 50 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
203 | WR2R7 | BUS REACTOR 1 JABALPUR 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
205 | WR2R9 | BUS REACTOR 1 SATNA 400kV 50MVAR | 50 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
206 | WR2R10 | BUS REACTOR 1 BINA 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
207 | WR2R11 | BUS REACTOR 1 DAMOH 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
208 | WR2R12 | BUS REACTOR 1 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
209 | WR2R13 | BUS REACTOR 1 KHANDWA 400kV 125MAVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
210 | WR2R14 | BUS REACTOR 2 DEHGAM 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
211 | WR2R15 | BUS REACTOR 1 BHACHAU 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
212 | WR2R16 | BUS REACTOR 1 SHUJALPUR 400kV 63MVAR | 63 | WR-II | -- | 2015-04-20 | 10:46 | 2015-04-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 253.23 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
213 | WR2R17 | BUS REACTOR 1 RAJGARH 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
214 | WR2R18 | BUS REACTOR 1 NAVSARI(GIS) 400kV 63MVAR | 63 | WR-II | -- | 2015-04-09 | 10:51 | 2015-04-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 517.15 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
215 | WR2R19 | BUS REACTOR 2 SATNA 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
216 | WR2R20 | SWITCHABLE LR SHUJALPUR 1 400kV 63MVAR AT NAGDA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
217 | WR2R21 | SWITCHABLE LR SHUJALPUR 2 400kV 63MVAR AT NAGDA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
218 | WR2R22 | BUS REACTOR 2 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-03-20 | 18:59 | 2015-04-03 | 00:05 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 48.08 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
219 | WR2R23 | BUS REACTOR 3 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
220 | WR2R24 | BUS REACTOR 1 INDORE(POOLING) 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
221 | WR2R25 | SWITCHABLE LR SHUJALPUR 2 400kV 63MVAR AT BINA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
222 | WR2R26 | SWITCHABLE LR SHUJALPUR 1 400kV 63MVAR AT BINA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
223 | WR2R27 | BUS REACTOR 1 JABALPUR(POOLING) 400kV 125MVAR | 125 | WR-II | -- | 2015-03-26 | 11:21 |  |  | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 720 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
224 | WR2R28 | BUS REACTOR 2 KHANDWA 400kV 125MVAR | 125 | WR-II | -- | 2015-04-30 | 11:11 | 2015-04-30 | 16:46 | -- | -- | -- | -- | -- | -- | 5.58 | 0 | 0 | 0 | -- | -- | -- | S/D availed by POWERGRID to attend hot spot in Reactor Isolator. | Agency: WRPC Mumbai | 99.22%
224 | WR2R28 | BUS REACTOR 2 KHANDWA 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 99.22%
225 | WR2R29 | BUS REACTOR 2 JABALPUR 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
226 | WR2R30 | BUS REACTOR 1 SATNA 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
227 | WR2R31 | SWITCHABLE LR BINA 1 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
228 | WR2R32 | SWITCHABLE LR BINA 2 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-02 | 6:36 | 2015-04-05 | 18:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 84.15 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-06 | 09:34 | 2015-04-08 | 5:09 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 43.58 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-20 | 8:29 | 2015-04-21 | 18:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 33.75 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-27 | 11:52 | 2015-04-27 | 17:59 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.12 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-29 | 8:55 | 2015-04-29 | 18:12 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.28 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
230 | WR2R34 | SWITCHABLE LR BINA 1 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
231 | WR2R35 | SWITCHABLE LR BINA 2 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
232 | WR2R36 | SWITCHABLE LR INDORE(POOLING) 1 765kV 240MVAR AT BINA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
233 | WR2R37 | SWITCHABLE LR BINA 1 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
234 | WR2R38 | BUS REACTOR 1 BINA 765kV 240MVAR | 240 | WR-II | -- | 2015-03-27 | 09:33 |  |  | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 720 | -- | -- | -- | Reactor H/T to faciliate jumpering work between Bus reactor # 1 & Bus reactor # 2 for commissioning of 765kV Bus Reactor # 2 at Bina. |  | 100%
235 | WR2R39 | SWITCHABLE LR BINA 2 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
236 | WR2R40 | BUS REACTOR 2 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-06 | 10:08 | 2015-04-07 | 18:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.45 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
236 | WR2R40 | BUS REACTOR 2 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-13 | 9:38 | 2015-04-15 | 21:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 59.9 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
236 | WR2R40 | BUS REACTOR 2 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-20 | 15:29 | 2015-04-21 | 18:23 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 26.9 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
237 | WR2R41 | SWITCHABLE LR GWALIOR 3 765kV 240MVAR AT BINA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
238 | WR2R42 | SWITCHABLE LR GWALIOR 1 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
239 | WR2R43 | SWITCHABLE LR JAIPUR 1 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
240 | WR2R44 | BUS REACTOR 1 KALA(GIS) 400kV 80MVAR | 80 | WR-II | -- | 2015-03-19 | 11:00 |  |  | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 720 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
241 | WR2R45 | BUS REACTOR 2 INDORE(POOLING) 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-06 | 10:08 | 2015-04-06 | 20:39 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.52 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-08 | 10:41 | 2015-04-11 | 17:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 79.15 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-13 | 13:33 | 2015-04-13 | 18:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 5.07 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-25 | 9:49 | 2015-04-26 | 18:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 32.93 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-04-26 | 22:40 | 2015-04-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 97.33 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
243 | WR2R47 | BUS REACTOR 2 SHUJALPUR 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
244 | WR2R48 | SWITCHABLE LR GWALIOR 2 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
245 | WR2R49 | BUS REACTOR 1 GWALIOR 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
246 | WR2R50 | BUS REACTOR 2 DAMOH 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
247 | WR2R51 | BUS REACTOR 1 PIRANA 400kV 125MVAR | 125 | WR-II | -- | 2015-04-20 | 9:35 | 2015-04-20 | 18:36 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.02 | -- | -- | -- | H/T to avail OCC approved S/D by POWERGRID for NTAMC work. |  | 100%
248 | WR2R52 | SWITCHABLE LR BINA 3 (IPTC) 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
249 | WR2R53 | SWITCHABLE LR BHOPAL 1 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
250 | WR2R54 | SWITCHABLE LR JAIPUR 2 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
251 | WR2R55 | BUS REACTOR 2 BHACHAU 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
252 | WR2R56 | BUS REACTOR 2 JABALPUR(POOLING) 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
253 | WR2R57 | BUS REACTOR 1 MAGARWADA 400kV 80MVAR | 80 | WR-II | -- | 2015-04-09 | 10:52 | 2015-04-27 | 5:55 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 427.05 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
253 | WR2R57 | BUS REACTOR 1 MAGARWADA 400kV 80MVAR | 80 | WR-II | -- | 2015-04-28 | 15:10 | 2015-04-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 56.83 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
254 | WR2R58 | SWITCHABLE LR SATNA 1 765kV 240MVAR AT VINDHYACHAL(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
255 | WR2R59 | BUS REACTOR 2 BINA 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%