## Tripping details JULY (hidden)
TRIPPING DETAILS OF WR-II FOR THE MONTH OF JULY' 2011
Sl. No. | EVENT No. | Name of line/ICT/BR | TRIPPING DATE | TRIPPING TIME | RESTORATION DATE | RESTORATION TIME | ATTRIBUTED TO PGCIL | OUTAGE HOURS ATTRIBUTED TO |  | OUTAGE DEEMED AVAILABLE | CAT. CODE | Details | WRLDC CODE FOR
[8 empty] | OTHERS | SYSTEM CONSTR. |  |  |  | TRIPPING | CHARGING
1 | 904070 | DAMOH-BHOPAL I 400KV | 2011-04-25 | 16:51 | 2011-04-25 | 16:51 | - | - | - | 9.7022e-13 | LVRD | Line H/T for Voltage Regulation as per WRLDC instruction. | LD 04/1432
2 | 904078 | DAMOH-BHOPAL II 400KV | 2011-04-26 | 17:54 | 2011-04-26 | 17:54 | - | - | - | -3.2337e-12 | LVRD | Line H/T for Voltage Regulation. | LD 04/1494
3 | 905010 | DAMOH BIRSINGHPUR II 400kV | 2011-05-02 | 15:05 | 2011-05-02 | 15:05 | - | - | - | -3.2337e-12 | LVRD | Line Kept out for voltage regulation on WRLDC Instruction. | LD 05 /83
4 | 905019 | DAMOH BIRSINGHPUR I 400kV | 2011-05-07 | 9:41 | 2011-05-07 | 9:41 | - | - | - | -1.7786e-12 | LVRD | Line H/T for Voltage Regulation. | LD/ 05/342
5 | 905114 | RAJGARH-NAGDA I 400kV | 2011-05-30 | 11:30 | 2011-05-30 | 11:30 | - | - | - | -2.4253e-12 | LVRD | Line H/T for Voltage Regulation. | LD 05/1718
6 | 906020 | NAGDA-DEHGAM II 400kV | 2011-06-04 | 5:07 | 2011-06-04 | 5:07 | - | - | - | -3.5571e-12 | LVRD | Line H/T for Voltage Regulation. | LD 06/189
7 | 906042 | SATNA-BINA(PG) I 400kV | 2011-06-08 | 18:17 | 2011-06-08 | 18:17 | - | - | 2.1019e-12 | - | LNCC | A/T on R- Ph to E/F due to Tower collapse at Loc No. 565 (A Type) due to heavy wind F/L - 57kM (Bina) & 78.9% (Satna)
8 | 906048 | KHANDWA-RAJGARH I 400kV | 2011-06-09 | 3:32 | 2011-06-09 | 3:32 | - | - | - | -3.2338e-13 | LVRD | Line kept out on O/V on WRLDC instruction. | LD 06/491
9 | 906068 | BINA-SHUJALPUR#1 400kV | 2011-06-15 | 6:00 | 2011-06-15 | 6:00 | - | - | 0 | - | GOVC | A/T on operation of O/V Protection at Shujalpur.Line kept out on O/V from 06:05hrs/15.06.11 vide ,WRLDC CODE LD 06/839
10 | 906069 | SHUJALPUR - NAGDA I 400kV | 2011-06-15 | 6:50 | 2011-06-15 | 6:50 | - | - | - | -3.2337e-12 | LVRD | Line H/T for Voltage regulation | LD 06/841
11 | 906072 | ITARSI-KHANDWA II 400kV | 2011-06-16 | 4:10 | 2011-06-16 | 4:10 | - | - | - | -1.6169e-12 | LVRD | Line H/T for Voltage regulation | LD 06/894
12 | 906089 | SHUJALPUR-NAGDA II 400kV | 2011-06-18 | 8:20 | 2011-06-18 | 8:20 | - | - | - | -3.2338e-12 | LVRD | Line H/T for voltage regulation | LD 06/1043
13 | 906093 | 220 kV KAWAS-HALDARWA # 1 | 2011-06-20 | 16:29 | 2011-06-20 | 16:29 | - | - | - | -2.2636e-12 | LPRD | H/T to control overloading of 220KV Kawas-icchapur line. | LD 06/1168
14 | 906095 | JABALPUR-ITARSI IV 400kV | 2011-06-21 | 17:38 | 2011-06-21 | 17:38 | - | - | - | 1.1319e-12 | LVRD | Line H/T for voltage regulation | LD 06/1225
15 | 906104 | 400/220 kV ICT BINA | 2011-06-24 | 8:20 | 2011-06-24 | 8:20 |  |  |  |  | SPRD | ICT H/T for Power Regulation due to non availibility of load . | LD 06/1364
16 | 906109 | VINDHYACHAL-JABALPUR III 400kV | 2011-06-24 | 22:07 | 2011-06-24 | 22:07 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1409
17 | 906121 | VINDHYACHAL-SATNA IV 400KV | 2011-06-26 | 7:04 | 2011-06-26 | 7:04 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1489
18 | 906124 | SEONI-BINA I(400kV) 765kV | 2011-06-26 | 8:04 | 2011-06-26 | 8:04 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1494
19 | 906125 | KHANDWA-RAJGARH II 400kV | 2011-06-27 | 0:11 | 2011-06-27 | 0:11 |  |  |  |  | LVRD | Line H/T for Power Regulation. | LD 06/1536
20 | 906133 | SARDAR SAROVAR-RAJGARH I 400kV | 2011-06-29 | 8:15 | 2011-06-29 | 8:15 |  |  |  |  | OSPD | H/T to avail S/D by GETCO. | LD 06/1649
21 | 906141 | KAWAS-ICHCHAPUR 220kV | 2011-06-30 | 17:30 | 2011-06-30 | 17:30 |  |  |  |  | OSPD | Line H/T to avail outage by NTPC for attending Hot Point at Kawas S/s. | LD 06/1740
22
23
24
25
26
27
28
29
30
31
32
33
34
34
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
Formulas:
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT. CODE, row below],1)="D"),[RESTORATION DATE, row below]+[RESTORATION TIME, row below]-[TRIPPING DATE, row below]-[TRIPPING TIME, row below],"-")
OUTAGE DEEMED AVAILABLE = IF((RIGHT([CAT. CODE],1)="D"),[RESTORATION DATE]+[RESTORATION TIME]-[TRIPPING DATE]-[TRIPPING TIME],"-")
SYSTEM CONSTR. = IF((RIGHT([CAT. CODE],1)="C"),[RESTORATION DATE]+[RESTORATION TIME]-[TRIPPING DATE]-[TRIPPING TIME],"-")

## List (hidden)
220 kV GANDHAR-HALDARWA # 1
220 kV GANDHAR-HALDARWA # 2
220 kV ICHCHAPUR-VAV
220 kV KAKRAPAR-HALDARWA # 1
220 kV KAKRAPAR-HALDARWA # 2
220 kV KAKRAPAR-VAPI # 1
220 kV KAKRAPAR-VAPI # 2
220 kV KAKRAPAR-VAV # 1
220 kV KAKRAPAR-VAV # 2
220 kV KAWAS-HALDARWA # 1
220 kV KAWAS-HALDARWA # 2
220 kV KAWAS-ICHCHAPUR
220 kV KAWAS-NAVSARI # 1
220 kV KAWAS-NAVSARI # 2
220 kV KAWAS-VAV # 1
220 kV VAPI-KHADOLI # 1
220 kV VAPI-KHADOLI#2
220 kV VAPI-KHARADPARA # 1
220 kV VAPI-KHARADPARA # 2
220 kV VAPI-MAGARWADA # 1
220 kV VAPI-MAGARWADA # 2
33 kV BUS REACTOR JABALPUR # 1
33 kV BUS REACTOR JABALPUR # 2
400 kV BINA(PG)-BINA(MPEB) # 1
400 kV BINA(PG)-BINA(MPEB) # 2
400 kV BINA-NAGDA # 1
400 kV BINA-NAGDA # 2
400 kV BUS REACTOR, BINA
400 kV BUS REACTOR, DAMOH
400 kV BUS REACTOR, DEHGAM
400 kV BUS REACTOR, GWALIOR
400 kV BUS REACTOR, ITARSI # 1
400 kV BUS REACTOR, ITARSI # 2
400 kV BUS REACTOR, ITARSI # 3
400 kV BUS REACTOR, JABALPUR # 3
400 kV BUS REACTOR, SATNA
400 kV DAMOH-BHOPAL # 1
400 kV DAMOH-BHOPAL # 2
400 kV GANDHAR(NTPC)-GANDHAR(GTEC)
400 kV GANDHAR-DEHGAM # 1
400 kV GANDHAR-DEHGAM # 2
400 kV GANDHAR-SUGEN # 1
400 kV GANDHAR-SUGEN # 2
400 kV INDORE-ASOJ # 1
400 kV INDORE-ASOJ # 2
400 kV JABALPUR-ITARSI # 1
400 kV JABALPUR-ITARSI#2
400 kV JABALPUR-ITARSI#3
400 kV JABALPUR-ITARSI#4
400 kV KHANDWA-DHULE#1
400 kV KHANDWA-DHULE#2
400 kV KHANDWA-RAJGARH#1
400 kV KHANDWA-RAJGARH#2
400 kV NAGDA-DEHGAM#1
400 kV NAGDA-DEHGAM#2
400 kV RAJGARH-NAGDA#1
400 kV RAJGARH-NAGDA#2
400 kV SARDAR SAROVAR-RAJGARH#1
400 kV SARDAR SAROVAR-RAJGARH#2
400 kV SATNA-BINA(PG)#1
400 kV SATNA-BINA(PG)#2
400 kV SATNA-BINA(PG)#3
400 kV SATNA-BINA(PG)#4
400 kV SATPURA-ITARSI
400 kV SEONI-KHANDWA#1
400 kV SEONI-KHANDWA#2
400 kV VAPI-SUGEN
400 kV VINDHYACHAL-JABALPUR#1
400 kV VINDHYACHAL-JABALPUR#2
400 kV VINDHYACHAL-JABALPUR#3
400 kV VINDHYACHAL-JABALPUR#4
400 kV VINDHYACHAL-SATNA#1
400 kV VINDHYACHAL-SATNA#2
400 kV VINDHYACHAL-SATNA#3
400 kV VINDHYACHAL-SATNA#4
400 kV#1TARSI-INDORE#1
400 kV#1TARSI-INDORE#2
400 kV#1TARSI-KHANDWA#1
400 kV#1TARSI-KHANDWA#2
400/220 kV ICT ITARSI
400/220 kV ICT#1 DAMOH
400/220 kV ICT#1 DEHGAM
400/220 kV ICT#1 GWALIOR
400/220 kV ICT#1 JABALPUR
400/220 kV ICT#1 KHANDWA
400/220 kV ICT#1 RAJGARH
400/220 kV ICT#1 SATNA
400/220 kV ICT#1 VAPI
400/220 kV ICT#2 DAMOH
400/220 kV ICT#2 DEHGAM
400/220 kV ICT#2 GWALIOR
400/220 kV ICT#2 JABALPUR
400/220 kV ICT#2 KHANDWA
400/220 kV ICT#2 RAJGARH
400/220 kV ICT#2 SATNA
400/220 kV ICT#2 VAPI
765 kV AGRA-GWALIOR#1 (400 kV)
765 kV AGRA-GWALIOR#2 (400 kV)
765 kV BINA-GWALIOR#1 (400 kV)
765 kV BINA-GWALIOR#2 (400 kV)
765 kV SEONI-BINA (400 kV)

## code (hidden)
POWER GRID CORPORATION OF INDIA LIMITED
400 / 220 kV SUB-STATION, JABALPUR
STANDARD LIST OF ELEMENT OUTAGE CATEGORIES
CATEGORY | Paertaining to | TYPE OF OUTAGE
GGDC | SYSTEM CONSTRAINTS | Power swings / trippings due to Grid disturbance / Under frequency islanding trippings / Reverse power flow blocking related tripping / Hand tripping due to loss of voltage
GOFC | SYSTEM CONSTRAINTS | ICT tripping on over fluxing
GOLC | SYSTEM CONSTRAINTS | ICT tripping on over loading / over-current
GOMD | SYSTEM CONSTRAINTS | Unable to restore after any outage ( other than grid disturbance ), due to system constraint
GOVC | SYSTEM CONSTRAINTS | Tripping on Over Voltage protection
LART | LINE FAULTS ON LINES OWNED BY POWERGRID | Auto Re-closure due to Earth faults
LCSD | OUTAGE OF ELEMENTS UNDER O&M TO FASCILITATE THE CONSTRUCTION ACTIVITIES OF NEW SYSTEM EXECUTED BY POWERGRID | Line shutdown taken to fascilitate construction activities of new system being executed by POWERGRID
LEFT | LINE FAULTS ON LINES OWNED BY POWERGRID | Tripping due to Earth faults
LHWT | LINE FAULTS ON LINES OWNED BY POWERGRID | Faults due to snapping of conductors, earth wire, jumper, insulator failure, failure of tower due to design & material deficiency etc.
LMAC | SYSTEM OUTAGE CAUSED BY MISCREANTS / MILITANT ACTIVITIES | Line breakdown caused by miscreants / militant activities
LNCC | OUTAGE OF SYSTEM DUE TO NATURAL CALAMITIES | Line outage due to Natural calamities
LPPT | LINE FAULTS ON LINES OWNED BY POWERGRID | Phase to phase faults, double line to Earth faults, 3-ph and 3-ph reath faults, but not due to Power Swings.
LPRD | SYSTEM CONSTRAINTS | Line hand tripped for Power Regulation on RLDC instruction
LVRD | SYSTEM CONSTRAINTS | Line hand tripped for Voltage Regulation on RLDC instruction
OMST | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Miscellaneous outages attributable to POWERGRID
OMSU | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Miscellaneous outages attributable to Other agency or force majeure condition.
OSFD | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Forced shutdown availed by other agency / agencies causing outage of POWERGRID element.
OSFT | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Forced shutdown ( e.g. E/W snapping / hotspots )
OSPD | OTHER OUTAGES RELATED TO OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Planned shutdown availed by other agency / agencies for maintenance or construction of their transmission system causing outage of POWERGRID element.
OSPT | OTHER OUTAGES RELATED TO POWERGRID INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUBSTATION | Planned shutdown for maintenance work of POWERGRID elements
SBBT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Busbar protection operation (POWERGRID Substation only including the fault initiated in POWERGRID owned by other agency
SBBU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Busbar protection operation
SCSD | OUTAGE OF ELEMENTS UNDER O&M TO FASCILITATE THE CONSTRUCTION ACTIVITIES OF NEW SYSTEM EXECUTED BY POWERGRID | Substation equipment shutdown taken to fascilitate construction activities of new system being executed by POWERGRID
SEFT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Equipment failure
SEFU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Equipment failure
SEMT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Equipment Mal-operation
SEMU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Equipment Mal-operation
SICT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | REF, Differential, Buchholz protection operation, PRV, OTI, WTI on ICT
SICU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | REF, Differential, Buchholz protection operation, PRV, OTI, WTI on ICT
SMAC | SYSTEM OUTAGE CAUSED BY MISCREANTS / MILITANT ACTIVITIES | Substation equipment failure caused by miscreants / militant activities
SNCC | OUTAGE OF SYSTEM DUE TO NATURAL CALAMITIES | Substation equipment outage due to Natural calamities
SPLT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Line tripped due to PLCC mal-operation
SPLU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Line tripped due to PLCC mal-operation of other agency
SPRD | SYSTEM CONSTRAINTS | Transformer hand tripped for Power Regulation on RLDC instruction
SRET | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Reactor Differential, REF, Backup impedance, Buchholz protection including NGR protections
SREU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Reactor Differential, REF, Backup impedance, Buchholz protection including NGR protections
SRMT | SUB-STATION FAULTS IN POWERGRID SUB-STATIONS INCLUDING THE BAYS OWNED BY POWERGRID TERMINATED AT SEB SUB-STATIONS | Relay Mal-operation
SRMU | SUBSTATION FAULTS IN OTHER AGENCIES CAUSING OUTAGE TO POWERGRID | Relay Mal-operation
SVRD | SYSTEM CONSTRAINTS | Bus reactor hand tripped for Voltage Regulation on RLDC instruction

## 1506 WR 2
Name of Transmission Licensee : POWER GRID CORPORATION OF INDIA LTD., WETSTERN REGION - II
Month: JUNE 2015
ANNEXURE - A
Sl No: | Unique ID of transmission Element | Element Name | Description (Length/Nos./MVA/MVAr/MW/etc.) | Region | Type of failure | OUTAGE |  | RESTORATION |  | Details of Outage |  |  |  |  | Total outage in days (1) | Durationn of outage attributable to (in Hrs) |  |  |  | Restoration Time as per Regulation 5(b) (in days) (2) | Whether Restoration Time more than normative (Y/N) | Difference between Actual and Norm 1-2 | Detailed Reason(s) for Outage | Outage Certifying Agency and Reference Document | % Availability as certified by certifying agency
[6 empty] | Date | Time | Date | Time | no. of insulator failed | No. of towers damaged | Snapping of phase conductor | Failure of earth wire | Failure of Bushing |  | ISTS Licensee | OTHERS | System Constraints/ Natural calamity / Militancy | Deemed Available
1 | WR2L1 | 400kV SATPURA-ITARSI | 79 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Agency: WRPC Mumbai | 100%
2 | WR2L2 | 400kV ITARSI-INDORE(MP) 1 | 207 | WR-II | -- | 2015-06-11 | 15:44 | 2015-06-11 | 18:06 | -- | -- | -- | -- | -- | -- | 0 | 2.37 | 0 | 0 | -- | -- | -- | Line H/T to charge line along with L/R, but due to Buchholze relay operation (at Indore MPEB end) line charged without L/R. |  | 100%
2 | WR2L2 | 400kV ITARSI-INDORE(MP) 1 | 207 | WR-II | -- | 2015-06-12 | 17:55 | 2015-06-12 | 18:49 | -- | -- | -- | -- | -- | -- | 0 | 0.9 | 0 | 0 | -- | -- | -- | Line H/T to take L/R into service along with line at Indore (MPPTCL). But Due to Isolator problem, line taken into service without LR. (Bays at MPPTCL station.) |  | 100%
2 | WR2L2 | 400kV ITARSI-INDORE(MP) 1 | 207 | WR-II | -- | 2015-06-15 | 11:19 | 2015-06-15 | 12:07 | -- | -- | -- | -- | -- | -- | 0 | 0.8 | 0 | 0 | -- | -- | -- | Line H/T to take line reactor into service at Indore(MP). |  | 100%
3 | WR2L3 | 400kV ITARSI-INDORE(MP) 2 | 214 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
4 | WR2L4 | 400kV INDORE(MP)-ASOJ 1 | 289 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
5 | WR2L5 | 400kV INDORE(MP)-ASOJ 2 | 273 | WR-II | -- | 2015-06-06 | 13:15 | 2015-06-06 | 13:40 | -- | -- | -- | -- | -- | -- | 0.42 | 0 | 0 | 0 | -- | -- | -- | line H/T to isolate L/R at Indore MPPTCL end and charged with out L/R. |  | 99.94%
6 | WR2L6 | 400kV VINDHYACHAL-JABALPUR 1 | 360 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
7 | WR2L7 | 400kV VINDHYACHAL-JABALPUR 2 | 360 | WR-II | -- | 2015-06-04 | 10:28 | 2015-06-04 | 16:37 | -- | -- | -- | -- | -- | -- | 6.15 | 0 | 0 | 0 | -- | -- | -- | Line H/T For AMP of Line terminal equipments. Line was made ready for charging from 16:37 hrs but charging delay due to problem at Vchal NTPC end. |  | 99.14%
7 | WR2L7 | 400kV VINDHYACHAL-JABALPUR 2 | 360 | WR-II | -- | 2015-06-04 | 16:37 | 2015-06-04 | 18:11 | -- | -- | -- | -- | -- | -- | 0 | 1.57 | 0 | 0 | -- | -- | -- | Line H/T For AMP of Line terminal equipments. Line was made ready for charging from 16:37 hrs but charging delay due to problem at Vchal NTPC end. |  | 99.14%
7 | WR2L7 | 400kV VINDHYACHAL-JABALPUR 2 | 360 | WR-II | -- | 2015-06-30 | 11:18 | 2015-06-30 | 19:43 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.42 | -- | -- | -- | Line H/T to avail emergency S/D by NTPC. |  | 99.14%
8 | WR2L8 | 400kV JABALPUR-ITARSI 1 | 232 | WR-II | -- | 2015-06-24 | 13:35 | 2015-06-24 | 13:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.25 | -- | -- | -- | Line A/T on DT reciept at Jabalpur, during NTAMC work in progress at Itarsi end. |  | 100%
9 | WR2L9 | 400kV JABALPUR-ITARSI 2 | 232 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
10 | WR2L10 | 400kV GANDHAR-DEHGAM 1 | 157 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
11 | WR2L11 | 400kV GANDHAR-DEHGAM 2 | 157 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
13 | WR2L13 | 400kV VINDHYACHAL-SASAN | 21 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
14 | WR2L14 | 400kV SASAN-JABALPUR | 368 | WR-II | -- | 2015-06-22 | 10:39 | 2015-06-22 | 13:28 | -- | -- | -- | -- | -- | -- | 2.82 | 0 | 0 | 0 | -- | -- | -- | H/T to avail OCC approved S/D for AMP work. |  | 99.61%
15 | WR2L15 | 400kV VINDHYACHAL-JABALPUR 4 | 389 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
16 | WR2L16 | 400kV JABALPUR-ITARSI 3 | 234 | WR-II | -- | 2015-06-23 | 8:23 | 2015-06-23 | 11:07 | -- | -- | -- | -- | -- | -- | 2.73 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D to test Yph line CVT at Itarsi. Sudden raise in Voltage. |  | 99.62%
17 | WR2L17 | 400kV JABALPUR-ITARSI 4 | 234 | WR-II | -- | 2015-06-08 | 18:17 | 2015-06-08 | 18:17 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R Successful at both ends on B-Ph to E/F, F/L- 169Kms from Jabalpur & 34 Kms from Itarsi F/C- 1.9KAmps. |  | 99.92%
17 | WR2L17 | 400kV JABALPUR-ITARSI 4 | 234 | WR-II | -- | 2015-06-20 | 17:54 | 2015-06-20 | 18:08 | -- | -- | -- | -- | -- | -- | 0.23 | 0 | 0 | 0 | -- | -- | -- | Line H/T to isolate LR at Itarsi end due to heavy sparking & melting of terminal connector bolts of Y phase secondary bushing. |  | 99.92%
17 | WR2L17 | 400kV JABALPUR-ITARSI 4 | 234 | WR-II | -- | 2015-06-22 | 16:54 | 2015-06-22 | 17:14 | -- | -- | -- | -- | -- | -- | 0.33 | 0 | 0 | 0 | -- | -- | -- | Line H/T to attend Hotspot in reactor isolator at Jabalpur end. |  | 99.92%
18 | WR2L18 | 400kV ITARSI-KHANDWA 1 | 196.64 | WR-II | -- | 2015-06-08 | 10:36 | 2015-06-08 | 20:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.5 | -- | -- | -- | H/T to avail OCC approved S/D for NTAMC Work. |  | 100%
19 | WR2L19 | 400kV ITARSI-KHANDWA 2 | 196.64 | WR-II | -- | 2015-06-17 | 16:29 | 2015-06-18 | 16:46 | -- | -- | -- | -- | -- | -- | 0 | 0 | 24.28 | 0 | -- | -- | -- | Line A/T on B ph to E/F due to Insulator string flashedover at Location no. 364 ( Top phase )., F/L - 50km from Khandwa, F/C: 0.43kA, There was heavy wind & thunder storm & lightning during tripping time. |  | 100%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | 2015-06-11 | 3:20 | 2015-06-11 | 3:58 | -- | -- | -- | -- | -- | -- | 0 | 0.63 | 0 | 0 | -- | -- | -- | Line A/R successfully from Khandwa end only on R ph to E/F and tripped at Dhule MSETCL end. F/L - 196.4km from Khandwa end. F/C: 1.85kA. Line idle charged from Khandwa and synchronised at 03:58 hrs from Dhule end. |  | 99.96%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | 2015-06-12 | 17:44 | 2015-06-12 | 18:02 | -- | -- | -- | -- | -- | -- | 0.3 | 0 | 0 | 0 | -- | -- | -- | A/T on R ph to E/F. F/C - 2.21kA and F/L - 145.2KM from Khandwa. |  | 99.96%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | 2015-06-17 | 10:52 | 2015-06-17 | 18:13 | -- | -- | -- | -- | -- | -- | 0 | 0 | 7.35 | 0 | -- | -- | -- | Line H/T to avail S/D for insulator string replacement works. Heavy rain & lightening observed during tripping. The line charging is delayed by Dhule due to system high voltage. |  | 99.96%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | 2015-06-17 | 18:13 | 2015-06-17 | 19:36 | -- | -- | -- | -- | -- | -- | 0 | 1.38 | 0 | 0 | -- | -- | -- | After insulator string replacement works, the line charging was delayed by Dhule due to system high voltage. |  | 99.96%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | 2015-06-21 | 20:51 | 2015-06-21 | 20:51 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R sucessful at Both ends on Y ph to E/F, F/C: 2.3kA, F/L: 149kM from Khandwa. |  | 99.96%
20 | WR2L20 | 400kV KHANDWA-DHULE 1 | 261.78 | WR-II | -- | 2015-06-22 | 1:10 | 2015-06-22 | 2:03 | -- | -- | -- | -- | -- | -- | 0 | 0.88 | 0 | 0 | -- | -- | -- | Line A/R Successful on R-Ph to E/F at Khadnwa end but A/T at Dhuje MSTCL end, F/L- 176.3KMs from Khandwa, F/C- 1.98KAmps, Line charged from Khandwa End. |  | 99.96%
21 | WR2L21 | 400kV KHANDWA-DHULE 2 | 261.78 | WR-II | -- | 2015-06-09 | 12:09 | 2015-06-09 | 20:41 | -- | -- | -- | -- | -- | -- | 8.53 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by WR I. Line charged without L/R at Dhule end. |  | 98.82%
22 | WR2L22 | 400kV GANDHAR-SUGEN | 57 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
23 | WR2L23 | 400kV SUGEN-VAPI | 110 | WR-II | -- | 2015-06-04 | 10:55 | 2015-06-04 | 19:42 | -- | -- | -- | -- | -- | -- | 8.78 | 0 | 0 | 0 | -- | -- | -- | To attend the hot spot on Line Isolator at Vapi |  | 98.77%
23 | WR2L23 | 400kV SUGEN-VAPI | 110 | WR-II | -- | 2015-06-21 | 9:20 | 2015-06-21 | 12:58 | -- | -- | -- | -- | -- | -- | 0 | 3.63 | 0 | 0 | -- | -- | -- | Line H/ T to avail shutdown by Sugen. |  | 98.77%
24 | WR2L24 | 400kV GANDHAR(NTPC)-GANDHAR(GTEC) | 13 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
25 | WR2L25 | 220kV GANDHAR-HALDARWA 1 | 13 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-25 | 0:56 | -- | -- | -- | -- | -- | -- | 0 | 5.83 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa & Kawas end. |  | 100%
26 | WR2L26 | 220kV GANDHAR-HALDARWA 2 | 13 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-25 | 16:50 | -- | -- | -- | -- | -- | -- | 0 | 21.73 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa & Kawas end. |  | 100%
27 | WR2L27 | 220kV KAWAS-NAVSARI(GIS) 1 | 58.15 | WR-II | -- | 2015-06-23 | 3:15 | 2015-06-23 | 3:30 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.25 | 0 | -- | -- | -- | Line A/T on R Ph to E/F due to heavy rain and lightening, F/L- 53Kms from Navsari, F/C- 3.301KAmps. |  | 100%
27 | WR2L27 | 220kV KAWAS-NAVSARI(GIS) 1 | 58.15 | WR-II | -- | 2015-06-24 | 5:16 | 2015-06-24 | 13:07 | -- | -- | -- | -- | -- | -- | 0 | 0 | 7.85 | 0 | -- | -- | -- | Line A/T on B ph to E/F due to heavy rain & lightning storm, F/L - 43km from Navsari, F/C: 3.1kA. Special patrolling carryout but not abnormality observed. F/L - 43km from Navsari. |  | 100%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-06-13 | 6:40 | 2015-06-13 | 7:01 | -- | -- | -- | -- | -- | -- | 0.35 | 0 | 0 | 0 | -- | -- | -- | A/T on R ph to E/F. F/C - 3.15kA and F/L - 44KM from Kawas. |  | 99.95%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-06-24 | 5:06 | 2015-06-24 | 6:52 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.77 | 0 | -- | -- | -- | Line A/T on R ph to E/F, F/L - 58km from Navsari, F/C - 3.2kA.due to heavy rain & lightning storm. |  | 99.95%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-06-24 | 6:56 | 2015-06-24 | 13:10 | -- | -- | -- | -- | -- | -- | 0 | 0 | 6.23 | 0 | -- | -- | -- | Line A/T on R ph to E/F due to heavy rain & lightning storm, F/L - 40km from Navsari, F/C - 3.2kA. |  | 99.95%
28 | WR2L28 | 220kV KAWAS-NAVSARI(GIS) 2 | 58.15 | WR-II | -- | 2015-06-24 | 13:10 | 2015-06-26 | 16:59 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 51.82 | -- | -- | -- | Line Kept out on Voltage regulation as per WRLDC instructions from 13:10 dt. 24.06.15. Line test charged at 15:11/25.06.2015 but A/T on SOTF. Line again kept out Voltage regulation as per WRLDC instructions. |  | 99.95%
29 | WR2L29 | 220kV NAVSARI(GIS)-NAVSARI 1 | 31.33 | WR-II | -- | 2015-06-26 | 9:57 | 2015-06-26 | 16:50 | -- | -- | -- | -- | -- | -- | 6.88 | 0 | 0 | 0 | -- | -- | -- | Line A/T on R&Y ph to ph fault due to opening of Y phase jumper at location no. 164. F/C - Rph-5.6kA, Yph 2.9kA at Navsari (PG). |  | 99.04%
30 | WR2L30 | 220kV NAVSARI(GIS)-NAVSARI 2 | 31.33 | WR-II | -- | 2015-06-24 | 16:15 | 2015-06-24 | 17:56 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.68 | 0 | -- | -- | -- | Line H/T to avail S/D for rectification of suspension I type B ph Pilot string at Location no. 49 due to heavy rain & lightning storm. | Agency: WRPC Mumbai | 99.96%
30 | WR2L30 | 220kV NAVSARI(GIS)-NAVSARI 2 | 31.33 | WR-II | -- | 2015-06-26 | 9:57 | 2015-06-26 | 10:15 | -- | -- | -- | -- | -- | -- | 0.3 | 0 | 0 | 0 | -- | -- | -- | Line A/T on R&Y ph to ph fault from Navsari GIS end only & line was holding from Navsari GETCO end. F/C - Rph - 5.6 kA & Yph 2.9kA. |  | 99.96%
30 | WR2L30 | 220kV NAVSARI(GIS)-NAVSARI 2 | 31.33 | WR-II | -- | 2015-06-26 | 10:15 | 2015-06-26 | 16:50 | -- | -- | -- | -- | -- | -- | 0 | 6.58 | 0 | 0 | -- | -- | -- | Line was ready for charging since 10:15Hrs/26.06.15, but GETCO was not ready to synchronise the same. |  | 99.96%
31 | WR2L31 | 220kV KAWAS-VAV 1 | 37 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
32 | WR2L32 | 220kV KAWAS-VAV 2 | 37 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-24 | 20:42 | -- | -- | -- | -- | -- | -- | 0 | 1.6 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa & Kawas end. |  | 100%
33 | WR2L33 | 220kV KAWAS-HALDARWA 1 | 81 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-24 | 22:33 | -- | -- | -- | -- | -- | -- | 0 | 3.45 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa end. |  | 100%
34 | WR2L34 | 220kV KAWAS-HALDARWA 2 | 81 | WR-II | -- | 2015-06-05 | 18:49 | 2015-06-05 | 23:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 4.72 | -- | -- | -- | Line A/T due to breaking of earthwire betwen location no. 152-153 during stringing of OPGW installation for ULDC Master communication paln in WR. |  | 100%
34 | WR2L34 | 220kV KAWAS-HALDARWA 2 | 81 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-25 | 18:56 | -- | -- | -- | -- | -- | -- | 0 | 23.83 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa end. |  | 100%
35 | WR2L35 | 220kV KAKRAPAR-HALDARWA 1 | 74 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-24 | 22:08 | -- | -- | -- | -- | -- | -- | 0 | 3.03 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa & Kawas end. |  | 100%
35 | WR2L35 | 220kV KAKRAPAR-HALDARWA 1 | 74 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
36 | WR2L36 | 220kV KAKRAPAR-HALDARWA 2 | 74 | WR-II | -- | 2015-06-24 | 19:06 | 2015-06-25 | 15:15 | -- | -- | -- | -- | -- | -- | 0 | 20.15 | 0 | 0 | -- | -- | -- | Line A/T due to Bus fault at Haldarwa & Kawas end. |  | 100%
37 | WR2L37 | 220kV KAKRAPAR-VAV 1 | 43 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
38 | WR2L38 | 220kV KAKRAPAR-VAV 2 | 43 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
39 | WR2L39 | 220kV KAKRAPAR-VAPI 1 | 117 | WR-II | -- | 2015-06-05 | 14:05 | 2015-06-05 | 16:21 | -- | -- | -- | -- | -- | -- | 2.27 | 0 | 0 | 0 | -- | -- | -- | Line H/T to attend hot spot in line |  | 99.68%
39 | WR2L39 | 220kV KAKRAPAR-VAPI 1 | 117 | WR-II | -- | 2015-06-24 | 2:53 | 2015-06-24 | 14:47 | -- | -- | -- | -- | -- | -- | 0 | 0 | 11.9 | 0 | -- | -- | -- | Line A/T on Y ph to E/F, F/C: 15.12kA due to heavy rain & lightening storm. |  | 99.68%
40 | WR2L40 | 220kV KAKRAPAR-VAPI 2 | 117 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
41 | WR2L41 | 400kV VINDHYACHAL-SATNA 1 | 267 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
42 | WR2L42 | 400kV VINDHYACHAL-SATNA 2 | 267 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
43 | WR2L43 | 400kV VINDHYACHAL-SATNA 3 | 258.31 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
44 | WR2L44 | 400kV VINDHYACHAL-SATNA 4 | 258.31 | WR-II | -- | 2015-06-08 | 18:45 | 2015-06-08 | 19:39 | -- | -- | -- | -- | -- | -- | 0.9 | 0 | 0 | 0 | -- | -- | -- | Line H/T to isolate L/R due to heavy oil leakage on Bushing at Satna End. |  | 99.77%
44 | WR2L44 | 400kV VINDHYACHAL-SATNA 4 | 258.31 | WR-II | -- | 2015-06-14 | 16:55 | 2015-06-14 | 17:10 | -- | -- | -- | -- | -- | -- | 0.25 | 0 | 0 | 0 | -- | -- | -- | Line H/T to take L/R at Satna end into service, Charging delayed due to problem at NTPC end. |  | 99.77%
44 | WR2L44 | 400kV VINDHYACHAL-SATNA 4 | 258.31 | WR-II | -- | 2015-06-14 | 17:10 | 2015-06-14 | 17:42 | -- | -- | -- | -- | -- | -- | 0 | 0.53 | 0 | 0 | -- | -- | -- | Line H/T to take L/R at Satna end into service, Charging delayed due to problem at NTPC end. |  | 99.77%
44 | WR2L44 | 400kV VINDHYACHAL-SATNA 4 | 258.31 | WR-II | -- | 2015-06-18 | 14:57 | 2015-06-18 | 15:06 | -- | -- | -- | -- | -- | -- | 0.15 | 0 | 0 | 0 | -- | -- | -- | Line H/T to isolate L/R at Satna end to attend oil leakage. |  | 99.77%
44 | WR2L44 | 400kV VINDHYACHAL-SATNA 4 | 258.31 | WR-II | -- | 2015-06-18 | 16:12 | 2015-06-18 | 16:35 | -- | -- | -- | -- | -- | -- | 0.38 | 0 | 0 | 0 | -- | -- | -- | Line H/T for taking L/R into serviece at Satna end. |  | 99.77%
47 | WR2L45 | 400kV SATNA-BINA 1 | 276 | WR-II | -- | 2015-06-07 | 9:39 | 2015-06-08 | 19:23 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 33.73 | -- | -- | -- | Line H/T to avail OCC Approved S/D for line crossing work of HVDC Champa Kurukshetra. |  | 100%
48 | WR2L46 | 400kV SATNA-BINA 2 | 276 | WR-II | -- | 2015-06-07 | 9:40 | 2015-06-08 | 19:40 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34 | -- | -- | -- | Line H/T to avail OCC Approved S/D for line crossing work of HVDC Champa Kurukshetra. |  | 100%
49 | WR2L47 | 400kV BINA-BINA(MP) 1 | 0.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
50 | WR2L48 | 400kV BINA-BINA(MP) 2 | 0.742 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
51 | WR2L49 | 765kV BINA-GWALIOR 1 | 234.931 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
52 | WR2L50 | 765kV AGRA-GWALIOR 1 | 129.435 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
53 | WR2L51 | 400kV SATNA-BINA 4 | 272.586 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
54 | WR2L52 | 400kV SATNA-BINA 3 | 272.586 | WR-II | -- | 2015-06-24 | 12:43 | 2015-06-24 | 13:04 | -- | -- | -- | -- | -- | -- | 0.35 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for attending oil leakage from R phase Bushing of L/R at Satna. |  | 99.95%
55 | WR2L53 | 400kV BINA-SHUJALPUR 1 | 199.936 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
56 | WR2L54 | 400kV BINA-SHUJALPUR 2 | 199.936 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
57 | WR2L55 | 400kV SHUJALPUR-NAGDA 1 | 152.229 | WR-II | -- | 2015-06-25 | 4:42 | 2015-06-25 | 8:04 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.37 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
58 | WR2L56 | 400kV SHUJALPUR-NAGDA 2 | 152.229 | WR-II | -- | 2015-06-09 | 19:49 | 2015-06-09 | 19:49 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R Successful on R ph to E/F, F/L - 105.5km from Shujalpur, F/C:2.8kA. |  | 100%
59 | WR2L57 | 400kV NAGDA-DEHGAM 2 | 331.442 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
60 | WR2L58 | 400kV NAGDA-DEHGAM 1 | 331.442 | WR-II | -- | 2015-06-25 | 3:40 | 2015-06-25 | 16:40 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
61 | WR2L59 | 400kV SEONI-KHANDWA 1 | 351.729 | WR-II | -- | 2015-06-08 | 16:25 | 2015-06-08 | 16:25 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R Successful at both ends on B-Ph to E/F, F/L- 183Kms from Khandwa (WR-I juridiction), F/C- 3.718KAmps. |  | 100%
61 | WR2L59 | 400kV SEONI-KHANDWA 1 | 351.729 | WR-II | -- | 2015-06-12 | 16:19 | 2015-06-12 | 16:40 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.35 | 0 | -- | -- | -- | Line A/T on R ph to E/F due ot heavy rain & wind, F/C - 5.8KA, F/L - 38KM from Khandwa end. |  | 100%
61 | WR2L59 | 400kV SEONI-KHANDWA 1 | 351.729 | WR-II | -- | 2015-06-12 | 16:40 | 2015-06-12 | 19:41 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.02 | -- | -- | -- | Line ready for charging from 16:40 and kept out on Voltage regulation as per WRLDC instructions. |  | 100%
61 | WR2L59 | 400kV SEONI-KHANDWA 1 | 351.729 | WR-II | -- | 2015-06-19 | 12:35 | 2015-06-19 | 20:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.82 | -- | -- | -- | Line H/T to avail S/D by WR# I for CSD relay commissioing work at Seoni end. |  | 100%
61 | WR2L59 | 400kV SEONI-KHANDWA 1 | 351.729 | WR-II | -- | 2015-06-21 | 17:32 | 2015-06-21 | 17:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0 | -- | -- | -- | Line A/R sucessful at both ends on R ph to E/F, F/C - 2.4KA, F/L - 243kM from Khandwa. |  | 100%
62 | WR2L60 | 400kV SEONI-KHANDWA 2 | 351.729 | WR-II | -- | 2015-06-12 | 15:21 | 2015-06-12 | 20:53 | -- | -- | -- | -- | -- | -- | 5.53 | 0 | 0 | 0 | -- | -- | -- | Line along with FSC-II H/T to avail S/D by WR-I. |  | 99.23%
63 | WR2L61 | 400kV KHANDWA-RAJGARH 2 | 220.588 | WR-II | -- | 2015-06-05 | 18:38 | 2015-06-06 | 7:52 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.23 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 99.65%
63 | WR2L61 | 400kV KHANDWA-RAJGARH 2 | 220.588 | WR-II | -- | 2015-06-06 | 10:17 | 2015-06-06 | 19:46 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.48 | -- | -- | -- | H/T to avail OCC approved S/D for NTAMC Work. |  | 99.65%
63 | WR2L61 | 400kV KHANDWA-RAJGARH 2 | 220.588 | WR-II | -- | 2015-06-06 | 21:38 | 2015-06-07 | 0:11 | -- | -- | -- | -- | -- | -- | 2.55 | 0 | 0 | 0 | -- | -- | -- | Line A/T due to Main2 (Omega) relay mal-operation at Khandwa end only. |  | 99.65%
63 | WR2L61 | 400kV KHANDWA-RAJGARH 2 | 220.588 | WR-II | -- | 2015-06-07 | 0:11 | 2015-06-09 | 11:22 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 59.18 | -- | -- | -- | Line kept out on Voltage regulation as per WRLDC instructions. |  | 99.65%
63 | WR2L61 | 400kV KHANDWA-RAJGARH 2 | 220.588 | WR-II | -- | 2015-06-15 | 18:21 | 2015-06-17 | 10:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 39.75 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 99.65%
64 | WR2L62 | 400kV SARDAR SAROVAR-RAJGARH 1(LILO) | 4.01 | WR-II | -- | 2015-05-27 | 11:18 | 2015-06-04 | 10:03 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 82.05 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
64 | WR2L62 | 400kV SARDAR SAROVAR-RAJGARH 1(LILO) | 4.01 | WR-II | -- | 2015-06-12 | 2:50 | 2015-06-17 | 7:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 124.47 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
64 | WR2L62 | 400kV SARDAR SAROVAR-RAJGARH 1(LILO) | 4.01 | WR-II | -- | 2015-06-19 | 0:14 | 2015-06-25 | 10:22 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 154.13 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
65 | WR2L63 | 400kV SARDAR SAROVAR-RAJGARH 2(LILO) | 4.01 | WR-II | -- | 2015-06-25 | 16:41 | 2015-06-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 127.32 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
66 | WR2L64 | 400kV RAJGARH-NAGDA 1(LILO) | 4.12 | WR-II | -- | 2015-06-09 | 10:22 | 2015-06-11 | 20:35 | -- | -- | -- | -- | -- | -- | 0 | 58.22 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by MPPTCL. |  | 100%
66 | WR2L64 | 400kV RAJGARH-NAGDA 1(LILO) | 4.12 | WR-II | -- | 2015-06-12 | 15:31 | 2015-06-12 | 16:03 | -- | -- | -- | -- | -- | -- | 0 | 0.53 | 0 | 0 | -- | -- | -- | Line A/T at Nagda end only on Y ph to E/F, F/C - 5.9KA and F/L:15.2kM from Rajgarh. Faulty section comes under MPPTCL Jurisdictions. |  | 100%
66 | WR2L64 | 400kV RAJGARH-NAGDA 1(LILO) | 4.12 | WR-II | -- | 2015-06-15 | 11:04 | 2015-06-15 | 20:32 | -- | -- | -- | -- | -- | -- | 0 | 9.47 | 0 | 0 | -- | -- | -- | Line H/T as S/D by MPPTCL. |  | 100%
66 | WR2L64 | 400kV RAJGARH-NAGDA 1(LILO) | 4.12 | WR-II | -- | 2015-06-19 | 12:44 | 2015-06-19 | 21:34 | -- | -- | -- | -- | -- | -- | 0 | 8.83 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D taken by MPPTCL. |  | 100%
66 | WR2L64 | 400kV RAJGARH-NAGDA 1(LILO) | 4.12 | WR-II | -- | 2015-06-20 | 12:36 | 2015-06-20 | 14:54 | -- | -- | -- | -- | -- | -- | 0 | 2.3 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D taken by MPPTCL. |  | 100%
67 | WR2L65 | 400kV RAJGARH-NAGDA 2(LILO) | 4.12 | WR-II | -- | 2015-06-24 | 17:22 | 2015-06-30 | 14:07 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 140.75 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-06-04 | 10:16 | 2015-06-04 | 20:48 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.53 | -- | -- | -- | H/T to avail OCC approved S/D for NTAMC Work. | Agency: WRPC Mumbai | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-06-06 | 21:36 | 2015-06-06 | 22:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.58 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-06-10 | 3:44 | 2015-06-13 | 11:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 79.67 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-06-13 | 15:08 | 2015-06-15 | 10:38 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 43.5 | -- | -- | -- | Line H/T on power regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-06-18 | 0:03 | 2015-06-18 | 7:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.2 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
68 | WR2L66 | 400kV KHANDWA-RAJGARH 1 | 220.588 | WR-II | -- | 2015-06-19 | 0:01 | 2015-06-30 | 9:16 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 273.25 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
69 | WR2L67 | 220kV VAPI-MAGARWADA 1 | 25.71 | WR-II | -- | 2015-06-24 | 3:21 | 2015-06-24 | 9:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 6.27 | 0 | -- | -- | -- | Line A/T on R ph to E/F due to snapping of eathwire during lightening & heavy rain between span 87-89-& 94-95. F/L - 220km from Vapi, F/C - 4.2kA. Line test charged at 04:33Hrs but did not hold & A/T on R ph to E/F, F/L - 22.67km from Vapi, F/C: 8.4kA. |  | 100%
70 | WR2L68 | 220kV VAPI-MAGARWADA 2 | 25.71 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
71 | WR2L69 | 220kV VAPI-KHARADPARA 1 | 29.66 | WR-II | -- | 2015-06-22 | 12:07 | 2015-06-22 | 16:35 | -- | -- | -- | -- | -- | -- | 4.47 | 0 | 0 | 0 | -- | -- | -- | Line A/T on Y ph to E/F, F/C:9.5kA and F/L:11.3kM from Vapi end. Line charged from Vapi but during synchro at Kharadpada end, line tripped on SOTF as the Jumper at location no. 45 was opened. As Ckt-I was charged from Vapi then Hand tripped the same. |  | 99.38%
72 | WR2L70 | 220kV VAPI-KHARADPARA 2 | 29.66 | WR-II | -- | 2015-06-22 | 12:07 | 2015-06-22 | 13:11 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.07 | 0 | -- | -- | -- | Line A/T on B ph to E/F due to heavy wind and severe lighting at the time of tripping, F/C: 6.7kA and F/L: 17kM from Vapi end. |  | 100%
72 | WR2L70 | 220kV VAPI-KHARADPARA 2 | 29.66 | WR-II | -- | 2015-06-24 | 12:36 | 2015-06-24 | 12:47 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.18 | 0 | -- | -- | -- | Line A/T on B ph to E/F due to breaking of earth wire at location no. 105/106, during lightening & heavy rain, F/C: 4.4kA and F/L:100% from Vapi. |  | 100%
72 | WR2L70 | 220kV VAPI-KHARADPARA 2 | 29.66 | WR-II | -- | 2015-06-24 | 17:04 | 2015-06-24 | 17:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.55 | 0 | -- | -- | -- | Line H/T to avail S/D to removal of broken Earth wire at Location no. 105/106 failed due to heavy rain and lightning storm. |  | 100%
73 | WR2L71 | 765kV BINA-GWALIOR 2 | 233.652 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
74 | WR2L72 | 765kV AGRA-GWALIOR 2 | 127.934 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
75 | WR2L73 | 765kV SEONI-BINA 1 | 292.046 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
76 | WR2L74 | 400kV DAMOH-BHOPAL 1 | 214.471 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
77 | WR2L75 | 400kV DAMOH-BHOPAL 2 | 213.8 | WR-II | -- | 2015-06-12 | 14:59 | 2015-06-12 | 15:29 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.5 | 0 | -- | -- | -- | Line A/T on R ph to E/F due to heavy rain and lightening. F/C - 5.3kA and F/L - 22kM from Damoh. |  | 100%
78 | WR2L76 | 220kV VAPI-KHADOLI 1 | 28.549 | WR-II | -- | 2015-06-24 | 5:45 | 2015-06-24 | 7:07 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.37 | 0 | -- | -- | -- | Line A/T on B ph to E/F due to heavy rain & lightning storm, F/L - 7.17km from Vapi, F/C -10.5kA. |  | 100%
80 | WR2L77.1 | 220kV VAPI-SAYALI | 18.3 | WR-II | -- | 2015-06-07 | 16:04 | 2015-06-07 | 17:28 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.4 | 0 | -- | -- | -- | Line A/T on Y Ph to E/F due to heavy rain around DNH S/S, F/C- 6.1KAmps, F/L- 18.43Kms from Vapi & 3.32Kms from Sayali. |  | 100%
81 | WR2L77.2 | 220kV SAYALI-KHADOLI | 12.235 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
82 | WR2L78 | 400kV DAMOH-BIRSINGHPUR 1 | 228.474 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
83 | WR2L79 | 400kV DAMOH-BIRSINGHPUR 2 | 228.474 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
84 | WR2L80 | 400kV DEHGAM-PIRANA 1 | 46.656 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
85 | WR2L81 | 400kV DEHGAM-PIRANA 2 | 46.656 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
86 | WR2L82 | 400kV MUNDRA-BHACHAU 1 | 99.468 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
87 | WR2L83 | 400kV MUNDRA-BHACHAU 2 | 99.468 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
88 | WR2L84 | 400kV BHACHAU-RANCHHODPURA 1 | 282.856 | WR-II | -- | 2015-06-23 | 8:23 | 2015-06-23 | 15:52 | -- | -- | -- | -- | -- | -- | 7.48 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D to rectify line clearence problem in the line. |  | 98.96%
89 | WR2L85 | 400kV BHACHAU-RANCHHODPURA 2 | 282.856 | WR-II | -- | 2015-06-07 | 20:26 | 2015-06-07 | 20:53 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0.45 | 0 | -- | -- | -- | Line A/T on Y-Ph to E/F, F/L- 145.7Kms from Bhachau, F/C- 3.03KAmps. Heavy wind & rain & lightning noticed at the instant of tripinng. |  | 100%
90 | WR2L86 | 400kV MUNDRA-LIMBDI 1 | 314.053 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-02 | 23:46 | 2015-06-03 | 2:30 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 2.73 | -- | -- | -- | Line A/T on Y ph to E/F due to OPGW installed on 400kV Bachau - Ranchodpura line for ULDC master communication plan in WR, at crossing point of 400kV Mudnra - Halvad line . F/L = 97.5 kms from Halvad. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-03 | 17:02 | 2015-06-03 | 17:44 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.7 | -- | -- | -- | Line A/T on R&Y ph to E/F due to OPGW installed on 400kV Bachau - Ranchodpura line for ULDC master communication plan in WR, at crossing point of 400kV Mudnra - Halvad line . F/L = 122.6 kms from Halvad. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-04 | 16:53 | 2015-06-04 | 17:33 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.67 | -- | -- | -- | Line A/T on Y ph to E/F due to OPGW installed on 400kV Bachau - Ranchodpura line for ULDC Master communication plan in WR, at crossing point of 400kV Mudnra - Halvad line. Problem has been rectifeid . F/L = 60.9 kms from Halvad. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-08 | 17:06 | 2015-06-08 | 18:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.2 | -- | -- | -- | Line A/T on Y ph to E/F due to OPGW installed on 400kV Bachau - Ranchodpura line for ULDC Master communication plan in WR, at crossing point of 400kV Mudnra - Halvad line. Problem has been rectifeid . F/L - 145 kms from Halvad & 126kM from Mundra, F/C - 3.8kA. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-10 | 15:58 | 2015-06-10 | 17:56 | -- | -- | -- | -- | -- | -- | 0 | 1.97 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by CGPL. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-12 | 8:32 | 2015-06-12 | 16:13 | -- | -- | -- | -- | -- | -- | 7.68 | 0 | 0 | 0 | -- | -- | -- | Line H/T to for providing Pilot insulator strings in all three phases at location no.165 (DD+6). |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-16 | 16:50 | 2015-06-16 | 17:13 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.38 | -- | -- | -- | Line A/T on Y ph to E/F due to OPGW installed on 400kV Bachau - Ranchodpura line for ULDC Master communication plan in WR, at crossing point of 400kV Mudnra - Halvad line. Problem has been rectifeid . F/L = 97.55 kms from Halvad. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-20 | 9:03 | 2015-06-20 | 18:48 | -- | -- | -- | -- | -- | -- | 0 | 9.75 | 0 | 0 | -- | -- | -- | Line H/T to facilitate S/D to CGPL. |  | 98.92%
92 | WR2L87.1 | 400kV MUNDRA-HALVAD | 221.923 | WR-II | -- | 2015-06-30 | 9:54 | 2015-06-30 | 13:55 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 4.02 | -- | -- | -- | Line H/T to avail emergency S/D by GETCO. |  | 98.92%
93 | WR2L87.2 | 400kV HALVAD-LIMBDI | 92.13 | WR-II | -- | 2015-06-08 | 11:29 | 2015-06-08 | 18:45 | -- | -- | -- | -- | -- | -- | 7.27 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC Approved outage for fixing of dislocated spacers at various location of TL. |  | 98.99%
94 | WR2L88 | 765kV SATNA-BINA 1 | 274.164 | WR-II | -- | 2015-06-27 | 12:31 | 2015-06-27 | 15:09 | -- | -- | -- | -- | -- | -- | 2.63 | 0 | 0 | 0 | -- | -- | -- | Line H/T for swapping of R phase L/R with spare L/R due to DGA Violation. |  | 99.53%
94 | WR2L88 | 765kV SATNA-BINA 1 | 274.164 | WR-II | -- | 2015-06-27 | 16:42 | 2015-06-27 | 17:26 | -- | -- | -- | -- | -- | -- | 0.73 | 0 | 0 | 0 | -- | -- | -- | Line A/T due to accidental wire opening while checking current in spare reactor at Bina. |  | 99.53%
95 | WR2L89 | 765kV SATNA-BINA 2 | 275.635 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
96 | WR2L90 | 765kV BINA-INDORE(POOLING) 1 | 311.81 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
97 | WR2L91 | 400kV GANDHAR-NAVSARI(GIS) 2 | 102.152 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
98 | WR2L92 | 400kV GANDHAR-NAVSARI(GIS) 1 | 102.152 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Agency: WRPC Mumbai | 100%
99 | WR2L93 | 400kV MUNDRA-JETPUR 1 | 336.742 | WR-II | -- | 2015-06-16 | 11:25 | 2015-06-16 | 13:15 | -- | -- | -- | -- | -- | -- | 1.83 | 0 | 0 | 0 | -- | -- | -- | Line H/T for taking oil sample of CT at Jetpur end. |  | 99.75%
100 | WR2L94 | 400kV MUNDRA-JETPUR 2 | 336.742 | WR-II | -- | 2015-06-16 | 13:22 | 2015-06-16 | 14:39 | -- | -- | -- | -- | -- | -- | 1.28 | 0 | 0 | 0 | -- | -- | -- | Line H/T for taking oil sample of CT at Jetpur end. |  | 99.82%
101 | WR2L95 | 400kV VINDHYACHAL(NTPC)-VINDHYACHAL(POOLING) 1 | 28.55 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
102 | WR2L96 | 400kV VINDHYACHAL(NTPC)-VINDHYACHAL(POOLING) 2 | 28.55 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
103 | WR2L97 | 400kV VINDHYACHAL(POOLING)-SASAN 1 | 5.443 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
104 | WR2L98 | 400kV VINDHYACHAL(POOLING)-SASAN 2 | 5.443 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
105 | WR2L99 | 765kV SASAN-SATNA 1 | 245.7 | WR-II | -- | 2015-06-23 | 9:09 | 2015-06-23 | 19:50 | -- | -- | -- | -- | -- | -- | 0 | 10.68 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D by SASAN. |  | 100%
105 | WR2L99 | 765kV SASAN-SATNA 1 | 245.7 | WR-II | -- | 2015-06-24 | 9:06 | 2015-06-24 | 19:18 | -- | -- | -- | -- | -- | -- | 0 | 10.2 | 0 | 0 | -- | -- | -- | Line H/T to avail OCC approved S/D by Sasan. |  | 100%
106 | WR2L100 | 400kV BINA-BINA(MP) 3 | 0.62 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
109 | WR2L101.1.1 | 400kV NAVSARI(GIS)-MAGARWADA(GIS) 1 | 125.8 | WR-II | -- | 2015-06-25 | 9:40 | 2015-06-25 | 18:23 | -- | -- | -- | -- | -- | -- | 8.72 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for replacement of CVT at Navsari. |  | 98.79%
110 | WR2L101.1.2 | 400kV KALA(GIS)-MAGARWADA(GIS) 1 | 52.9 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
111 | WR2L101.2 | 400kV KALA(GIS)-VAPI 1 | 49 | WR-II | -- | 2015-06-07 | 10:30 | 2015-06-07 | 14:53 | -- | -- | -- | -- | -- | -- | 4.38 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for Jumper replacement work at location no. 38A/0. |  | 99.39%
112 | WR2L102 | 400kV VAPI-NAVASARI(GIS) 2 | 116.879 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
113 | WR2L103 | 765kV SASAN-SATNA 2 | 242.23 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
114 | WR2L104 | 400kV BINA-BINA(MP) 4 | 0.62 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
115 | WR2L105 | 400kV INDORE(MP)-INDORE(POOLING) 1 | 49.73 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
116 | WR2L106 | 400kV INDORE(MP)-INDORE(POOLING) 2 | 49.73 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
117 | WR2L107 | 400kV JABALPUR-JABALPUR(POOLING) 1 | 15.456 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
118 | WR2L108 | 400kV JABALPUR-JABALPUR(POOLING) 2 | 15.456 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
119 | WR2L109 | 765kV JABALPUR(POOLING)-BINA 1 | 229.74 | WR-II | -- | 2015-06-12 | 11:11 | 2015-06-12 | 11:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.35 | -- | -- | -- | A/T at Bina end only due to DT received from JABALPUR(POOLING). PLCC testing work is under progress at JABALPUR(POOLING) for under construction Dharamjaygarh # 3/4 line. |  | 100%
120 | WR2L110 | 765kV JABALPUR(POOLING)-BINA 2 | 229.74 | WR-II | -- | 2015-06-15 | 11:31 | 2015-06-15 | 14:46 | -- | -- | -- | -- | -- | -- | 3.25 | 0 | 0 | 0 | -- | -- | -- | Line H/T due to oil Leakage from NCT of Reactor at Bina end. |  | 99.55%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-06-01 | 15:35 | 2015-06-01 | 16:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.25 | 0 | -- | -- | -- | Line A/T on R phase to E/F due to high speed whrilwind near Satna area , F/L - 293km from Gwalior, Satna = 72.46 kms. F/C: 1.68kA. |  | 100%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-06-02 | 17:18 | 2015-06-02 | 18:39 | -- | -- | -- | -- | -- | -- | 0 | 0 | 1.35 | 0 | -- | -- | -- | Line A/T on B ph to E/F due to high speed wind with gale storm in that area, F/L - 33km from Gwalior, F/C: 8.41kA. |  | 100%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-06-24 | 1:29 | 2015-06-24 | 2:36 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.12 | -- | -- | -- | Line A/T on Y ph to E/F due to hanging of PP rope between location no. 661-674 used for OPGW installtaion, F/L - 84.75km from Gwalior & 255km from Satna, F/C - 3.12kA (Gwalior) & 2.48kA (Satna). |  | 100%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-06-25 | 10:17 | 2015-06-25 | 10:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.55 | -- | -- | -- | Line A/T on Y ph to E/F due to slipping of PP rope between location no. 661-674 used for OPGW installtaion for Master communication plan of WR, F/C - 5.4kA and F/L - 83 KM from Gwalior. |  | 100%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-06-25 | 11:05 | 2015-06-25 | 21:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.22 | -- | -- | -- | A/T on Y ph to E/F due to slipping of PP rope between location no. 661-674 used for OPGW installtaion for Master communication scheme plan , F/C - 5.4kA and F/L - 83 KM from Gwalior. |  | 100%
121 | WR2L111 | 765kV SATNA-GWALIOR 1 | 336.63 | WR-II | -- | 2015-06-26 | 9:51 | 2015-06-26 | 19:58 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 10.12 | -- | -- | -- | Line H/T to avail S/D for Attending broken pilot wire of OPGW between location nos. 661-674. |  | 100%
122 | WR2L112 | 400kV PIRANA-ASOJ 1 | 143.539 | WR-II | -- | 2015-04-19 | 20:50 | 2015-05-31 | 3:52 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 723.87 | -- | -- | -- | Line made ready and idle charged from Pirana end upto Vadodara SS gantry for connecting 765kV Dhule - Vadodara line M/s BDTCL at 400kV level as contigency measures. But lines finally charged as per original approved schemes i.e. 400kV Vadodara (Pooling)-Asoj # 1 & 400kV Vadodara (Pooling) - Pirana #2 lines on 31.05.15 |  | 100%
122 | WR2L112 | 400kV PIRANA-ASOJ 1 | 143.539 | WR-II | -- | 2015-06-26 | 11:49 | 2015-06-27 | 22:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 34.18 | -- | -- | -- | Shutdown availed for removing contigency arrangement of 400kV Pirana-Asoj line & connecting same at Vadodara GIS as per approved scheme i.e.400kV Vadodara-Pirana # I( First time charged at 21:29Hrs/Code: LD06-3125) & 400kV Vadodara-Asoj # 2( First time charged at 22:00Hrs/ Code: LD06-3126). |  | 100%
123 | WR2L113 | 400kV PIRANA-ASOJ 2 | 143.539 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
124 | WR2L114 | 400kV INDORE(POOLING)-ASOJ 3 | 321.203 | WR-II | -- | 2015-05-23 | 9:31 | 2015-06-06 | 2:45 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 122.75 | -- | -- | -- | Upgradation of 765kV Indore - Asoj # 3 from 400kV level to 765kV level. Line was charged under contingency scheme at 400kV level. Shutdown availed for removing jumper, shifting of line to new tower and from 400kV switchyard to 765kV yard at Indore and terminating the line at Vadodara end. Lines finally charged as per original approved schemes i.e. 400kV Indore (PG) - Indore (MP) Ckt.2 and 765kV Indore (PG) - Vadodara (pooling) line. Also testing of all protection and PLCC system at Indore and Vadodara ends before commissioning carried out. |  | 100%
125 | WR2L115 | 765kV BINA-GWALIOR 3 | 231.27 | WR-II | -- | 2015-06-02 | 17:18 | 2015-06-20 | 19:23 | -- | -- | -- | -- | -- | -- | 0 | 0 | 434.08 | 0 | -- | -- | -- | Line A/T on Y & B ph to ph fault due to collapse of 6 nos. towers (From location no. 573 to 578) due to high speed whrilwind alongwith gale storm., F/L - 16km from Gwalior, F/C: 11kA. |  | 100%
126 | WR2L116 | 765kV SATNA-GWALIOR 2 | 342.15 | WR-II | -- | 2015-06-25 | 18:32 | 2015-06-25 | 22:00 | -- | -- | -- | -- | -- | -- | 3.47 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D to for Rectification of shut down nature defects & replacement of CVT. |  | 99.52%
127 | WR2L117 | 400kV ANUPPUR-JABALPUR(POOLING) 1 | 246.409 | WR-II | -- | 2015-06-06 | 5:58 | 2015-06-07 | 18:16 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.3 | -- | -- | -- | Line H/T for Crossing work of 765kV JABALPUR (POOLING) - Dharamjaygarh TL. |  | 100%
128 | WR2L118 | 400kV ANUPPUR-JABALPUR(POOLING) 2 | 246.409 | WR-II | -- | 2015-06-06 | 5:58 | 2015-06-07 | 18:25 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 36.45 | -- | -- | -- | Line H/T for Crossing work of 765kV JABALPUR (POOLING) - Dharamjaygarh TL. |  | 100%
129 | WR2L119 | 400kV BHACHAU-VARSANA 1 | 9.3 | WR-II | -- | 2015-06-24 | 3:05 | 2015-06-25 | 14:51 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 35.77 | -- | -- | -- | Line H/T on Voltage regulation as per WRLDC instructions. |  | 100%
130 | WR2L120 | 400kV BHACHAU-VARSANA 2 | 9.3 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-10 | 19:02 | 2015-06-10 | 19:47 | -- | -- | -- | -- | -- | -- | 0 | 0.75 | 0 | 0 | -- | -- | -- | Line A/T at Tarapur end only due to suspected some problem at Tarapur end. |  | 97.94%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-10 | 22:18 | 2015-06-11 | 1:15 | -- | -- | -- | -- | -- | -- | 0 | 2.95 | 0 | 0 | -- | -- | -- | Line A/T at Tarapur end only. Charging delayed due to problem at Tarapur end. |  | 97.94%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-11 | 9:45 | 2015-06-11 | 12:44 | -- | -- | -- | -- | -- | -- | 0 | 2.98 | 0 | 0 | -- | -- | -- | Line A/T due to Relay maloperation at Tarapur (MSEB) end. |  | 97.94%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-11 | 15:33 | 2015-06-11 | 18:26 | -- | -- | -- | -- | -- | -- | 0 | 2.88 | 0 | 0 | -- | -- | -- | Line A/T due to Relay maloperation at Tarapur (MSEB) end. | Agency: WRPC Mumbai | 97.94%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-15 | 11:25 | 2015-06-15 | 19:52 | -- | -- | -- | -- | -- | -- | 0 | 8.45 | 0 | 0 | -- | -- | -- | Line H/T on emergency basis by Tarapur. |  | 97.94%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-19 | 10:31 | 2015-06-19 | 15:02 | -- | -- | -- | -- | -- | -- | 4.52 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D to attend hot spot at location nos. 43 & 45. |  | 97.94%
131 | WR2L121 | 220kV TARAPUR-BOISAR | 20.56 | WR-II | -- | 2015-06-25 | 10:44 | 2015-06-25 | 20:40 | -- | -- | -- | -- | -- | -- | 9.93 | 0 | 0 | 0 | -- | -- | -- | Line H/T to avail S/D for Rectification of shut down nature defects & replacement of CVT. |  | 97.94%
132 | WR2L122 | 400kV TARAPUR-PADGHE 1 | 91.119 | WR-II | -- | 2015-06-29 | 9:33 | 2015-06-29 | 19:32 | -- | -- | -- | -- | -- | -- | 9.98 | 0 | 0 | 0 | -- | -- | -- | Line H/T for rectification of line defects. |  | 98.61%
133 | WR2L123 | 400kV TARAPUR-PADGHE 2 | 91.119 | WR-II | -- | 2015-06-30 | 9:13 | 2015-06-30 | 19:20 | -- | -- | -- | -- | -- | -- | 10.12 | 0 | 0 | 0 | -- | -- | -- | Line H/T for rectification of line defects. |  | 98.59%
134 | WR2L124 | 400kV BOISAR-PADGHE | 101 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
135 | WR2L125 | 400kV TARAPUR-BOISAR 1 | 20.881 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
136 | WR2L126 | 400kV TARAPUR-BOISAR 2 | 20.881 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
137 | WR2L127 | 400kV VAPI-BOISAR | 94 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
138 | WR2L128 | 400kV KALA(GIS)-VAPI 2 | 52.947 | WR-II | -- | 2015-06-02 | 9:43 | 2015-06-02 | 12:20 | -- | -- | -- | -- | -- | -- | 2.62 | 0 | 0 | 0 | -- | -- | -- | Line H/T to connect one of sub-condctior B phase Jumper at Location no. 65. |  | 99.64%
139 | WR2L129 | 400kV NAVSARI(GIS)-MAGARWADA(GIS) 2 | 125.8 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
140 | WR2L130 | 400kV KALA(GIS)-MAGARWADA(GIS) 2 | 53.33 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
141 | WR2L131 | 765kV VINDHYACHAL(POOLING)-SATNA 1 | 264 | WR-II | -- | 2015-06-10 | 15:12 | 2015-06-10 | 16:39 | -- | -- | -- | -- | -- | -- | 1.45 | 0 | 0 | 0 | -- | -- | -- | Line A/T due to mal operation of reactor OTI at Satna. DT received at Vindhyachal Pooling. |  | 98.13%
142 | WR2L132 | 765kV SASAN-VINDHYACHAL(POOLING) 1 | 10 | WR-II | -- | 2015-06-02 | 11:01 | 2015-06-02 | 18:50 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 7.82 | -- | -- | -- | Line H/T for construction works by NR-I. |  | 100%
143 | WR2L133 | 400KV VADODARA(GIS)-PIRANA 2 | 132.5 | WR-II | -- | 2015-06-10 | 10:17 | 2015-06-10 | 10:55 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 0.63 | -- | -- | -- | Line A/T on R ph to E/F at Vadodara GIS end only during testing activities in new Vadodara station. Line charged from Pirana end. |  | 100%
144 | WR2L134 | 400KV VADODARA(GIS)-ASOJ 1 | 13.82 | WR-II | -- | 2015-06-27 | 15:09 | 2015-06-27 | 18:25 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.27 | -- | -- | -- | H/T due to induction on removing cotingent arrangement of 400kV Pirana-Asoj line & connecting same at Vadodara as per approved scheme i.e.400kV Vadodara-Pirana # I & 400kV Vadodara-Asoj # 2 |  | 100%
145 | WR2L135 | 400KV VADODARA(GIS)-PIRANA 1 | 132.5 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
146 | WR2L136 | 400KV VADODARA(GIS)-ASOJ 2 | 13.82 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
147 | WR2L137 | 765KV VADODARA(GIS)-INDORE(POOLING) 1 | 321.203 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
148 | WR2T1 | ICT1 JABALPUR 400/220kV | 315 | WR-II | -- | 2015-06-09 | 12:56 | 2015-06-09 | 18:58 | -- | -- | -- | -- | -- | -- | 0 | 6.03 | 0 | 0 | -- | -- | -- | H/T to avail emergency outage by MPPTCL. |  | 100%
149 | WR2T2 | ICT2 JABALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
150 | WR2T3 | ICT1 DEHGAM 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
151 | WR2T4 | ICT2 DEHGAM 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
152 | WR2T5 | ICT1 SATNA 400/220kV | 315 | WR-II | -- | 2015-06-19 | 16:58 | 2015-06-19 | 17:16 | -- | -- | -- | -- | -- | -- | 0.3 | 0 | 0 | 0 | -- | -- | -- | H/T to attend hotspot in B-ph Bushing connector. |  | 99.96%
153 | WR2T6 | ICT2 SATNA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
154 | WR2T7 | ICT1 KHANDWA 400/220kV | 315 | WR-II | -- | 2015-06-05 | 10:56 | 2015-06-05 | 19:01 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.08 | -- | -- | -- | H/T to avail OCC approved S/D for NTAMC Work. |  | 100%
155 | WR2T8 | ICT2 KHANDWA 400/220kV | 315 | WR-II | -- | 2015-06-13 | 10:20 | 2015-06-13 | 19:48 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.47 | -- | -- | -- | H/T to avail OCC approved S/D for NTAMC Work. |  | 100%
156 | WR2T9 | ICT1 VAPI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
157 | WR2T10 | ICT2 VAPI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
158 | WR2T11 | ICT1 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
159 | WR2T12 | ICT1 RAJGARH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
160 | WR2T13 | ICT2 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
161 | WR2T14 | ICT1 ITARSI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
162 | WR2T15 | ICT1 DAMOH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
163 | WR2T16 | ICT2 DAMOH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
164 | WR2T17 | ICT2 RAJGARH 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
165 | WR2T18 | ICT1 BINA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
166 | WR2T19 | ICT1 PIRANA 400/220kV | 315 | WR-II | -- | 2015-06-17 | 12:21 | 2015-06-17 | 13:49 | -- | -- | -- | -- | -- | -- | 1.47 | 0 | 0 | 0 | -- | -- | -- | To avail outage to attend oil leakage from R phase OLTC |  | 99.8%
167 | WR2T20 | ICT2 PIRANA 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
168 | WR2T21 | ICT3 GWALIOR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
169 | WR2T22 | ICT1 SHUJALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
170 | WR2T23 | ICT1 BHACHAU 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
171 | WR2T24 | ICT2 BHACHAU 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
172 | WR2T25 | ICT2 SHUJALPUR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
173 | WR2T26 | ICT1 SATNA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
174 | WR2T27 | ICT2 NAVSARI(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
175 | WR2T28 | ICT1 NAVSARI(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
176 | WR2T29 | ICT2 SATNA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
177 | WR2T30 | ICT1 BINA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
178 | WR2T31 | ICT3 VAPI 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
179 | WR2T32 | ICT2 BINA 765/400kV | 1000 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
180 | WR2T33 | ICT1 GWALIOR 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
181 | WR2T34 | ICT2 GWALIOR 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
182 | WR2T35 | ICT2 INDORE(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-06-06 | 10:14 | 2015-06-06 | 15:13 | -- | -- | -- | -- | -- | -- | 4.98 | 0 | 0 | 0 | -- | -- | -- | ICT H/T to taking out Bph of ICT -2 for modification of LA connection of lt winding. |  | 99.31%
182 | WR2T35 | ICT2 INDORE(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-06-25 | 10:58 | 2015-06-25 | 17:52 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.9 | -- | -- | -- | H/T to take B phase unit out for correction of 33 kV LA connection inside the ICT. |  | 99.31%
183 | WR2T36 | ICT1 INDORE(POOLING) 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
184 | WR2T37 | ICT1 JABALPUR(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-06-13 | 9:56 | 2015-06-13 | 18:15 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.32 | -- | -- | -- | H/T to carry out the commissining work of spare ICT. |  | 100%
185 | WR2T38 | ICT2 JABALPUR(POOLING) 765/400kV | 1500 | WR-II | -- | 2015-06-12 | 9:14 | 2015-06-12 | 17:42 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.47 | -- | -- | -- | H/T to carry out the commissining work of spare phase in place of Yph. |  | 100%
186 | WR2T39 | ICT1 KALA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
187 | WR2T40 | ICT2 KALA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
188 | WR2T41 | ICT3 NAVSARI(GIS) 400/220kV | 500 | WR-II | -- | 2015-06-01 | 8:35 | 2015-06-05 | 13:30 | -- | -- | -- | -- | -- | -- | 100.92 | 0 | 0 | 0 | -- | -- | -- | H/T to attend SF6 Gas leakage at Navsari. |  | 85.98%
189 | WR2T42 | ICT1 MAGARWADA(GIS) 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
190 | WR2T43 | ICT2 MAGARWADA(GIS) 400/220kV | 315 | WR-II | -- | 2015-06-01 | 10:48 | 2015-06-01 | 13:49 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.02 | -- | -- | -- | H/T for remote operation testing from Vapi. |  | 100%
191 | WR2T44 | ICT1 BOISAR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
192 | WR2T45 | ICT2 BOISAR 400/220kV | 315 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
193 | WR2T46 | ICT3 BOISAR 400/220kV | 500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
194 | WR2T47 | ICT2 VINDHYACHAL(POOLING) 765/400kV | 1500 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
195 | WR2T48 | ICT1 VADODARA(GIS) 765/400kV | 1500 | WR-II | -- | 2015-06-18 | 18:35 | 2015-06-18 | 21:25 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 2.83 | -- | -- | -- | ICT A/T during wiring/testing work of ICT# II |  | 100%
196 | WR2T49 | ICT2 VADODARA(GIS) 765/400kV | 1500 | WR-II | -- | 2015-06-23 | 18:20 | 2015-06-23 | 19:58 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 1.63 | -- | -- | -- | A/T of 765/400kV ICT2 at Vadodara (pooling) S/S during testing of Pirana 1 & Asoj 2 bays. |  | 100%
197 | WR2R1 | BUS REACTOR 1 DEHGAM 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
198 | WR2R2 | BUS REACTOR 1 JABALPUR 33kV 25MVAR | 25 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
199 | WR2R3 | BUS REACTOR 2 JABALPUR 33kV 25MVAR | 25 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
200 | WR2R4 | BUS REACTOR 1 ITARSI 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
201 | WR2R5 | BUS REACTOR 2 ITARSI 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
202 | WR2R6 | BUS REACTOR 3 ITARSI 400kV 50MVAR | 50 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
203 | WR2R7 | BUS REACTOR 1 JABALPUR 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
205 | WR2R9 | BUS REACTOR 1 SATNA 400kV 50MVAR | 50 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
206 | WR2R10 | BUS REACTOR 1 BINA 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
207 | WR2R11 | BUS REACTOR 1 DAMOH 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
208 | WR2R12 | BUS REACTOR 1 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-05 | 21:53 | 2015-06-13 | 9:06 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 179.22 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. | Agency: WRPC Mumbai | 100%
208 | WR2R12 | BUS REACTOR 1 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-16 | 16:23 | 2015-06-20 | 19:07 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 98.73 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
208 | WR2R12 | BUS REACTOR 1 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-25 | 18:50 | 2015-06-29 | 18:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 95.47 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
208 | WR2R12 | BUS REACTOR 1 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-30 | 10:56 | 2015-06-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 13.07 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
209 | WR2R13 | BUS REACTOR 1 KHANDWA 400kV 125MAVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
210 | WR2R14 | BUS REACTOR 2 DEHGAM 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
211 | WR2R15 | BUS REACTOR 1 BHACHAU 400kV 63MVAR | 63 | WR-II | -- | 2015-06-25 | 15:45 | 2015-06-25 | 20:04 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 4.32 | -- | -- | -- | Reactor H/T to avail S/D for CSD relay commissining at Bhachau. |  | 100%
212 | WR2R16 | BUS REACTOR 1 SHUJALPUR 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
213 | WR2R17 | BUS REACTOR 1 RAJGARH 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
214 | WR2R18 | BUS REACTOR 1 NAVSARI(GIS) 400kV 63MVAR | 63 | WR-II | -- | 2015-04-09 | 10:51 | 2015-06-07 | 17:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 161.4 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
215 | WR2R19 | BUS REACTOR 2 SATNA 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
216 | WR2R20 | SWITCHABLE LR SHUJALPUR 1 400kV 63MVAR AT NAGDA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
217 | WR2R21 | SWITCHABLE LR SHUJALPUR 2 400kV 63MVAR AT NAGDA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
218 | WR2R22 | BUS REACTOR 2 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-05 | 21:57 | 2015-06-13 | 13:32 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 183.58 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
218 | WR2R22 | BUS REACTOR 2 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-17 | 10:31 | 2015-06-20 | 19:12 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 80.68 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
218 | WR2R22 | BUS REACTOR 2 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-25 | 18:52 | 2015-06-30 | 24:00 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 125.13 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
219 | WR2R23 | BUS REACTOR 3 GWALIOR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-17 | 10:33 | 2015-06-24 | 17:35 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 175.03 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
220 | WR2R24 | BUS REACTOR 1 INDORE(POOLING) 400kV 125MVAR | 125 | WR-II | -- | 2015-06-08 | 10:47 | 2015-06-08 | 17:13 | -- | -- | -- | -- | -- | -- | 6.43 | 0 | 0 | 0 | -- | -- | -- | B/R H/T to avail OCC Approved outage for AMP Works. |  | 99.11%
220 | WR2R24 | BUS REACTOR 1 INDORE(POOLING) 400kV 125MVAR | 125 | WR-II | -- | 2015-06-29 | 9:55 | 2015-06-29 | 18:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 8.32 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 99.11%
220 | WR2R24 | BUS REACTOR 1 INDORE(POOLING) 400kV 125MVAR | 125 | WR-II | -- | 2015-06-30 | 8:56 | 2015-06-30 | 18:02 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 9.1 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 99.11%
221 | WR2R25 | SWITCHABLE LR SHUJALPUR 2 400kV 63MVAR AT BINA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
222 | WR2R26 | SWITCHABLE LR SHUJALPUR 1 400kV 63MVAR AT BINA | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
223 | WR2R27 | BUS REACTOR 1 JABALPUR(POOLING) 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
224 | WR2R28 | BUS REACTOR 2 KHANDWA 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
225 | WR2R29 | BUS REACTOR 2 JABALPUR 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
226 | WR2R30 | BUS REACTOR 1 SATNA 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
227 | WR2R31 | SWITCHABLE LR BINA 1 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
228 | WR2R32 | SWITCHABLE LR BINA 2 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-03 | 10:51 | 2015-06-04 | 5:10 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 18.32 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
229 | WR2R33 | BUS REACTOR 1 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-05 | 22:53 | 2015-06-06 | 2:21 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 3.47 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
230 | WR2R34 | SWITCHABLE LR BINA 1 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
231 | WR2R35 | SWITCHABLE LR BINA 2 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
232 | WR2R36 | SWITCHABLE LR INDORE(POOLING) 1 765kV 240MVAR AT BINA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
233 | WR2R37 | SWITCHABLE LR BINA 1 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
234 | WR2R38 | BUS REACTOR 1 BINA 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
235 | WR2R39 | SWITCHABLE LR BINA 2 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
236 | WR2R40 | BUS REACTOR 2 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-17 | 10:34 | 2015-06-19 | 0:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 37.83 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
237 | WR2R41 | SWITCHABLE LR GWALIOR 3 765kV 240MVAR AT BINA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
238 | WR2R42 | SWITCHABLE LR GWALIOR 1 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
239 | WR2R43 | SWITCHABLE LR JAIPUR 1 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
240 | WR2R44 | BUS REACTOR 1 KALA(GIS) 400kV 80MVAR | 80 | WR-II | -- | 2015-05-25 | 14:41 | 2015-06-07 | 19:01 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 163.02 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
241 | WR2R45 | BUS REACTOR 2 INDORE(POOLING) 400kV 63MVAR | 63 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-05-27 | 10:46 | 2015-06-02 | 20:29 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 44.48 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
242 | WR2R46 | BUS REACTOR 2 INDORE(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-03 | 22:18 | 2015-06-04 | 18:36 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 20.3 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
243 | WR2R47 | BUS REACTOR 2 SHUJALPUR 400kV 125MVAR | 125 | WR-II | -- | 2015-06-27 | 12:43 | 2015-06-27 | 13:31 | -- | -- | -- | -- | -- | -- | 0.8 | 0 | 0 | 0 | -- | -- | -- | S/D to attend HOT SPOT on B Ph Bushing terminal. |  | 99.89%
244 | WR2R48 | SWITCHABLE LR GWALIOR 2 765kV 240MVAR AT SATNA | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
245 | WR2R49 | BUS REACTOR 1 GWALIOR 765kV 240MVAR | 240 | WR-II | -- | 2015-06-01 | 11:40 | 2015-06-01 | 18:21 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 6.68 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
245 | WR2R49 | BUS REACTOR 1 GWALIOR 765kV 240MVAR | 240 | WR-II | -- | 2015-06-02 | 14:01 | 2015-06-07 | 18:18 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 124.28 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
245 | WR2R49 | BUS REACTOR 1 GWALIOR 765kV 240MVAR | 240 | WR-II | -- | 2015-06-11 | 15:33 | 2015-06-12 | 2:37 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 11.07 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
245 | WR2R49 | BUS REACTOR 1 GWALIOR 765kV 240MVAR | 240 | WR-II | -- | 2015-06-16 | 11:04 | 2015-06-20 | 2:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 87.33 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
245 | WR2R49 | BUS REACTOR 1 GWALIOR 765kV 240MVAR | 240 | WR-II | -- | 2015-06-25 | 18:38 | 2015-06-28 | 18:12 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 71.57 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
246 | WR2R50 | BUS REACTOR 2 DAMOH 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
247 | WR2R51 | BUS REACTOR 1 PIRANA 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
248 | WR2R52 | SWITCHABLE LR BINA 3 (IPTC) 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
249 | WR2R53 | SWITCHABLE LR BHOPAL 1 765kV 240MVAR AT JABALPUR(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
250 | WR2R54 | SWITCHABLE LR JAIPUR 2 765kV 240MVAR AT GWALIOR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
251 | WR2R55 | BUS REACTOR 2 BHACHAU 400kV 125MVAR | 125 | WR-II | -- | 2015-06-04 | 10:55 | 2015-06-04 | 22:09 | -- | -- | -- | -- | -- | -- | 11.23 | 0 | 0 | 0 | -- | -- | -- | Reactor H/T To attend the hot spot on Line Isolator at Bhachau. |  | 98.44%
252 | WR2R56 | BUS REACTOR 2 JABALPUR(POOLING) 400kV 125MVAR | 125 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
253 | WR2R57 | BUS REACTOR 1 MAGARWADA 400kV 80MVAR | 80 | WR-II | -- | 2015-04-28 | 15:10 | 2015-06-08 | 20:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 188.45 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
254 | WR2R58 | SWITCHABLE LR SATNA 1 765kV 240MVAR AT VINDHYACHAL(POOLING) | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
255 | WR2R59 | BUS REACTOR 2 BINA 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%
256 | WR2R60 | BUS REACTOR 1 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-05-21 | 9:38 | 2015-06-03 | 18:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 66.23 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
256 | WR2R60 | BUS REACTOR 1 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-05 | 9:49 | 2015-06-07 | 17:24 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 55.58 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
256 | WR2R60 | BUS REACTOR 1 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-15 | 9:49 | 2015-06-18 | 10:14 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 72.42 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. | Agency: WRPC Mumbai | 100%
256 | WR2R60 | BUS REACTOR 1 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-23 | 21:30 | 2015-06-25 | 4:22 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 30.87 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
256 | WR2R60 | BUS REACTOR 1 JABALPUR(POOLING) 765kV 240MVAR | 240 | WR-II | -- | 2015-06-30 | 11:08 | 2015-06-30 | 13:27 | -- | -- | -- | -- | -- | -- | 0 | 0 | 0 | 2.32 | -- | -- | -- | Reactor H/T on Voltage regulation as per WRLDC instructions. |  | 100%
257 | WR2R61 | BUS REACTOR 2 SATNA 765kV 240MVAR | 240 | WR-II | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |  | 100%