|  |
| --- |
|  **Clarification I - Sub-station package (SS-116) is envisaged for a) Extn. of 400/220 kV Nalagarh-S/S S/S under Augmentation of transformation capacity at 400/220kV Nalagarh S/S by 400/220kV, 1x500MVA ICT (4th) and Extn. of 400/220 kV Bikaner-II P/S under Augmentation of transformation capacity at 400/220kV Bikaner-II P/S by 400/220kV, 1x500MVA ICT (3rd)” through RTM route (SPECIFICATION No.: CC/NT/W-AIS/DOM/A02/23/07106)** |
| **S. No**  | **Volume/Section Clause No.**  | **Description**  | **Query**  | **POWERGRID's Reply**  |
| 1. **A- Extension of Nalagarh S/s**
 |
| 1  | Price Schedule- Sr. no. 75  | 245 kV, 1600A, 50kA, 3 single Phase/3 Phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure (Quantity mentioned here is for 3 Phase Type)  | Please confirm the GIB is single phase or 3 – Phase type and also confirm the quantity mentioned in the prize schedule (250 Mtr) is for single phase or for 3-phase.  | The BPS description is amply clear. The quantity mentioned in BPS is for 3-Phase Type.  |
| 2  | Price Schedule- Sr. no. 90 to 96  | CRP for conventional 420 kV and 220 kV Bays  | Please provide the make, model, type of existing Control Relay Panel & Bus bar protection scheme. The details of control relay panel & Bus bar protection scheme is not available in the tender document. Please provide the same.  | Please refer Section Project, clause 2.1,A,7. The other details regarding make, model shall be provided during detailed engineering  |