| Sr. No | Clause No. | Existing Clause | Bidder’s Query | Clarification |
| --- | --- | --- | --- | --- |
| 1 | Clause 2.1 (i), Section Project, Technical Specification, Volume-II  | 6 (Six) numbers of 110MVAR, 1-Phase, 765/√3 kV Shunt Reactors to be used as two banks of 330MVAR, 3-Phase, 765kV Line Reactors along with associated 132 kV Surge Arrestors, dry type air core Neutral Grounding Reactor | Scope requirement is for dry type air core Neutral Grounding Reactor but Ohms detail is not give in Section Project.Request to kindly provide Ohms detail for NGR | NGR of 400 Ohm is envisaged in TS. |
| 2 | Clause 3.0, Section Project, Technical Specification, Volume-II  | EXCLUSIONS | Civil work requirement is not mentioned in Exclusion. Based on past reference , we understand that Civil Work is not in our Scope. Kinldy confirm | Civil work is not envisaged in TS. |