| S.No: | Clause No | Existing Clause | Amended Clause |
| --- | --- | --- | --- |
| 1 | 1.0 | .... The Contractor's scope of work shall be as described in Clauses 1.1, 1.2, 1.3 and 1.4 herein...... ....SCOPE OF WORK..... .... SCOPE OF CONTRACTOR'S SUPPLY ..... | REPLACE: ......The Contractor's scope of work shall be broadly as described in Clauses 1.1, 1,2, 1.3 and 1.4 herein ....... ....1.2 SCOPE OF WORK..... ....1.3 SCOPE OF CONTRACTOR'S SUPPLY ..... |
| 2 | 1.1 | ... Considering the nature of works covered under the subject package, in the eventuality of damages to the Employers’ facilities during execution by the Contractor, the requisite analysis for the same shall be carried out. Bidder shall attributable to the Employer, so as to restore the damaged facilities to its condition as existing before commencement of subject work by the contractor ..... | REPLACE: .... Considering the nature of works covered under the subject package, in the eventuality of damages to the Employers’ facilities during execution by the Contractor, the requisite analysis for the same shall be carried out. Contractor shall restore the damaged facilities to its condition as existing before commencement of subject work by contractor to the satisfaction of Employer. .... |
| 3 | 1.2.18 | … 18. Necessary interface requirement for successful integration with existing Pole-II (1 x 500 MW) … | DELETE: Clause stands deleted. … Necessary interface requirement for successful integration with existing Pole-II (1 x 500 MW) … |
| 4 | 1.2.20 | .... Routing of fibre optic cables inside valve hall from valve base cubicles shall be offset to the hanging valve structures to the extent possible to avoid damage of fibres in case of fire in Valve Structure... | REPLACE: .....Routing of fibre optic cables inside valve hall from valve base cubicles shall be offset to the valve structures to the extent possible to avoid damage of fibres in case of fire in Valve Structure... |
| 5 | 1.2.22 | Contractor shall install new interface panel (comprising of signals of Pole-1 which are required for integrated operation of Pole-1 & Pole-2 together) for further use in HVDC control and Protection and SCADA system. Contractor may make suitable arrangements to bring the signals of Pole-1 to interface panel in control room. Further, at present, Monitoring of pole -2 is available in Pole-1 HMI through remote interface panel placed in Pole-1 control room. This monitoring of Pole-2 shall also be made available in new HMI under present scope. All works related to this interface is under present scope of contractor. | REPLACE: Contractor shall install new interface panel (comprising of signals of Pole-1 which are required for integrated operation of Pole-1 & Pole-2 together) for further use in HVDC control and Protection and SCADA system. Contractor may make suitable arrangements to bring the signals of Pole-1 to interface panel in control room. Further, at present, Monitoring of pole -2 is available in Pole-1 HMI through remote interface panel placed in Pole-1 control room. This monitoring of Pole-2 shall also be made available in new HMI under present scope. All works related to this interface is under present scope of contractor. Employer intends to integrate the refurbished 1X500 MW Pole-1 in future with 1X500 MW Pole-2 for joint operation of 1000 MW. The joint operation is envisaged at a later stage after refurbishment of Pole-2. Contractor shall prepare a detailed document for future integration stating the requirement for joint operation along with detailed signal lists required for the same. The report shall be submitted for Employer’s approval during detailed engineering. All signals of Pole-1 along with filters which are required for integration of Pole-2 for joint operation of Pole-1 & 2 together shall be provided in an Interface cubicle under present scope. This interface cubicle can be placed inside control room. |
| 6 | 1.3.4 | 1.3.4 TYPE TESTING ….. | EXISTING CLAUSE 1.3.4 DELETED. NEW CLAUSE 1.6 ADDED. 1.6 Type Testing The bidder shall offer type tested equipment for the project and the Employer shall accept the equipment type test reports under the following conditions: (i) Type test in accordance with the relevant specified Standards & Technical specification. (ii)The type tested equipment shall be of the same design, insulation class as per the equipment offered under this contract. Technical justification shall be submitted for differences between tested and offered equipment. Employer’s interpretation for this shall be final. In the event that equipment furnished includes important modifications of, or significant departure from, the designs of equipment on which type test report has been furnished or if there is evidence that the equipment does not comply with the requirements of the Specifications, type test procedure was not properly followed as laid down in standards, the Contractor shall conduct the type test without any cost implication to the Employer. In the price bid, the type test charges shall be included in the contract price and no separate type test charges shall be indicated by the bidder. The equipment shall be supplied from the same manufacturing works, where from the sample unit was manufactured and successfully type tested as per relevant standard or at the works of Parent organization in case of technology transfer/ Joint Venture (JV) for the initial period of 03 years from the date of establishment of manufacturing plant. In case of own manufacturing plant at different location within India, the type test of the original manufacturing works shall also be acceptable for the equipment manufactured and supplied from the different location subject to the following conditions: - The relevant standard does not bar the same, - The equipment being manufactured at different locations shall be identical in design, drawings, specifications, ratings to that of the type tested sample in the original facility (where it was manufactured and successfully type tested) - The equipment being manufactured at different locations shall be identical in material & critical components, manufacturing process/ practices, and quality control to that of the type tested sample in the original facility (where it was manufactured and successfully type tested), - Also, while submitting the Type Test Reports, the Original Equipment Manufacturer (OEM), shall furnish an undertaking for above conditions (i), (ii) and (iii). Unless otherwise specified elsewhere, the type test reports submitted shall be of the tests conducted within the years specified below from the Originally scheduled last date of bid submission. While submitting the Type Test Reports, the Original Equipment Manufacturer (OEM), shall furnish an undertaking with it declaring that there is: i) No change in the Design ii) No change in the material, iii) No change in manufacturing process, and iv) No amendment/revision in the relevant standard as regard to type test conditions, since the type test. In case the test reports are of the test conducted earlier than the years specified below from the date of NOA, the contractor shall repeat these test(s) at no extra cost to the Employer. Serial No.; Name of Equipment (As Applicable); Validity of Type test (in Years). 1; Circuit Breaker; 15. 2; Isolator; 15. 3; Lighting Arrester; 15. 4; Instrument Transformer; 15. 5; LT switchgear and MV switchgear; 5. 6; Cable and associated accessories; 10. 7; Control and Relay Panel; 10. 8; Numerical Relays/ BCPU/ BCU/ Process Interface Unit (PIU)/ Stand-alone merging unit (SAMU)/ Transformer Monitoring Unit (TMU); 10. 9; SAS; 10. 10; AC PLC Filter Capacitors; 10. 11; AC PLC Filter Reactors; 10. 12; Battery and Battery Charger; 10. 13; Conductor and Earth wire; 10. 14; AC Insulators (Porcelain/Glass); 10. 15; AC Insulators (Composite); 5. 16; DC Equipment (Thyristor Valves, DC Measuring Devices, Smoothing reactors, DC Switchgear, DC Wall bushings, DC Arresters, DC PLC/RI filter equipments or other HF filter components or any equipment covered under HVDC system; 15. 17; DG Set; 10. 18; HVDC control and protection equipment and Fibre-optic communication equipment; 10. 19; Power, Control and Fibre Optic Cables; 10. 20; Ventilation system; 10. 21; UPS; 10. Table- 1: Validity of Type test for major equipment For all other items not stated above, the type test validity shall be as per CEA (Central Electricity authority) the Guidelines for validity period of type test(s) conducted on Major Electrical equipment in Power Transmission system which is available in the official website of CEA. Acceptance of the type test reports shall be at the discretion of the Employer. In case the test reports are of the test conducted earlier than the years specified above from the date of Originally scheduled last date of bid submission, the contractor shall repeat these test(s) at no extra cost to the Employer. All type tests for equipment, if performed after the date of award of the Contract shall be witnessed by the Employer unless authority to proceed with the tests in his absence is received from the Employer in writing. All expenses towards Employer deputation for witnessing of type testing, shall be borne by Employer. The Contractor shall intimate the Employer the detailed program about the type tests at least two (2) weeks in advance in case of domestic supplies & six (6) weeks in advance in case of foreign supplies. The seismic withstanding test on the DC equipment shall be carried out along with supporting structure in accordance to the Seismic zone of Vizag as per IS-1893/ relevant IEC. Alternatively, Seismic Calculations certified by NABL/other authorized Labs/OEMS shall also be acceptable. |
| 7 | 1.3.5 | ..... 1.3.5 CIVIL WORKS... .....1.3.4.3 FOUNDATIONS AND STRUCTURES.... | REPLACE: ..... 1.3.4 CIVIL WORKS... ....1.3.4.2 FOUNDATIONS AND STRUCTURES... |
| 8 | 1.3.7 | 1.3.7 SPARE PARTS ….. | 1.3.7 SPARE PARTS 1.3.7.1 GENERAL The spare parts and maintenance accessories shall be classified into the following: a) Spare parts and maintenance accessories required by the Contractor to meet the guaranteed availability and reliability over the guarantee period as specified further in Chapter 11. b) Optional spare parts and maintenance accessories recommended by the Contractor or specified in the relevant section(s) of the Specifications, in addition to (a). c) Spares required by the Contractor during installation, testing & commissioning of the system. d) The operation & maintenance accessories and tools & tackles as recommended by the Contractor and as specified here & elsewhere in the Specification. e) Mandatory spares All spares shall be of the same materials and workmanship as the corresponding parts of the equipment furnished and shall be fully interchangeable with those. Further, all main equipment for which a common spare is provided shall be interchangeable with each other. A spare part intended for use as a replacement for any one of several identical parts, for example a capacitor unit, shall be a replacement to any one of those parts without resulting in a deterioration in the performance of the equipment / system. All spares as applicable meant for outdoor use, shall be suitable for prolonged outdoor storage without being energized. The spare equipment shall be supplied complete with accessories etc. as applicable. The spares shall also be packaged in accordance with Clause 1.3.5.1. Should the Contractor consider it necessary or advisable to maintain any equipment energised during storage he shall be responsible for providing the necessary power supplies complete with all necessary switches and protections and for the connections to the equipment in storage and for all monitoring equipment associated with the energized spare(s). All spare parts shall be scheduled to be at the site before the start of testing/ re-commissioning of the first Pole of the HVDC system. The Contractor may use the spares of different equipment as per agreed list from Employer's stock during the guarantee period, provided they are duly replaced by him in the most expeditious manner. All contractual spares (Mandatory and Availability spares) shall be handed over to the Employer prior to start of Availability and reliability monitoring period. In case any Mandatory spares is utilised during availability/Reliability monitoring period, the Employer shall release the reliability bank guarantee only after the spares are replenished. 1.3.7.2.1 Availability Spares The contractor shall supply the spare parts required to meet the specified guaranteed availability and shall include such spare parts in the scope of supply. The spare parts list shall be categorized in two parts i) major components including test equipment, special tools and fixtures & ii) minimum parts required for scheduled inspections and overhaul. The detailed lists of spare parts to meet the guaranteed reliability & availability requirements shall be part of the contract documents. However, if it is found during detailed engineering or Reliability & Availability prediction calculation that additional spares are required to meet target values, the same shall be made available by the Contractor without any additional cost to the Employer. 1.3.7.2.2 Mandatory Spares S.No.; MANDATORY SPARES AND MAINTENANCE EQUIPMENT; Vizag. Spares for Control & Protection; As per Annexure_C & P. Complete DC Current transformer along with all accessories including electronics; 1 no. of each type and rating. DC Current transformer Insulators, cables, accessories & electronics; 1 set of each type and function. Complete DC Voltage Divider of each type along with electronic unit with fitment, hardware & accessories; 1no. of each type and rating. DC Voltage Divider accessories & electronics; 1 set of each type and function. Valve Cooling Equipment; As per Annex-VC. AC PLC Filter Equipment Capacitor units for each type, fitments hardware & accessories of each type of capacitor Reactor unit of each type, Fitments, hardware & accessories Applicable Tuning Unit if any; 2% of population or minimum 02 nos 1 Set 1 Set. Prefabricated cables / patch cords / factory fitted cables with end terminations for control, protection, data acquisition, communication, fault recording, diagnostic, annunciation, alarm and monitoring (except telecommunication).; Minimum 10% or 2 sets (Whichever is higher) of each type and length. In case quantity arrives in fraction then it shall be rounded up.. Battery and Battery Charger; As per Annex-BT. UPS / UMD Spare (For Valve Cooling UPS); As per Annexure_UPS. UPS Spare (For SCADA UPS); As per Annexure_UPS. Hybrid Arc/UV Detection; 1 No along with associated electronics. Cable System (Applicable for items not covered in S.No 12 of this table); As per Annex-CL. DG Set; As per Annex-DG. Clamps & Connectors; 10% of each type and rating or minimum 2 no.s whichever is higher.. Erection Hardware; 10% of each type and rating or minimum 2 no.s whichever is higher.. Thyristor Valve; As per Annexure-K1. DC Surge Arrester with fitments, hardware and accessories and counter; 2 No.s of each type and rating. Arrestor counter of each type; 2 No.s. Mandatory Spares, wherever mentioned, are envisaged for the equipment/items being supplied under the main equipment heads under present scope meeting the requirements of Technical Specifications. The component/sub-component of an equipment/item specified in BPS under Mandatory Spare, which is not applicable as per the offered design of respective main equipment, shall not be referred to. The Contractor may request the Employer and can use the equipment from Employer's stock (supplied as mandatory spares) during the availability guarantee period for maintaining Availability requirements, provided they are duly replaced by the Contractor in the most expeditious manner. If it is found during detailed engineering and/or Availability prediction calculation that additional spares are required to meet target availability values, the same shall be made available by the Contractor without any additional cost to the Employer. Note: - Wherever voltage class is not mentioned, it shall cover all the applicable voltage classes of HVDC terminal. - Wherever spares in BPS/Technical Specification have been specified as “each type/each rating/each type & rating”: If the offered spare/spares is sufficient to replace the respective main equipment of all types/ratings, then such offered spare/spares shall be acceptable. It implies that common spare/spare set fulfilling the spare requirement of all types/ratings shall also be acceptable, provided it is configurable at site itself without special assistance of OEM. - Respective Spares shall be applicable only if main equipment is supplied in that station. - In case quantity arrives in fraction then it shall be rounded up to next higher integer 1.3.7.3 OPTIONAL SPARES (RECOMMENDED SPARES) The Contractor shall supply, on the request of the Employer at any time prior to the expiration of the Availability/reliability monitoring period, the spare parts listed below or any part thereof, at unit prices not greater than those quoted by the Contractor in his Bid against mandatory spares. • Thyristor electronics (PCBs) of each type, Gate cards / TCU/ TE/ Multi Star Coupler / TVM/ RPU as applicable; • each type of relay supplied under this contract, and / or their circuit cards; • each type of printed circuit board/cards; • special tools, materials, instruments or devices required for installation, testing and maintenance. In the event of utilization of any optional spare(s), which is/are purchased by the Employer, during the guarantee period to keep the down time to a minimum, it shall still be considered as ’NOT AVAILABLE" for the purpose of calculating guaranteed availability. 1.3.7.4 COMMISSIONING SPARES The contractor shall supply additional spares which he expects to consume during installation, testing and commissioning of the systems. The quantity of these spares shall be decided based on his previous experience, such that site work shall not be hampered due to non-availability of these spares. The unused spares may be left at the respective sites for later use by the Employer. 1.3.7.5 TOOLS & TACKLES The Contractor shall also supply at site one set of all special tools & tackles, testing equipment, handling equipment, etc. (under the present scope) which are required by the Employer's maintenance staff to maintain the stations successfully. The contractor may use these tools & tackles, testing equipment, handling equipment specified by employer at site during commissioning and same shall be handed over to site after successful commissioning. The condition of equipment shall be good at time of handing over of equipment and the damaged equipment shall be rectified/ repaired to the satisfaction of site engineer or else shall be replaced by the contractor/ bidder. |
| 10 | 1.4.3 | … For the first 30 days after start of trial operation of both poles/blocks, there shall be one engineer of the Contractor on a round the clock basis. … | REPLACE: … For the first 30 days after start of trial operation of refurbished Pole1, there shall be one engineer of the Contractor on a round the clock basis. … |
| 11 | 1.4.5 | ..... i) Energy Availability. ii) Reliability iii) Station Power rating iV) Thyristor failure rate v) Relay module /C&P module/Component failure. Vi) Rate shut down duration. Vii) Station efficiency(Station loss) ..... | REPLACE: ..... i) Energy Availability. ii) Reliability iii) Station Power rating iV) Thyristor failure rate v) Relay module /C&P module/Component failure. Vi) shut down duration. Vii) Station efficiency(Station loss) ..... |
| 12 | 1.8 | 1.8 TECHNICAL REQUIREMENTS …. | REPLACE: 1.8 Technical Requirements: General: Bidder shall clearly indicate the manufacturer name and address of works, country of origin, and BOQ in the Bid for the HVDC equipment as mentioned in clause 1.8.1 -In case the bidder proposes to get the civil/erection works executed through sub- contractors, then such sub-contractors must have at least two years’ experience in executing such works of similar value. 1.8.1 Technical Requirement of HVDC Equipment Following equipment shall be offered from the facilities of manufacturer(s) who meets the technical requirements as stipulated here: 1.8.1.1 Technical requirement of thyristor valve: - The Manufacturer whose Thyristor Valve(s) are offered should be a regular manufacturer from last five (5) years and must have designed, manufactured/ assembled, tested & supplied Thyristor Valve(s) for minimum one no. long distance HVDC Converter station of rating at least 500kV, 1000 MW HVDC Station or a Back to Back HVDC Station of rating 250MW or above and the same should have been in satisfactory operation for at least two (2) years as on the date of NOA. - Alternatively, Thyristor Valve(s) may also be offered from Indian manufacturer who meets the following requirements: - Who have assembled, routine tested, supplied thyristor valves for minimum one long distance HVDC converter station or a Back-to-Back HVDC station from their works and the same should have been in satisfactory operation as on the date of NOA. OR - Who have established manufacturing/ assembly facilities in India based on the technological support of the Parent/Principal/Group Company subject to carrying out routine tests in India. Further, Indian manufacturer and Parent/ Principal/ Group company shall submit a joint deed of undertaking (as per the relevant format attached in Section Project) during detailed engineering for the successful performance of the Thyristor Valve. Notwithstanding the stipulation at 1.8.1.1 above, i) In case of Thyristor Valves, it is required that manufacture or assembly of 100% thyristor Valve module and its routine testing is to be carried out in India. Type testing is required to be carried out on Thyristor valve modules assembled in India. 1.8.1.2 Technical requirement of HVDC control and protection: - The Manufacturer whose HVDC Control & Protection (HVDC C&P) System are offered should be a regular manufacturer from last five (5) years and must have designed, manufactured, tested, installed & commissioned HVDC C&P System for minimum one no. long distance HVDC Converter station of rating at least 500kV, 1000 MW HVDC Station or a Back-to-Back HVDC Station of rating 250MW or above and the same should have been in satisfactory operation for at least two (2) years as on the date of NOA. - In case, the Manufacturer offers their latest version of HVDC Control and Protection System which is not in operation as on the date of NOA, the same shall also be acceptable however, the defect liability period of the same shall be 05 years from DOCO. - Alternatively, HVDC Control & Protection (HVDC C&P) System may also be offered from Indian manufacturer who have established manufacturing/ assembly facilities in India based on the technological support of the Parent/Principal/Group Company subject to carrying out routine testing & factory acceptance test in India. Further, the Indian manufacturer and Parent/ Principal/ Group company shall submit a joint deed of undertaking (as per the relevant format attached in Section Project) during detailed engineering for the successful performance of the HVDC control and protection system. 1.8.1.3 Technical requirement of valve cooling system - The Manufacturer whose Valve Cooling System are offered should be a regular manufacturer from last five (5) years and must have manufactured, tested, & supplied Valve Cooling System for minimum one no. long distance HVDC Converter station of rating at least 500kV, 1000 MW HVDC Station or a Back to Back HVDC Station of rating 250MW or above and the same should have been in satisfactory operation for at least two (2) years as on the date of NOA. - Alternatively, the manufacturer, who have established manufacturing and testing facilities in India for the Valve Cooling System and not meeting the requirement stipulated in (i) above, can also be considered provided that: - Such equipment (Valve Cooling System) have been manufactured in the above Indian works & type tested (as per IEC/IS standard) as on the date of NOA. - The defect liability period for above items/equipment shall be five (5) years from DOCO. - Alternatively, the manufacturer, who have established manufacturing and testing facilities in India for the Valve Cooling System and not meeting the requirement stipulated in (i) above, can also be considered provided that: - Manufacturer must conduct successful type tests under the project. - The defect liability period for above items/equipment shall be five (5) years from DOCO. - Manufacturer receives POWERGRID approval after assessment of the facility/plant to ascertain their ability to manufacture/assembly. 1.8.1.4 Technical requirement of other HVDC equipment (as applicable) - The bidders/Contractor shall offer equipment, DC CT, DCVD, CVT/CVD, Smoothing Reactors, PLC Filter DC Disconnector, DC Commutation Switches, DC Wall Bushings, DC arresters, On line DC Line fault locator from manufacturers whose similar equipment for similar applications have been in service for at least two years as on the date of NOA and should have been type tested as per relevant standards. - Alternatively, the manufacturer, who have established manufacturing and testing facilities outside India for the offered equipment and not meeting the requirement stipulated in (i) above, can also be considered provided that: - Such equipment have been manufactured in the above works & type tested (as per IEC/IS standard) as on the date of NOA. - The defect liability period for above items/equipment shall be five (5) years from DOCO. - Alternatively, the manufacturer, who have established manufacturing and testing facilities in India for the offered equipment and not meeting the requirement stipulated in (i) above, can also be considered provided that: - Such equipment have been manufactured in the above Indian works & type tested (as per IEC/IS standard) as on the date of NOA. - The defect liability period for above items/equipment shall be five (5) years from DOCO. - Alternatively, the manufacturer, who have established manufacturing and testing facilities in India for the offered equipment and not meeting the requirement stipulated in (i) above, can also be considered provided that: - Manufacturer must conduct successful type test under the project. - The defect liability period for above items/equipment shall be five (5) years from DOCO. - Manufacturer receives POWERGRID approval after assessment of the facility/plant to ascertain their ability to manufacture/assembly. 1.8.1.5 Technical Requirement of ACDB / DCDB Panels: The ACDB / DCDB panels have to be supplied from the OEM of switchgear supplier, and which are in operation for at least two years as on the date of NOA. The Testing and Commissioning of the LT system has to be done by the commissioning team of OEM only. Annexure- JDU is attached for format of Joint Deed of Undertaking for Thyristor Valve/ Control and Protection. |
| 13 | Annexure Outage Schedule | .... The upgrade is to be done only a short total outage for the station control is allowed. Hence the link will be available to transfer half the power during the execution time, except for the days when the Station control is upgraded. A maximum outage time allowed for upgrade projects is as per below: ... | REPLACE: ... The permissible outage schedule is as under: ..... |
| 14 | Annexure Outage Schedule | ..... Pole-1 Outage 130 days (100 days upgrade work and 30 days for power and control cable replacement) ..... | REPLACE: .... Pole-1 Outage 130 days (for upgrade work and power and control cable replacement). However, Contractor may plan the work simultaneously to minimise Outage time for Pole 1. ..... |
| 15 | 2.1 | ........... Data which the Contractor shall assume in the design of all works and equipment in his scope is given in Clauses 2.4 of the Technical Specification and Existing equipment data provided as part of TS ...... | REPLACE: ........... Data which the Contractor shall assume in the design of all works and equipment in his scope is given in Clause 2.3 of the Technical Specification and Existing equipment data provided as part of TS ...... |
| 16 |  | ..... 2.4.1.2 2.4.1.3 2.4.1.4 2.4.1.5 2.4.1.6 2.4.1.7 2.4.1.8 2.4.1.9 .... | REPLACE: ..... 2.3.1.2 2.3.1.3 2.3.1.4 2.3.1.5 2.3.1.6 2.3.1.7 2.3.1.8 2.3.1.9 .... |
| 17 | 2.2.1 |  | ADD: (in the Table) Last row of Table: Site Temperature; VIZAG. Max Ambient temperature (dry bulb one-hour average) Minimum Ambient temp. Max dry bulb 24hr average; 50 deg C 0 deg C 40 deg C. |
| 18 | 2.4.1.10 |  | ADD: New Clause SPECIFIC REQUIREMENTS AT VIZAG DUE TO COASTAL ZONE All outdoor equipment & support structure envisaged in this project shall be designed for coastal saline environment. Zinc coating for galvanization of towers, beams, structures, equipment support structures, ladders of equipment, cleats, base plates, foundation bolts etc. shall not be less than 900 gm/sqm. RTV coating of all AIS equipment to be carried out for Coastal area protection. Any additional protection for outdoor switchyard equipment shall also be carried out considering coastal area of Vizag as per RFP/relevant standards. Corrosivity category C4 shall be considered in line with IS 14191:2024. The Contractor shall take specific measures for protection against airborne salt at Vizag for all the equipment. |
| 19 | 2.4.3.1 | … The design consideration shall be such that any one subbank filter can be taken out upto transmitted power level of 1000 MW. For power levels beyond 1000 MW this subbank shall be considered available. …. | REPLACE: … The design consideration shall be such that any one subbank filter can be taken out upto transmitted power level of 500 MW. For power levels beyond 500 MW this subbank shall be considered available. …. |
| 20 | 2.4.3.2 | … The design consideration shall be such that any one subbank filter can be taken out upto transmitted power level of 1000 MW. For power levels beyond 1000 MW this subbank shall be considered available. …. | REPLACE: … The design consideration shall be such that any one subbank filter can be taken out upto transmitted power level of 500 MW. For power levels beyond 500 MW this subbank shall be considered available. …. |
| 21 | 2.4.7.3 | Refer Annexure-Generator for preliminary list of generators in proximity of Chandrapur HVDC (up to three electrical buses away). | REPLACE: Refer Annexure-Generator for preliminary list of generators in proximity of Vizag HVDC (up to three electrical buses away). |
| 22 | Chapter 3, 3.15.1 3.15.2 3.15.3 | … 3.15.1…. 3.15.2…. 3.15.3 … ….. | Delete: Clause 3.15.1, 3.15.2 & 3.15.3 stands deleted. |
| 23 | 6.3.2.2 (Chapter 5) | …. The minimum weight of the zinc coating shall be 618 gm/sq.m and …… …. | REPLACE: Refer Chapter 5, Rev01 |
| 24 | 6.1 to 6.5.3 (Chapter 5) | References Correction | REPLACE: Refer Chapter 5, Rev01 |
| 25 | 6.3.1 | …. However, such design should have been in satisfactory operation in a similar environment for at least two years on the date of bid opening. …. | REPLACE: …. However, such design should have been in satisfactory operation in a similar environment for at least two years on the originally scheduled date of bid opening. …. |
| 26 | 8.9.7 | … 8.9.7 PRE-ENGINEERED STORE BUILDING Size : About 18mx80M …… | REPLACE: … 8.9.7 PRE-ENGINEERED STORE BUILDING Size : About 18mx100M …… |
| 27 | Chapter-11 | DELETE | ADD: Refer Chapter 11, Rev01 |