| Sl. No | Clause Ref. No. | Existing provision | Amended as |
| --- | --- | --- | --- |
|  | GCC/SCC Clause 23.3(b) | Replace the Sub- Clause GCC 23.3(b) in SCC: pay liquidated damages to the Employer in respect of the failure to meet the Functional Guarantees and Shut down duration/ Outage Schedule as specified at Chapter-11 and Clause 1.11 of Part-1 of Technical Specifications, Vol-II of the Bidding Documents and as per rates given here under: S.N; Parameters for levy of liquidated damages on failure to meet the guarantees; Liquidated Damages. 1.; Station Losses for Block-1. - a) No load losses(KW) - b) Equivalent load losses (KW); - No load losses@ INR 0.8 million per KW - Equivalent load losses@ 0.4 million per KW. 2.; System Availability Minimum Energy availability requirement for Block 1 per half year; INR 30 Million for each 0.1% or part thereof for the shortfall below 99.8% down to 98%. 3.; System Reliability a) Equivalent Outage Frequency (EOF) for Block 1 per half year; - INR 1 Million for each EOF or part thereof above the guaranteed value. 4.; Station Power Rating Guarantee Shortfall: Shortfall in the total power transfer capability (1000 MW) joint operation of Block-1 and Block-2 & (500MW) for block-1 individually; INR 0.2 million for each KW or part thereof **. 5.; Shut down duration/ Outage Schedule of Running System (a) Block 1 (b) Both Blocks; INR 1 Million per Block for each additional 24 Hours or part thereof^ INR 0.5 Million for each 24 Hours or part thereof^^. ** a) Compensation shall be paid up to a maximum 500 Million INR of Block-1 due to shortfall in total power transfer capability (500 MW) b) Compensation shall be paid up to a maximum of 1000 Million INR for joint operation of Block-1 and Block-2 operation due to shortfall in total power transfer capability (1000 MW) Maximum limit on compensation payable under (a) and (b) above in aggregate shall be 500 Million INR per block. ^ Liquidated damages of INR 1 Million for Block-1 for each additional 24 Hours or part thereof, due to revenue loss to Employer, subject to maximum period of upto 1 month. ^^ Liquidated damages of INR 0.5 Million for each 24 Hours or part thereof, subject to maximum period of upto 1 month. Further, overall capping on the cumulative LD for Availability, Reliability, Station Power Rating, Transient Disturbances and Outage Schedule shall be 15% of Contract Price. In addition to the above, the Contractor shall guarantee the performance of the following parameters. Sl No; Parameter; Guaranteed Values. 1.; Annual rate of failure of thyristor level ( defined per six months); ≤0.1% of each 12 pulse valve group except first unit failure. 2.; Guaranteed Failure rate of Relay Module/C&P Module/Component ( defined per six months); ≤ 0.5% except first unit failure. In the event of any shortfall in performance of the guaranteed values as above, the Contractor shall supply additional spares pursuant to Chapter-11, Part – 1 Technical Specifications, Vol – II of the Bidding Documents. The amount of liquidated damages so recoverable shall be as per the aforesaid ceiling and shall not prejudice the contractor's other liabilities under the Contract in any manner. The liquidated damages for shortfall in guaranteed parameters and for delay in completion are independent of each other and shall be levied separately and concurrently. | Replace the Sub- Clause GCC/SCC 23.3(b) in SCC: pay liquidated damages to the Employer in respect of the failure to meet the Functional Guarantees and Shut down duration/ Outage Schedule as specified at Chapter-11 and Clause 1.11 of Part-1 of Technical Specifications, Vol-II of the Bidding Documents and as per rates given here under: S.N; Parameters for levy of liquidated damages on failure to meet the guarantees; Liquidated Damages. 1.; Station Losses for Block-1. - a) No load losses(KW) - b) Equivalent load losses (KW); - No load losses@ INR 0.8 million per KW - Equivalent load losses@ 0.4 million per KW. 2.; System Availability Minimum Energy availability requirement for Block 1 per half year; INR 30 Million for each 0.1% or part thereof for the shortfall below 99.8% down to 98%. 3.; System Reliability Equivalent Outage Frequency (EOF) for Block 1 per half year; INR 1 Million for each EOF or part thereof above the guaranteed value. 4.; Station Power Rating Guarantee Shortfall: Shortfall in the total power transfer capability (500MW) for block-1 individually; INR 0.2 million for each KW or part thereof **. 5.; Shut down duration/ Outage Schedule of Running System Block 1; INR 1 Million per Block for each additional 24 Hours or part thereof ^. ** a) Compensation shall be paid up to a maximum 500 Million INR of Block-1 due to shortfall in total power transfer capability (500 MW) ^ Liquidated damages of INR 1 Million for Block-1 for each additional 24 Hours or part thereof, due to revenue loss to Employer, subject to maximum period of upto 1 month. Further, overall capping on the cumulative LD for Availability, Reliability, Station Power Rating and Outage Schedule shall be 15% of Contract Price. In addition to the above, the Contractor shall guarantee the performance of the following parameters. Sl No; Parameter; Guaranteed Values. 1.; Annual rate of failure of thyristor level ( defined per six months); ≤0.1% of each 12 pulse valve group except first unit failure. 2.; Guaranteed Failure rate of Relay Module/C&P Module/Component ( defined per six months); ≤ 0.5% except first unit failure. In the event of any shortfall in performance of the guaranteed values as above, the Contractor shall supply additional spares pursuant to Chapter-11, Part – 1 Technical Specifications, Vol – II of the Bidding Documents. The amount of liquidated damages so recoverable shall be as per the aforesaid ceiling and shall not prejudice the contractor's other liabilities under the Contract in any manner. The liquidated damages for shortfall in guaranteed parameters and for delay in completion are independent of each other and shall be levied separately and concurrently. |
|  | Appendix-8(b), Functional Guarantees of Section-VI | FUNCTIONAL GUARANTEES 1.0 The Facilities and all parts thereof offered shall meet the Functional Guarantees requirements stipulated in Technical Specification. 2.0 The following Guaranteed parameters and respective Guaranteed values of the Facilities and all parts thereof are guaranteed by the Bidder/ Contractor: Sl. No.; Parameter; Guaranteed Values. 1; Rated Station capacity 1. Block-1 2. Joint operation of Block –1 & Block-2; 1. 500 MW 2. 1000MW. 2; Station Availability Minimum Energy availability requirement for Block-1; ≥ 99.8%. 3; Station Reliability Equivalent Outage Frequency for Block-1 per half year; ≤ 1. 4 a); Efficiency No load losses with Converter Transformer set at principal tap* for Block-1; (In kW); For Block-1:…………... b); Equivalent Load Losses (In kW). For Block-1. 5; Thyristor level failure rate ( defined per six months); ≤0.1% per 12 pulse valve group. 8; Guaranteed Failure rate of Relay Module/C&P Module/Component ( defined per six months); ≤ 0.5% except first unit failure. 9; Shutdown of running system (a) Block 1 (b) Both Block outage; (a) ≤ 100 days (c) ≤ 15 days. In the event of any shortfall in performance of the guaranteed performance of the system / equipments, as mentioned above, the relevant provisions of SCC / GCC in conjunction with the Technical Specification, shall govern. Note: * Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (500 MW per pole) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. | FUNCTIONAL GUARANTEES 1.0 The Facilities and all parts thereof offered shall meet the Functional Guarantees requirements stipulated in Technical Specification. 2.0 The following Guaranteed parameters and respective Guaranteed values of the Facilities and all parts thereof are guaranteed by the Bidder/ Contractor: Sl. No.; Parameter; Guaranteed Values. 1; Rated Station capacity Block-1; 500 MW. 2; Station Availability Minimum Energy availability requirement for Block-1; ≥ 99.8%. 3; Station Reliability Equivalent Outage Frequency for Block-1 per half year; ≤ 1. 4 a); Efficiency No load losses with Converter Transformer set at principal tap* for Block-1; (In kW); For Block-1:…………... b); Equivalent Load Losses (In kW). For Block-1. 5; Thyristor level failure rate ( defined per six months); ≤0.1% per 12 pulse valve group. 8; Guaranteed Failure rate of Relay Module/C&P Module/Component (defined per six months); ≤ 0.5% except first unit failure. 9; Shutdown of running system Block 1; ≤ 130 days. In the event of any shortfall in performance of the guaranteed performance of the system / equipment’s, as mentioned above, the relevant provisions of SCC / GCC in conjunction with the Technical Specification, shall govern. Note: * Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (500 MW) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. |
|  | Attachment-10(Guarantee Declaration) to First Envelope Bid Form | In view of the above, the existing Attachment-10(Guarantee Declaration) is stand revised and enclosed in the revised First Envelope Bid Form excel file namely ‘First Envelope and Bid Forms_rev01’. Note- Bidders are requested to consider the revised excel ‘First Envelope and Bid Forms_rev01’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘First Envelope and Bid Forms_rev01’ to ‘First Envelope and Bid Forms’. As per the provisions of the portal, it is mandatory to upload the excel file titled ‘First Envelope and Bid Forms’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |