| Clarification-II dated 13.02.2020 for Bidding documents of Spare Transformer package TR02 for procurement of (i) 01 no. 500MVA, 400/220/33kV 3 phase Transformer at Bidadi S/s, (ii) 02 nos. 150MVA, (400/√3) / (220/√3) / 33kV, 1 phase Transformer at Panipat S/s and (iii) 01 no. 63MVAR 420kV 3 phase Reactor at Bongaigaon S/s.. Spec no. CC-CS/1007-SR2/TR-4073/3/G2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.No | REFERENCE DOCUMENT | Clause Description | Bidder’s Query/Comments | POWERGRID’s Reply/Clarification |
|  | Section/ Clause No./ PAGE No. |  |  |  |
|  | Annexure I-1.7, Vol-II, Section Project | Impedance of 150MVA 400/220/33kV 1ph Auto Transformer | With reference to subject Tender, we are having the below Query regarding Impedance of 150MVA 400/220/33kV Auto Transformer as under. - HV-MV @ Normal Tap=13.58% (+/- IEC Tolerance) - HV-MV @Maximum Tap=6.8% - HV-MV @ Minimum Tap = 18% It is observed that impedance at maximum tap is very much on lower side. In view of above, we request you to please confirm reconfirm the impedance values of 150MVA 400/22/33kV Auto Transformers | Bidder to comply with the requirement of impedance value of 150MVA 400/22/33kV Auto Transformer as per TS. |