| Clarification-I dated 07.02.2020 for Bidding documents of Spare Transformer package TR02 for procurement of (i) 01 no. 500MVA, 400/220/33kV 3 phase Transformer at Bidadi S/s, (ii) 02 nos. 150MVA, (400/√3) / (220/√3) / 33kV, 1 phase Transformer at Panipat S/s and (iii) 01 no. 63MVAR 420kV 3 phase Reactor at Bongaigaon S/s.. Spec no. CC-CS/1007-SR2/TR-4073/3/G2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.No | REFERENCE DOCUMENT | Clause Description | Bidder’s Query/Comments | POWERGRID’s Reply/Clarification |
|  | Section/ Clause No./ PAGE No. |  |  |  |
|  | 400 KV AUTO TRANSFORMER_R11 - CL 3.13.1 | Dynamic Short Circuit Test requirement 3.13.1 - For 400 kV Class Auto transformer – Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit test on 315MVA, 400/220/33kV Auto transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report/certificate along with bid. In case bidder has not successfully tested 315MVA, 400/220/33kV Auto transformer for Dynamic Short Circuit test, their bid shall be considered technically non responsive. Further, design review of offered 400 kV Class Auto transformer shall be carried out based on the design of short circuit tested 315MVA Auto transformer. | We have conducted successfully Dynamic Short circuit test on 315MVA, 400/220/33kV Auto Transformer with Constant Ohmic Impedance (May 2009) at KEMA. As per specification require transformer is single phase, IV voltage variation with constant ohmic impedance pattern. Hence 315MVA transformer falls outside the definition of similar transformer as per IEC60076-5. Due to the same, we request to verify the SC withstand capability as per IEC60076-5 A.3.1 (Design review by check against manufacturer’s design rules for short circuit strength). Kindly please confirm. | For bidder’s qualification, existing contract documents clause shall prevail. The design of 150MVA, 400/220/33KV 1-ph Transformer shall be finalized on calculation basis with nearest rating/design transformer. Short Circuit testing of 150MVA Transformer is not envisaged under the package. |